## Engine NOx
REPORTING YEAR | RECORD_NUMBER | FACILITY ID | FACILITY NAME | ADDRESS | CITY | ZIP5 | ZIP4 | COUNTY | EUID | EUID DESCRIPTION | EVALUATION DATE | CONTROL EQUPMENT | COMPANY PERFORMING TEST | MAX RATE | ALLOWABLE RATE | TESTED OPERATING RATE | TESTED EMISSION RATE | METHOD NUMBER | POLLUTANTS | RESULTS | CONFORM | AUDIT | NOTES | COULD_BE_GENERATOR
2003 | 1 | 0339020174 | NORWALK COMPRESSOR STATION | 4481 SR 601 | Norwalk | 44857 |  | Huron | P002 | 1680 hp natural gas fired engine with catalytic reduction | 2003-11-21 | catalytic | ALMEGA ENVIRONMENTAL, INC. | 1680 hp | 7.41 lbs/hr | 1525.3 hp | 0.11 lbs/hr | 7 | Nitrogen Dioxide | PASS | NA | Y
2003 | 2 | 0387000389 | CYGNET COMPRESSOR STATION | 5215 ROCK RIDGE RD | Cygnet | 43413 |  | Wood | P001 | 1680 hp natural gas fired engine with catalytic reduction | 2003-12-16 | catalytic | ALMEGA ENVIRONMENTAL, INC. | 1680 hp | 7.41 lbs/hr | 1518.2 hp | 0.30 lbs/hr | 7 | Nitrogen Dioxide | PASS | NA | Y
2003 | 12 | 0387000389 | CYGNET COMPRESSOR STATION | 5215 ROCK RIDGE RD | Cygnet | 43413 |  | Wood | P002 | 1680 hp natural gas fired engine with catalytic reduction | 2003-12-17 | catalytic | ALMEGA ENVIRONMENTAL, INC. | 1680 hp | 7.41 lbs/hr | 1518.2 hp | 1.8 lbs/hr | 7 | Nitrogen Dioxide | PASS | NA | Y
2003 | 13 | 0339020174 | NORWALK COMPRESSOR STATION | 4481 SR 601 | Norwalk | 44857 |  | Huron | P001 | 1680 hp Natrual gas fired engine with catalytic reduction | 2003-11-21 | catalytic | ALMEGA ENVIRONMENTAL, INC. | 1680 hp | 7.41 lbs/hr | 1557.6 hp | 2.4 lbs/hr | 7 | Nitrogen Dioxide | PASS | NA | Y
2003 | 14 | 0679000075 | Dominion Transmission Inc - Gilmore Station | 656 Gravel Lick Road | Port Washington | 43837 |  | Tuscarawas | B008 | 3200 HP Dresser Rand TLAD-8 natural gas-fired, 2-stroke lean-burn reciprocating internal combustion engine | 2003-04-16 | engine tuning | DOMINION TRANSMISSION | 3200 hp | 14.11 lb/hr | 3147 hp | 9.2 lb/hr | 7 | Nitrogen Dioxide | PASS | NA | Y
2003 | 15 | 0125102034 | Dominion - Groveport Compressor Station | 5509 Berger Road | Groveport | 43125 |  | Franklin | B002 | 4200 HP Engine-spark ignition, 2-stroke, lean burn | 2003-05-28 | none | DOMINION TRANSMISSION | 4200 | 18.52 lbs/hr | 4066 | 12.3 lbs/hr | 7 | Nitrogen Dioxide | PASS | NA | Y
2003 | 17 | 0679000075 | Dominion Transmission Inc - Gilmore Station | 656 Gravel Lick Road | Port Washington | 43837 |  | Tuscarawas | B007 | 4200 HP Dresser Rand TCV10 natural gas-fired, 2-stroke lean-burn reciprocating internal combustion engine | 2003-04-16 | engine tuning | DOMINION TRANSMISSION | 4200 hp | 18.52 lb/hr | 4090 hp | 14.6 lb/hr | 7 | Nitrogen Dioxide | PASS | NA | Y
2003 | 18 | 0125102034 | Dominion - Groveport Compressor Station | 5509 Berger Road | Groveport | 43125 |  | Franklin | B003 | 3200 HP Engine-spark ignition, 2-stroke, lean burn | 2003-04-04 | none | DOMINION TRANSMISSION | 3200 hp | 14.11 lbs/hr | 3149.6 hp | 12.3 lbs/hr | 7 | Nitrogen Dioxide | PASS | NA | Y | stack test reviewed well prior to ceta form k function becoming operational in our office. Therefore, form k data was entered into ceta august 2003. TS
2003 | 19 | 0125102034 | Dominion - Groveport Compressor Station | 5509 Berger Road | Groveport | 43125 |  | Franklin | B001 | 4200 HP Engine-spark ignition, 2-stroke, lean burn | 2003-04-02 | none | DOMINION TRANSMISSION | 4200 hp | 18.52 lbs/hr | 4072.9 hp | 16.2 lbs/hr | 7 | Nitrogen Dioxide | PASS | NA | Y | stack test reviewed well prior to ceta form k function becoming operational in our office. Therefore, form k data was entered into ceta august 2003. TS
2003 | 21 | 1576001799 | East Ohio Gas - Robinson Station | 5433 West Blvd | Canton | 44718 |  | Stark | P002 | Cooper-Bessemer, 2-Stroke, spark ignition, Lean Burn, Internal Combustion Engine, Model GMV10-T,1350 HP rated power output, 11.5 MMBtu/hr rated heat input | 2003-08-05 | none | AIR/COMPLIANCE CONSULTANTS, INC. | 1350 bhp | see comment | 1220 bhp | 12.35 lbs/hr nox | 7 | Nitrogen Dioxide | PASS | NA | Y
2003 | 41 | 0857103154 | PINNACLE GAS PRODUCERS LLC | 4220 PINNACLE RD | MORAINE | 45439 |  | Montgomery | B001 | 12 MMBtu/hour (1,626 bhp) pipeline quality gas/natural gas-fired compressor engine | 2003-07-30 | N/A | DERENZO & ASSOCIATES |  |  |  |  | 7 | Nitrogen Dioxide | PASS | NA | Y
2003 | 42 | 0857103154 | PINNACLE GAS PRODUCERS LLC | 4220 PINNACLE RD | MORAINE | 45439 |  | Montgomery | B001 | 12 MMBtu/hour (1,626 bhp) pipeline quality gas/natural gas-fired compressor engine | 2003-07-30 | N/A | DERENZO & ASSOCIATES |  |  |  |  | 7 | Nitrogen Oxide | PASS | NA | Y
2003 | 65 | 1576001799 | East Ohio Gas - Robinson Station | 5433 West Blvd | Canton | 44718 |  | Stark | P003 | Cooper-Bessemer, 2-Stroke, spark ignition, Lean Burn, Internal Combustion Engine, Model GMV10-T,1350 HP rated power output, 11.5 MMBtu/hr rated heat input | 2003-08-05 | none | AIR/COMPLIANCE CONSULTANTS, INC. | 1350 bhp | see comment | 1299 bhp | 14.85 lbs/hr nox | 7 | Nitrogen Dioxide | PASS | NA | Y
2003 | 66 | 1576001799 | East Ohio Gas - Robinson Station | 5433 West Blvd | Canton | 44718 |  | Stark | P001 | Cooper-Bessemer, 2-Stroke, spark ignition, Lean Burn, Internal Combustion Engine, Model GMV10-T,1350 HP rated power output, 11.5 MMBtu/hr rated heat input | 2003-08-05 | none | AIR/COMPLIANCE CONSULTANTS, INC. | 1350 bhp | see comment | 1259 bhp | 14.96 lbs/hr nox | 7 | Nitrogen Dioxide | PASS | NA | Y
2003 | 67 | 1576001799 | East Ohio Gas - Robinson Station | 5433 West Blvd | Canton | 44718 |  | Stark | P004 | Cooper-Bessemer, 2-Stroke, spark ignition ,Lean Burn, Internal Combustion Engine, Model GMV10-T,1350 HP rated power output, 11.5 MMBtu/hr rated heat input | 2003-08-05 | none | AIR/COMPLIANCE CONSULTANTS, INC. | 1350 bhp | see comment | 1305 bhp | 16.13 lbs/hr nox | 7 | Nitrogen Dioxide | PASS | NA | Y
2006 | 1216 | 1318120179 | Ford Motor Company, Cleveland Engine Plants | 17601 Brookpark Rd | Brook Park | 44142 | 1518 | Cuyahoga | P245 | This PTI application is for the modification of emissions unit P245 to allow the capacity of testing larger (3.5 liter) engines and to provide a larger thermal (recuperative) oxidizer to control the resulting engine exhaust emissions. | 2006-12-08 | Thermal Oxidizer | Conestoga-Rovers & Associates |  |  |  |  | 7 | Nitrogen Oxide | PASS | NA | Y
2006 | 1219 | 1318120179 | Ford Motor Company, Cleveland Engine Plants | 17601 Brookpark Rd | Brook Park | 44142 | 1518 | Cuyahoga | P245 | This PTI application is for the modification of emissions unit P245 to allow the capacity of testing larger (3.5 liter) engines and to provide a larger thermal (recuperative) oxidizer to control the resulting engine exhaust emissions. | 2006-12-08 | Thermal Oxidizer | Conestoga-Rovers & Associates |  |  |  |  | 7 | Nitrogen Dioxide | PASS | NA | Y
2007 | 321 | 0210000046 | Tennessee Gas Pipeline - Station 214 | 2029 Cobbler Road NE | Carrollton | 44615 | 0000 | Carroll | P016 | 2000 HP (22 mmBtu/hr) natural gas-fired, spark ignition, 4-cycle/lean burn, reciprocating pipeline compressor engine | 2007-04-10 | LEC | Clean Air Engineering |  |  |  |  | 7 | Nitrogen Dioxide | PASS | NA | Y
2007 | 322 | 0210000046 | Tennessee Gas Pipeline - Station 214 | 2029 Cobbler Road NE | Carrollton | 44615 | 0000 | Carroll | P016 | 2000 HP (22 mmBtu/hr) natural gas-fired, spark ignition, 4-cycle/lean burn, reciprocating pipeline compressor engine | 2007-04-10 | LEC | Clean Air Engineering |  |  |  |  | 7 | Nitrogen Oxide | PASS | NA | Y
2007 | 323 | 0210000046 | Tennessee Gas Pipeline - Station 214 | 2029 Cobbler Road NE | Carrollton | 44615 | 0000 | Carroll | P014 | 2000 HP (22 mmBtu/hr) natural gas-fired, spark ignition, 4-cycle/lean burn, reciprocating pipeline compressor engine | 2007-04-11 | LEC | Clean Air Engineering |  |  |  |  | 7 | Nitrogen Oxide | PASS | NA | Y
2007 | 324 | 0210000046 | Tennessee Gas Pipeline - Station 214 | 2029 Cobbler Road NE | Carrollton | 44615 | 0000 | Carroll | P014 | 2000 HP (22 mmBtu/hr) natural gas-fired, spark ignition, 4-cycle/lean burn, reciprocating pipeline compressor engine | 2007-04-11 | LEC | Clean Air Engineering |  |  |  |  | 7 | Nitrogen Dioxide | PASS | NA | Y
2007 | 325 | 0210000046 | Tennessee Gas Pipeline - Station 214 | 2029 Cobbler Road NE | Carrollton | 44615 | 0000 | Carroll | P015 | 2000 HP (22 mmBtu/hr) natural gas-fired, spark ignition, 4-cycle/lean burn, reciprocating pipeline compressor engine | 2007-04-11 | LEC | Clean Air Engineering |  |  |  |  | 7 | Nitrogen Dioxide | PASS | NA | Y
2007 | 326 | 0210000046 | Tennessee Gas Pipeline - Station 214 | 2029 Cobbler Road NE | Carrollton | 44615 | 0000 | Carroll | P015 | 2000 HP (22 mmBtu/hr) natural gas-fired, spark ignition, 4-cycle/lean burn, reciprocating pipeline compressor engine | 2007-04-11 | LEC | Clean Air Engineering |  |  |  |  | 7 | Nitrogen Oxide | PASS | NA | Y
2007 | 327 | 0210000046 | Tennessee Gas Pipeline - Station 214 | 2029 Cobbler Road NE | Carrollton | 44615 | 0000 | Carroll | P006 | 1320 HP (14.52 mmBtu/hr) natural gas-fired, spark ignition, 4-cycle/rich burn, reciprocating pipeline compressor engine with non-selective catalytic reduction | 2007-04-13 | NSCR | Clean Air Engineering |  |  |  |  | 7 | Nitrogen Dioxide | PASS | NA | Y
2007 | 328 | 0210000046 | Tennessee Gas Pipeline - Station 214 | 2029 Cobbler Road NE | Carrollton | 44615 | 0000 | Carroll | P006 | 1320 HP (14.52 mmBtu/hr) natural gas-fired, spark ignition, 4-cycle/rich burn, reciprocating pipeline compressor engine with non-selective catalytic reduction | 2007-04-13 | NSCR | Clean Air Engineering |  |  |  |  | 7 | Nitrogen Oxide | PASS | NA | Y
2007 | 329 | 0210000046 | Tennessee Gas Pipeline - Station 214 | 2029 Cobbler Road NE | Carrollton | 44615 | 0000 | Carroll | P013 | 2000 HP (22 mmBtu/hr) natural gas-fired, spark ignition, 4-cycle/lean burn, reciprocating pipeline compressor engine | 2007-04-13 | LEC | Clean Air Engineering |  |  |  |  | 7 | Nitrogen Dioxide | PASS | NA | Y
2007 | 330 | 0210000046 | Tennessee Gas Pipeline - Station 214 | 2029 Cobbler Road NE | Carrollton | 44615 | 0000 | Carroll | P013 | 2000 HP (22 mmBtu/hr) natural gas-fired, spark ignition, 4-cycle/lean burn, reciprocating pipeline compressor engine | 2007-04-13 | LEC | Clean Air Engineering |  |  |  |  | 7 | Nitrogen Oxide | PASS | NA | Y
2007 | 331 | 0210000046 | Tennessee Gas Pipeline - Station 214 | 2029 Cobbler Road NE | Carrollton | 44615 | 0000 | Carroll | B002 | 1320 HP (14.52 mmBtu/hr) natural gas-fired, spark ignition, 4-cycle/rich burn, reciprocating pipeline compressor engine with non-selective catalytic reduction | 2007-04-14 | NSCR | Clean Air Engineering |  |  |  |  | 7 | Nitrogen Oxide | PASS | NA | Y
2007 | 332 | 0210000046 | Tennessee Gas Pipeline - Station 214 | 2029 Cobbler Road NE | Carrollton | 44615 | 0000 | Carroll | B002 | 1320 HP (14.52 mmBtu/hr) natural gas-fired, spark ignition, 4-cycle/rich burn, reciprocating pipeline compressor engine with non-selective catalytic reduction | 2007-04-14 | NSCR | Clean Air Engineering |  |  |  |  | 7 | Nitrogen Dioxide | PASS | NA | Y
2007 | 333 | 0210000046 | Tennessee Gas Pipeline - Station 214 | 2029 Cobbler Road NE | Carrollton | 44615 | 0000 | Carroll | P009 | 1320 HP (14.52 mmBtu/hr) natural gas-fired, spark ignition, 4-cycle/rich burn, reciprocating pipeline compressor engine with non-selective catalytic reduction | 2007-04-14 | NSCR | Clean Air Engineering |  |  |  |  | 7 | Nitrogen Oxide | PASS | NA | Y
2007 | 334 | 0210000046 | Tennessee Gas Pipeline - Station 214 | 2029 Cobbler Road NE | Carrollton | 44615 | 0000 | Carroll | P009 | 1320 HP (14.52 mmBtu/hr) natural gas-fired, spark ignition, 4-cycle/rich burn, reciprocating pipeline compressor engine with non-selective catalytic reduction | 2007-04-14 | NSCR | Clean Air Engineering |  |  |  |  | 7 | Nitrogen Dioxide | PASS | NA | Y
2007 | 335 | 0210000046 | Tennessee Gas Pipeline - Station 214 | 2029 Cobbler Road NE | Carrollton | 44615 | 0000 | Carroll | P005 | 1320 HP (14.52 mmBtu/hr) natural gas-fired, spark ignition, 4-cycle/rich burn, reciprocating pipeline compressor engine with non-selective catalytic reduction | 2007-04-16 | NSCR | Clean Air Engineering |  |  |  |  | 7 | Nitrogen Dioxide | PASS | NA | Y
2007 | 336 | 0210000046 | Tennessee Gas Pipeline - Station 214 | 2029 Cobbler Road NE | Carrollton | 44615 | 0000 | Carroll | P005 | 1320 HP (14.52 mmBtu/hr) natural gas-fired, spark ignition, 4-cycle/rich burn, reciprocating pipeline compressor engine with non-selective catalytic reduction | 2007-04-16 | NSCR | Clean Air Engineering |  |  |  |  | 7 | Nitrogen Oxide | PASS | NA | Y
2007 | 337 | 0210000046 | Tennessee Gas Pipeline - Station 214 | 2029 Cobbler Road NE | Carrollton | 44615 | 0000 | Carroll | P007 | 1320 HP (14.52 mmBtu/hr) natural gas-fired, spark ignition, 4-cycle/rich burn, reciprocating pipeline compressor engine with non-selective catalytic reduction | 2007-04-17 | NSCR | Clean Air Engineering |  |  |  |  | 7 | Nitrogen Oxide | PASS | NA | Y
2007 | 338 | 0210000046 | Tennessee Gas Pipeline - Station 214 | 2029 Cobbler Road NE | Carrollton | 44615 | 0000 | Carroll | P007 | 1320 HP (14.52 mmBtu/hr) natural gas-fired, spark ignition, 4-cycle/rich burn, reciprocating pipeline compressor engine with non-selective catalytic reduction | 2007-04-17 | NSCR | Clean Air Engineering |  |  |  |  | 7 | Nitrogen Dioxide | PASS | NA | Y
2007 | 339 | 0210000046 | Tennessee Gas Pipeline - Station 214 | 2029 Cobbler Road NE | Carrollton | 44615 | 0000 | Carroll | P008 | 1320 HP (14.52 mmBtu/hr) natural gas-fired, spark ignition, 4-cycle/rich burn, reciprocating pipeline compressor engine with non-selective catalytic reduction | 2007-04-18 | NSCR | Clean Air Engineering |  |  |  |  | 7 | Nitrogen Oxide | PASS | NA | Y
2007 | 340 | 0210000046 | Tennessee Gas Pipeline - Station 214 | 2029 Cobbler Road NE | Carrollton | 44615 | 0000 | Carroll | P008 | 1320 HP (14.52 mmBtu/hr) natural gas-fired, spark ignition, 4-cycle/rich burn, reciprocating pipeline compressor engine with non-selective catalytic reduction | 2007-04-18 | NSCR | Clean Air Engineering |  |  |  |  | 7 | Nitrogen Dioxide | PASS | NA | Y
2007 | 341 | 0210000046 | Tennessee Gas Pipeline - Station 214 | 2029 Cobbler Road NE | Carrollton | 44615 | 0000 | Carroll | P010 | 1320 HP (14.52 mmBtu/hr) natural gas-fired, spark ignition, 4-cycle/rich burn, reciprocating pipeline compressor engine with non-selective catalytic reduction | 2007-04-18 | NSCR | Clean Air Engineering |  |  |  |  | 7 | Nitrogen Oxide | PASS | NA | Y
2007 | 342 | 0210000046 | Tennessee Gas Pipeline - Station 214 | 2029 Cobbler Road NE | Carrollton | 44615 | 0000 | Carroll | P010 | 1320 HP (14.52 mmBtu/hr) natural gas-fired, spark ignition, 4-cycle/rich burn, reciprocating pipeline compressor engine with non-selective catalytic reduction | 2007-04-18 | NSCR | Clean Air Engineering |  |  |  |  | 7 | Nitrogen Dioxide | PASS | NA | Y
2007 | 343 | 0210000046 | Tennessee Gas Pipeline - Station 214 | 2029 Cobbler Road NE | Carrollton | 44615 | 0000 | Carroll | P011 | 1320 HP (14.52 mmBtu/hr) natural gas-fired, spark ignition, 4-cycle/rich burn, reciprocating pipeline compressor engine with non-selective catalytic reduction | 2007-04-19 | NSCR | Clean Air Engineering |  |  |  |  | 7 | Nitrogen Oxide | PASS | NA | Y
2007 | 344 | 0210000046 | Tennessee Gas Pipeline - Station 214 | 2029 Cobbler Road NE | Carrollton | 44615 | 0000 | Carroll | P011 | 1320 HP (14.52 mmBtu/hr) natural gas-fired, spark ignition, 4-cycle/rich burn, reciprocating pipeline compressor engine with non-selective catalytic reduction | 2007-04-19 | NSCR | Clean Air Engineering |  |  |  |  | 7 | Nitrogen Dioxide | PASS | NA | Y
2007 | 345 | 0210000046 | Tennessee Gas Pipeline - Station 214 | 2029 Cobbler Road NE | Carrollton | 44615 | 0000 | Carroll | P012 | 1320 HP (14.52 mmBtu/hr) natural gas-fired, spark ignition, 4-cycle/rich burn, reciprocating pipeline compressor engine with non-selective catalytic reduction | 2007-04-19 | NSCR | Clean Air Engineering |  |  |  |  | 7 | Nitrogen Oxide | PASS | NA | Y
2007 | 346 | 0210000046 | Tennessee Gas Pipeline - Station 214 | 2029 Cobbler Road NE | Carrollton | 44615 | 0000 | Carroll | P012 | 1320 HP (14.52 mmBtu/hr) natural gas-fired, spark ignition, 4-cycle/rich burn, reciprocating pipeline compressor engine with non-selective catalytic reduction | 2007-04-19 | NSCR | Clean Air Engineering |  |  |  |  | 7 | Nitrogen Dioxide | PASS | NA | Y
2007 | 955 | 0448020085 | LINDE GAS NORTH AMERICA, LLC | 2226 NAVARRE RD | Oregon | 43616 |  | Lucas | P001 | Hydrogen Reformer Train 1 - 514 MMBtu/hr methane steam reformer train with low NOx burners and selective catalytic reduction (SCR) control device. | 2007-01-04 | ast mobile cems | AST ENVIRONMENTAL INC. |  |  |  |  | 7 | Nitrogen Oxide | PASS | NA | Y
2007 | 956 | 0448020085 | LINDE GAS NORTH AMERICA, LLC | 2226 NAVARRE RD | Oregon | 43616 |  | Lucas | P001 | Hydrogen Reformer Train 1 - 514 MMBtu/hr methane steam reformer train with low NOx burners and selective catalytic reduction (SCR) control device. | 2007-01-04 | ast mobile cems | AST ENVIRONMENTAL INC. |  |  |  |  | 7 | Nitrogen Dioxide | PASS | NA | Y
2007 | 959 | 0448020085 | LINDE GAS NORTH AMERICA, LLC | 2226 NAVARRE RD | Oregon | 43616 |  | Lucas | P002 | Hydrogen Reformer Train 2 - 514 MMBtu/hr methane steam reformer train with low NOx burners and selective catalytic reduction (SCR) control device. | 2007-02-22 | ast mobile cems | AST ENVIRONMENTAL INC. |  |  |  |  | 7 | Nitrogen Dioxide | PASS | NA | Y
2007 | 960 | 0448020085 | LINDE GAS NORTH AMERICA, LLC | 2226 NAVARRE RD | Oregon | 43616 |  | Lucas | P002 | Hydrogen Reformer Train 2 - 514 MMBtu/hr methane steam reformer train with low NOx burners and selective catalytic reduction (SCR) control device. | 2007-02-22 | ast mobile cems | AST ENVIRONMENTAL INC. |  |  |  |  | 7 | Nitrogen Oxide | PASS | NA | Y
2007 | 1027 | 0605000020 | Tennessee Gas Pipeline Station 204 | 2335 US Route 50 West | Albany | 45710 | 0000 | Athens | B012 | Recip. Engine 11A - Clark Gas Engine TLA-10 3,400 hp | 2007-03-27 | N/A | Tennessee Gas |  |  |  |  | 7 | Nitrogen Dioxide | PASS | NA | Y
2007 | 1028 | 0605000020 | Tennessee Gas Pipeline Station 204 | 2335 US Route 50 West | Albany | 45710 | 0000 | Athens | B012 | Recip. Engine 11A - Clark Gas Engine TLA-10 3,400 hp | 2007-03-27 | N/A | Tennessee Gas |  |  |  |  | 7 | Nitrogen Oxide | PASS | NA | Y
2007 | 1029 | 0605000020 | Tennessee Gas Pipeline Station 204 | 2335 US Route 50 West | Albany | 45710 | 0000 | Athens | B013 | Recip. Engine 12A - Clark Gas Engine TLA-10 3,400 hp | 2007-03-28 | N/A | Tennessee Gas |  |  |  |  | 7 | Nitrogen Oxide | PASS | NA | Y
2007 | 1030 | 0605000020 | Tennessee Gas Pipeline Station 204 | 2335 US Route 50 West | Albany | 45710 | 0000 | Athens | B013 | Recip. Engine 12A - Clark Gas Engine TLA-10 3,400 hp | 2007-03-28 | N/A | Tennessee Gas |  |  |  |  | 7 | Nitrogen Dioxide | PASS | NA | Y
2008 | 402 | 0125102034 | Dominion - Groveport Compressor Station | 5509 Berger Road | Groveport | 43125 |  | Franklin | B001 | 4200 HP Engine-spark ignition, 2-stroke, lean burn | 2008-11-06 | none | DOMINION TRANSMISSION | 4200 hp | 18.52 lbs/hr | 4072.9 hp | 4.80 lbs/hr | 7 | Nitrogen Dioxide | PASS | NA | Y
2008 | 403 | 0125102034 | Dominion - Groveport Compressor Station | 5509 Berger Road | Groveport | 43125 |  | Franklin | B003 | 3200 HP Engine-spark ignition, 2-stroke, lean burn | 2008-11-06 | none | DOMINION TRANSMISSION | 3200 hp | 14.11 lbs/hr | 3149.6 hp | 7.59 lbs/hr | 7 | Nitrogen Dioxide | PASS | NA | Y
2008 | 1166 | 0605000020 | Tennessee Gas Pipeline Station 204 | 2335 US Route 50 West | Albany | 45710 | 0000 | Athens | B012 | Recip. Engine 11A - Clark Gas Engine TLA-10 3,400 hp | 2008-08-05 | N/A | El Paso Pipeline Group - Tennessee Gas |  |  |  |  | 7E | Nitrogen Dioxide | PASS | NA | Y
2008 | 1167 | 0605000020 | Tennessee Gas Pipeline Station 204 | 2335 US Route 50 West | Albany | 45710 | 0000 | Athens | B012 | Recip. Engine 11A - Clark Gas Engine TLA-10 3,400 hp | 2008-08-05 | N/A | El Paso Pipeline Group - Tennessee Gas |  |  |  |  | 7E | Nitrogen Oxide | PASS | NA | Y
2008 | 1168 | 0605000020 | Tennessee Gas Pipeline Station 204 | 2335 US Route 50 West | Albany | 45710 | 0000 | Athens | B013 | Recip. Engine 12A - Clark Gas Engine TLA-10 3,400 hp | 2008-08-05 | N/A | El Paso Pipeline Group - Tennessee Gas |  |  |  |  | 7E | Nitrogen Oxide | PASS | NA | Y
2008 | 1169 | 0605000020 | Tennessee Gas Pipeline Station 204 | 2335 US Route 50 West | Albany | 45710 | 0000 | Athens | B013 | Recip. Engine 12A - Clark Gas Engine TLA-10 3,400 hp | 2008-08-05 | N/A | El Paso Pipeline Group - Tennessee Gas |  |  |  |  | 7E | Nitrogen Dioxide | PASS | NA | Y
2009 | 3 | 0210000046 | Tennessee Gas Pipeline - Station 214 | 2029 Cobbler Road NE | Carrollton | 44615 | 0000 | Carroll | P006 | 1320 HP (14.52 mmBtu/hr) natural gas-fired, spark ignition, 4-cycle/rich burn, reciprocating pipeline compressor engine with non-selective catalytic reduction | 2009-06-16 | NSCR | Plant Services Dept of Tennessee Gas Pipeline |  |  |  |  | 7E | Nitrogen Oxide | PASS | NA | Y
2009 | 4 | 0210000046 | Tennessee Gas Pipeline - Station 214 | 2029 Cobbler Road NE | Carrollton | 44615 | 0000 | Carroll | P006 | 1320 HP (14.52 mmBtu/hr) natural gas-fired, spark ignition, 4-cycle/rich burn, reciprocating pipeline compressor engine with non-selective catalytic reduction | 2009-06-16 | NSCR | Plant Services Dept of Tennessee Gas Pipeline |  |  |  |  | 7E | Nitrogen Dioxide | PASS | NA | Y
2009 | 5 | 0210000046 | Tennessee Gas Pipeline - Station 214 | 2029 Cobbler Road NE | Carrollton | 44615 | 0000 | Carroll | P007 | 1320 HP (14.52 mmBtu/hr) natural gas-fired, spark ignition, 4-cycle/rich burn, reciprocating pipeline compressor engine with non-selective catalytic reduction | 2009-06-16 | NSCR | Plant Services Dept of Tennessee Gas Pipeline |  |  |  |  | 7E | Nitrogen Oxide | PASS | NA | Y
2009 | 6 | 0210000046 | Tennessee Gas Pipeline - Station 214 | 2029 Cobbler Road NE | Carrollton | 44615 | 0000 | Carroll | P007 | 1320 HP (14.52 mmBtu/hr) natural gas-fired, spark ignition, 4-cycle/rich burn, reciprocating pipeline compressor engine with non-selective catalytic reduction | 2009-06-16 | NSCR | Plant Services Dept of Tennessee Gas Pipeline |  |  |  |  | 7E | Nitrogen Dioxide | PASS | NA | Y
2009 | 7 | 0210000046 | Tennessee Gas Pipeline - Station 214 | 2029 Cobbler Road NE | Carrollton | 44615 | 0000 | Carroll | P008 | 1320 HP (14.52 mmBtu/hr) natural gas-fired, spark ignition, 4-cycle/rich burn, reciprocating pipeline compressor engine with non-selective catalytic reduction | 2009-06-17 | NSCR | Plant Services Dept of Tennessee Gas Pipeline |  |  |  |  | 7E | Nitrogen Oxide | PASS | NA | Y
2009 | 8 | 0210000046 | Tennessee Gas Pipeline - Station 214 | 2029 Cobbler Road NE | Carrollton | 44615 | 0000 | Carroll | P008 | 1320 HP (14.52 mmBtu/hr) natural gas-fired, spark ignition, 4-cycle/rich burn, reciprocating pipeline compressor engine with non-selective catalytic reduction | 2009-06-17 | NSCR | Plant Services Dept of Tennessee Gas Pipeline |  |  |  |  | 7E | Nitrogen Dioxide | PASS | NA | Y
2009 | 9 | 0210000046 | Tennessee Gas Pipeline - Station 214 | 2029 Cobbler Road NE | Carrollton | 44615 | 0000 | Carroll | P009 | 1320 HP (14.52 mmBtu/hr) natural gas-fired, spark ignition, 4-cycle/rich burn, reciprocating pipeline compressor engine with non-selective catalytic reduction | 2009-06-17 | NSCR | Plant Services Dept of Tennessee Gas Pipeline |  |  |  |  | 7E | Nitrogen Oxide | PASS | NA | Y
2009 | 10 | 0210000046 | Tennessee Gas Pipeline - Station 214 | 2029 Cobbler Road NE | Carrollton | 44615 | 0000 | Carroll | P009 | 1320 HP (14.52 mmBtu/hr) natural gas-fired, spark ignition, 4-cycle/rich burn, reciprocating pipeline compressor engine with non-selective catalytic reduction | 2009-06-17 | NSCR | Plant Services Dept of Tennessee Gas Pipeline |  |  |  |  | 7E | Nitrogen Dioxide | PASS | NA | Y
2009 | 11 | 0210000046 | Tennessee Gas Pipeline - Station 214 | 2029 Cobbler Road NE | Carrollton | 44615 | 0000 | Carroll | P010 | 1320 HP (14.52 mmBtu/hr) natural gas-fired, spark ignition, 4-cycle/rich burn, reciprocating pipeline compressor engine with non-selective catalytic reduction | 2009-06-18 | NSCR | Plant Services Dept of Tennessee Gas Pipeline |  |  |  |  | 7E | Nitrogen Oxide | PASS | NA | Y
2009 | 12 | 0210000046 | Tennessee Gas Pipeline - Station 214 | 2029 Cobbler Road NE | Carrollton | 44615 | 0000 | Carroll | P010 | 1320 HP (14.52 mmBtu/hr) natural gas-fired, spark ignition, 4-cycle/rich burn, reciprocating pipeline compressor engine with non-selective catalytic reduction | 2009-06-18 | NSCR | Plant Services Dept of Tennessee Gas Pipeline |  |  |  |  | 7E | Nitrogen Dioxide | PASS | NA | Y
2009 | 13 | 0210000046 | Tennessee Gas Pipeline - Station 214 | 2029 Cobbler Road NE | Carrollton | 44615 | 0000 | Carroll | P011 | 1320 HP (14.52 mmBtu/hr) natural gas-fired, spark ignition, 4-cycle/rich burn, reciprocating pipeline compressor engine with non-selective catalytic reduction | 2009-06-18 | NSCR | Plant Services Dept of Tennessee Gas Pipeline |  |  |  |  | 7E | Nitrogen Dioxide | PASS | NA | Y
2009 | 14 | 0210000046 | Tennessee Gas Pipeline - Station 214 | 2029 Cobbler Road NE | Carrollton | 44615 | 0000 | Carroll | P011 | 1320 HP (14.52 mmBtu/hr) natural gas-fired, spark ignition, 4-cycle/rich burn, reciprocating pipeline compressor engine with non-selective catalytic reduction | 2009-06-18 | NSCR | Plant Services Dept of Tennessee Gas Pipeline |  |  |  |  | 7E | Nitrogen Oxide | PASS | NA | Y
2009 | 15 | 0210000046 | Tennessee Gas Pipeline - Station 214 | 2029 Cobbler Road NE | Carrollton | 44615 | 0000 | Carroll | P013 | 2000 HP (22 mmBtu/hr) natural gas-fired, spark ignition, 4-cycle/lean burn, reciprocating pipeline compressor engine | 2009-06-22 | NSCR | Plant Services Dept of Tennessee Gas Pipeline |  |  |  |  | 7E | Nitrogen Oxide | PASS | NA | Y
2009 | 16 | 0210000046 | Tennessee Gas Pipeline - Station 214 | 2029 Cobbler Road NE | Carrollton | 44615 | 0000 | Carroll | P013 | 2000 HP (22 mmBtu/hr) natural gas-fired, spark ignition, 4-cycle/lean burn, reciprocating pipeline compressor engine | 2009-06-22 | NSCR | Plant Services Dept of Tennessee Gas Pipeline |  |  |  |  | 7E | Nitrogen Dioxide | PASS | NA | Y
2009 | 17 | 0210000046 | Tennessee Gas Pipeline - Station 214 | 2029 Cobbler Road NE | Carrollton | 44615 | 0000 | Carroll | P014 | 2000 HP (22 mmBtu/hr) natural gas-fired, spark ignition, 4-cycle/lean burn, reciprocating pipeline compressor engine | 2009-06-23 | NSCR | Plant Services Dept of Tennessee Gas Pipeline |  |  |  |  | 7E | Nitrogen Dioxide | PASS | NA | Y
2009 | 18 | 0210000046 | Tennessee Gas Pipeline - Station 214 | 2029 Cobbler Road NE | Carrollton | 44615 | 0000 | Carroll | P014 | 2000 HP (22 mmBtu/hr) natural gas-fired, spark ignition, 4-cycle/lean burn, reciprocating pipeline compressor engine | 2009-06-23 | NSCR | Plant Services Dept of Tennessee Gas Pipeline |  |  |  |  | 7E | Nitrogen Oxide | PASS | NA | Y
2009 | 19 | 0210000046 | Tennessee Gas Pipeline - Station 214 | 2029 Cobbler Road NE | Carrollton | 44615 | 0000 | Carroll | P015 | 2000 HP (22 mmBtu/hr) natural gas-fired, spark ignition, 4-cycle/lean burn, reciprocating pipeline compressor engine | 2009-06-23 | NSCR | Plant Services Dept of Tennessee Gas Pipeline |  |  |  |  | 7E | Nitrogen Dioxide | PASS | NA | Y
2009 | 20 | 0210000046 | Tennessee Gas Pipeline - Station 214 | 2029 Cobbler Road NE | Carrollton | 44615 | 0000 | Carroll | P015 | 2000 HP (22 mmBtu/hr) natural gas-fired, spark ignition, 4-cycle/lean burn, reciprocating pipeline compressor engine | 2009-06-23 | NSCR | Plant Services Dept of Tennessee Gas Pipeline |  |  |  |  | 7E | Nitrogen Oxide | PASS | NA | Y
2009 | 21 | 0210000046 | Tennessee Gas Pipeline - Station 214 | 2029 Cobbler Road NE | Carrollton | 44615 | 0000 | Carroll | B002 | 1320 HP (14.52 mmBtu/hr) natural gas-fired, spark ignition, 4-cycle/rich burn, reciprocating pipeline compressor engine with non-selective catalytic reduction | 2009-06-24 | NSCR | Plant Services Dept of Tennessee Gas Pipeline |  |  |  |  | 7E | Nitrogen Oxide | PASS | NA | Y
2009 | 22 | 0210000046 | Tennessee Gas Pipeline - Station 214 | 2029 Cobbler Road NE | Carrollton | 44615 | 0000 | Carroll | B002 | 1320 HP (14.52 mmBtu/hr) natural gas-fired, spark ignition, 4-cycle/rich burn, reciprocating pipeline compressor engine with non-selective catalytic reduction | 2009-06-24 | NSCR | Plant Services Dept of Tennessee Gas Pipeline |  |  |  |  | 7E | Nitrogen Dioxide | PASS | NA | Y
2009 | 23 | 0210000046 | Tennessee Gas Pipeline - Station 214 | 2029 Cobbler Road NE | Carrollton | 44615 | 0000 | Carroll | P016 | 2000 HP (22 mmBtu/hr) natural gas-fired, spark ignition, 4-cycle/lean burn, reciprocating pipeline compressor engine | 2009-06-24 | NSCR | Plant Services Dept of Tennessee Gas Pipeline |  |  |  |  | 7E | Nitrogen Dioxide | PASS | NA | Y
2009 | 24 | 0210000046 | Tennessee Gas Pipeline - Station 214 | 2029 Cobbler Road NE | Carrollton | 44615 | 0000 | Carroll | P016 | 2000 HP (22 mmBtu/hr) natural gas-fired, spark ignition, 4-cycle/lean burn, reciprocating pipeline compressor engine | 2009-06-24 | NSCR | Plant Services Dept of Tennessee Gas Pipeline |  |  |  |  | 7E | Nitrogen Oxide | PASS | NA | Y
2009 | 25 | 0210000046 | Tennessee Gas Pipeline - Station 214 | 2029 Cobbler Road NE | Carrollton | 44615 | 0000 | Carroll | P005 | 1320 HP (14.52 mmBtu/hr) natural gas-fired, spark ignition, 4-cycle/rich burn, reciprocating pipeline compressor engine with non-selective catalytic reduction | 2009-06-25 | NSCR | Plant Services Dept of Tennessee Gas Pipeline |  |  |  |  | 7E | Nitrogen Dioxide | PASS | NA | Y
2009 | 26 | 0210000046 | Tennessee Gas Pipeline - Station 214 | 2029 Cobbler Road NE | Carrollton | 44615 | 0000 | Carroll | P005 | 1320 HP (14.52 mmBtu/hr) natural gas-fired, spark ignition, 4-cycle/rich burn, reciprocating pipeline compressor engine with non-selective catalytic reduction | 2009-06-25 | NSCR | Plant Services Dept of Tennessee Gas Pipeline |  |  |  |  | 7E | Nitrogen Oxide | PASS | NA | Y
2009 | 27 | 0210000046 | Tennessee Gas Pipeline - Station 214 | 2029 Cobbler Road NE | Carrollton | 44615 | 0000 | Carroll | P012 | 1320 HP (14.52 mmBtu/hr) natural gas-fired, spark ignition, 4-cycle/rich burn, reciprocating pipeline compressor engine with non-selective catalytic reduction | 2009-06-25 | NSCR | Plant Services Dept of Tennessee Gas Pipeline |  |  |  |  | 7E | Nitrogen Dioxide | FAIL | NA | Y
2009 | 28 | 0210000046 | Tennessee Gas Pipeline - Station 214 | 2029 Cobbler Road NE | Carrollton | 44615 | 0000 | Carroll | P012 | 1320 HP (14.52 mmBtu/hr) natural gas-fired, spark ignition, 4-cycle/rich burn, reciprocating pipeline compressor engine with non-selective catalytic reduction | 2009-06-25 | NSCR | Plant Services Dept of Tennessee Gas Pipeline |  |  |  |  | 7E | Nitrogen Oxide | FAIL | NA | Y
2009 | 29 | 0210000046 | Tennessee Gas Pipeline - Station 214 | 2029 Cobbler Road NE | Carrollton | 44615 | 0000 | Carroll | P012 | 1320 HP (14.52 mmBtu/hr) natural gas-fired, spark ignition, 4-cycle/rich burn, reciprocating pipeline compressor engine with non-selective catalytic reduction | 2009-06-26 | NSCR | Plant Services Dept of Tennessee Gas Pipeline |  |  |  |  | 7E | Nitrogen Oxide | PASS | NA | Y
2009 | 30 | 0210000046 | Tennessee Gas Pipeline - Station 214 | 2029 Cobbler Road NE | Carrollton | 44615 | 0000 | Carroll | P012 | 1320 HP (14.52 mmBtu/hr) natural gas-fired, spark ignition, 4-cycle/rich burn, reciprocating pipeline compressor engine with non-selective catalytic reduction | 2009-06-26 | NSCR | Plant Services Dept of Tennessee Gas Pipeline |  |  |  |  | 7E | Nitrogen Dioxide | PASS | NA | Y
2009 | 47 | 0605000020 | Tennessee Gas Pipeline Station 204 | 2335 US Route 50 West | Albany | 45710 | 0000 | Athens | B012 | Recip. Engine 11A - Clark Gas Engine TLA-10 3,400 hp | 2009-06-05 | N/A | El Paso Pipeline Group - Tennessee Gas |  |  |  |  | 7E | Nitrogen Oxide | PASS | NA | Y
2009 | 48 | 0605000020 | Tennessee Gas Pipeline Station 204 | 2335 US Route 50 West | Albany | 45710 | 0000 | Athens | B012 | Recip. Engine 11A - Clark Gas Engine TLA-10 3,400 hp | 2009-06-05 | N/A | El Paso Pipeline Group - Tennessee Gas |  |  |  |  | 7E | Nitrogen Dioxide | PASS | NA | Y
2009 | 49 | 0605000020 | Tennessee Gas Pipeline Station 204 | 2335 US Route 50 West | Albany | 45710 | 0000 | Athens | B013 | Recip. Engine 12A - Clark Gas Engine TLA-10 3,400 hp | 2009-06-05 | N/A | El Paso Pipeline Group - Tennessee Gas |  |  |  |  | 7E | Nitrogen Oxide | PASS | NA | Y
2009 | 50 | 0605000020 | Tennessee Gas Pipeline Station 204 | 2335 US Route 50 West | Albany | 45710 | 0000 | Athens | B013 | Recip. Engine 12A - Clark Gas Engine TLA-10 3,400 hp | 2009-06-05 | N/A | El Paso Pipeline Group - Tennessee Gas |  |  |  |  | 7E | Nitrogen Dioxide | PASS | NA | Y
2009 | 59 | 0679000075 | Dominion Transmission Inc - Gilmore Station | 656 Gravel Lick Road | Port Washington | 43837 |  | Tuscarawas | B007 | 4200 HP Dresser Rand TCV10 natural gas-fired, 2-stroke lean-burn reciprocating internal combustion engine | 2009-11-30 | engine tuning | DOMINION TRANSMISSION |  |  |  |  | 7E | Nitrogen Dioxide | PASS | NA | Y
2009 | 60 | 0679000075 | Dominion Transmission Inc - Gilmore Station | 656 Gravel Lick Road | Port Washington | 43837 |  | Tuscarawas | B007 | 4200 HP Dresser Rand TCV10 natural gas-fired, 2-stroke lean-burn reciprocating internal combustion engine | 2009-11-30 | engine tuning | DOMINION TRANSMISSION |  |  |  |  | 7E | Nitrogen Oxide | PASS | NA | Y
2009 | 61 | 0679000075 | Dominion Transmission Inc - Gilmore Station | 656 Gravel Lick Road | Port Washington | 43837 |  | Tuscarawas | B008 | 3200 HP Dresser Rand TLAD-8 natural gas-fired, 2-stroke lean-burn reciprocating internal combustion engine | 2009-11-30 | engine tuning | DOMINION TRANSMISSION |  |  |  |  | 7E | Nitrogen Oxide | PASS | NA | Y
2009 | 62 | 0679000075 | Dominion Transmission Inc - Gilmore Station | 656 Gravel Lick Road | Port Washington | 43837 |  | Tuscarawas | B008 | 3200 HP Dresser Rand TLAD-8 natural gas-fired, 2-stroke lean-burn reciprocating internal combustion engine | 2009-11-30 | engine tuning | DOMINION TRANSMISSION |  |  |  |  | 7E | Nitrogen Dioxide | PASS | NA | Y
2009 | 105 | 1576002033 | East Ohio Gas - Pike Compressor Station | 6024 Kieffer Ave., SW | Canton | 44706 |  | Stark | P001 | Caterpillar G3516-LE-AFR, 1340 hp, 9.9 mmbtu/hr capacity, natural gas fired engine. | 2009-09-24 | catalytic incinerator | Air Compliance Testing Inc. |  |  |  |  | 7E | Nitrogen Dioxide | PASS | NA | Y | Tested pollutants: NO2, NO; Permitted Allowable Emission Rate = 4.4 lbs NOx/hr; Permitted Maximum Operating Rate = 1340 bhp; Average Tested Emission Rate = 4.4 lbs NOx/hr; Average Tested Operating Rate = 1242 bhp; Results = Passed; AFS Date = 2010-02-11 00:00:00.0; AFS ID = legacy) Per engineering guide 16 marginal compliance retest is required and may coinside with permit required P003 testing in 2.5 years from issue date (11/17/08).
2009 | 106 | 1576002033 | East Ohio Gas - Pike Compressor Station | 6024 Kieffer Ave., SW | Canton | 44706 |  | Stark | P001 | Caterpillar G3516-LE-AFR, 1340 hp, 9.9 mmbtu/hr capacity, natural gas fired engine. | 2009-09-24 | catalytic incinerator | Air Compliance Testing Inc. |  |  |  |  | 7E | Nitrogen Oxide | PASS | NA | Y | Tested pollutants: NO2, NO; Permitted Allowable Emission Rate = 4.4 lbs NOx/hr; Permitted Maximum Operating Rate = 1340 bhp; Average Tested Emission Rate = 4.4 lbs NOx/hr; Average Tested Operating Rate = 1242 bhp; Results = Passed; AFS Date = 2010-02-11 00:00:00.0; AFS ID = legacy) Per engineering guide 16 marginal compliance retest is required and may coinside with permit required P003 testing in 2.5 years from issue date (11/17/08).
2009 | 107 | 1576002033 | East Ohio Gas - Pike Compressor Station | 6024 Kieffer Ave., SW | Canton | 44706 |  | Stark | P002 | Caterpillar G3516-LE-AFR, 1,340 hp, 9.9 mmbtu/hr capacity natural gas fired engine. | 2009-09-24 | catalytic incinerator | Air Compliance Testing Inc. |  |  |  |  | 7E | Nitrogen Oxide | PASS | NA | Y | Tested pollutants: NO2, NO; Permitted Allowable Emission Rate = 4.4 lbs NOx/hr; Permitted Maximum Operating Rate = 1340 bhp; Average Tested Emission Rate = 3.99 lbs NOx/hr; Average Tested Operating Rate = 1242 bhp; Results = Passed; AFS Date = 2010-02-11 00:00:00.0; AFS ID = legacy) Per engineering guide 16 marginal compliance retest is required and may coinside with permit required P003 testing at 2.5 years from issue date (11/17/08).
2009 | 108 | 1576002033 | East Ohio Gas - Pike Compressor Station | 6024 Kieffer Ave., SW | Canton | 44706 |  | Stark | P002 | Caterpillar G3516-LE-AFR, 1,340 hp, 9.9 mmbtu/hr capacity natural gas fired engine. | 2009-09-24 | catalytic incinerator | Air Compliance Testing Inc. |  |  |  |  | 7E | Nitrogen Dioxide | PASS | NA | Y | Tested pollutants: NO2, NO; Permitted Allowable Emission Rate = 4.4 lbs NOx/hr; Permitted Maximum Operating Rate = 1340 bhp; Average Tested Emission Rate = 3.99 lbs NOx/hr; Average Tested Operating Rate = 1242 bhp; Results = Passed; AFS Date = 2010-02-11 00:00:00.0; AFS ID = legacy) Per engineering guide 16 marginal compliance retest is required and may coinside with permit required P003 testing at 2.5 years from issue date (11/17/08).
2010 | 1 | 0210000046 | Tennessee Gas Pipeline - Station 214 | 2029 Cobbler Road NE | Carrollton | 44615 | 0000 | Carroll | P005 | 1320 HP (14.52 mmBtu/hr) natural gas-fired, spark ignition, 4-cycle/rich burn, reciprocating pipeline compressor engine with non-selective catalytic reduction | 2010-09-01 | NSCR | Plant Services Dept of Tennessee Gas Pipeline |  |  |  |  | 7E | Nitrogen Oxide | PASS | NA | Y | Tested pollutants:NO2, NO; Permitted Allowable Emission Rate = 2.0 grams/BHP-hr; Permitted Maximum Operating Rate = 1320 HP; Average Tested Emission Rate = 0.14 gram/BHP-hr; Average Tested Operating Rate = 1291 HP; Results = Passed; AFS Date = 2010-11-19 00:00:00.0; AFS ID = legacy) OAC rule 3745-14-12 (NOx SIP call) Catalyst inlet temp was 1070.7¿F. Catalyst differential pressure was 3.70" H2O.
2010 | 2 | 0210000046 | Tennessee Gas Pipeline - Station 214 | 2029 Cobbler Road NE | Carrollton | 44615 | 0000 | Carroll | P012 | 1320 HP (14.52 mmBtu/hr) natural gas-fired, spark ignition, 4-cycle/rich burn, reciprocating pipeline compressor engine with non-selective catalytic reduction | 2010-08-24 | NSCR | El Paso Pipelline Group |  |  |  |  | 7E | Nitrogen Dioxide | PASS | NA | Y | Tested pollutants:NO2, NO; Permitted Allowable Emission Rate = 2.0 gram/HP-hr; Permitted Maximum Operating Rate = 1320 HP; Average Tested Emission Rate = 0.28 gram/HP-hr; Average Tested Operating Rate = 1267 HP; Results = Passed; AFS Date = 2010-11-19 00:00:00.0; AFS ID = legacy) OAC rule 3745-14-12 (NOx SIP call) RICE MACT requires the pressure drop across the catalyst not vary by more than 2" water at 100% load +/- 10% from the average pressure drop during the test. The average pressure drop across the catalyst during the test was 3.92" water. RICE MACT requires the catalyst inlet temperature be between 450¿F-1350¿F. The catalyst inlet temperature during the test was 1072.0¿F.
2010 | 3 | 0210000046 | Tennessee Gas Pipeline - Station 214 | 2029 Cobbler Road NE | Carrollton | 44615 | 0000 | Carroll | P010 | 1320 HP (14.52 mmBtu/hr) natural gas-fired, spark ignition, 4-cycle/rich burn, reciprocating pipeline compressor engine with non-selective catalytic reduction | 2010-08-26 | NSCR | Plant Services Dept of Tennessee Gas Pipeline |  |  |  |  | 7E | Nitrogen Oxide | PASS | NA | Y | Tested pollutants:NO2, NO; Permitted Allowable Emission Rate = 2.0 grams/BHP-hr; Permitted Maximum Operating Rate = 1320 HP; Average Tested Emission Rate = 0.48 gram/BHP-hr; Average Tested Operating Rate = 1321 HP; Results = Passed; AFS Date = 2010-11-19 00:00:00.0; AFS ID = legacy) OAC rule 3745-14-12 (NOx SIP call) Ave catalyst inlet temp was 1051.5¿F. Ave catalyst differential pressure was 3.62" H2O.
2010 | 4 | 0546015002 | Bellefontaine Gas Producers, LLC | 2946 US Route 68 North | Bellefontaine | 43311 |  | Logan | P003 | 2275 Hp, 4-stroke lean burn, non-emergency, spark ignition RICE; Ch. 31 modification issued 1/8/2014. | 2010-05-26 | NA | DTE Energy |  |  |  |  | 7E | Nitrogen Dioxide | PASS | NA | Y | Tested pollutants:NO2, NO; Permitted Allowable Emission Rate = 0.6 g/BHp-Hr; Permitted Maximum Operating Rate = 1600 KW; Average Tested Emission Rate = 0.5 g/BHp-Hr; Average Tested Operating Rate = 1600 KW; Results = Passed; AFS Date = 2010-08-31 00:00:00.0; AFS ID = legacy)
2010 | 5 | 0546015002 | Bellefontaine Gas Producers, LLC | 2946 US Route 68 North | Bellefontaine | 43311 |  | Logan | P003 | 2275 Hp, 4-stroke lean burn, non-emergency, spark ignition RICE; Ch. 31 modification issued 1/8/2014. | 2010-08-17 | NA | DTE Energy |  |  |  |  | 7E | Nitrogen Dioxide | PASS | NA | Y | Tested pollutants:NO2, NO; Permitted Allowable Emission Rate = 0.6 g/BHp-Hr; Permitted Maximum Operating Rate = 1600 KW; Average Tested Emission Rate = 0.5 g/BHp-Hr; Average Tested Operating Rate = 1600 KW; Results = Passed; AFS Date = 2010-09-28 00:00:00.0; AFS ID = legacy)
2010 | 6 | 0210000046 | Tennessee Gas Pipeline - Station 214 | 2029 Cobbler Road NE | Carrollton | 44615 | 0000 | Carroll | P011 | 1320 HP (14.52 mmBtu/hr) natural gas-fired, spark ignition, 4-cycle/rich burn, reciprocating pipeline compressor engine with non-selective catalytic reduction | 2010-08-24 | NSCR | Plant Services Dept of Tennessee Gas Pipeline |  |  |  |  | 7E | Nitrogen Dioxide | PASS | NA | Y | Tested pollutants:NO2, NO; Permitted Allowable Emission Rate = 2.0 grams/BH-/hr; Permitted Maximum Operating Rate = 1320 HP; Average Tested Emission Rate = 0.69 gram/BHP-hr; Average Tested Operating Rate = 1251 HP; Results = Passed; AFS Date = 2010-11-19 00:00:00.0; AFS ID = legacy) OAC rule 3745-14-12 (NOx SIP call) Ave catalyst inlet temp was 1070.9¿F. Ave. catalyst differential pressure was 3.84" H2O.
2010 | 7 | 0210000046 | Tennessee Gas Pipeline - Station 214 | 2029 Cobbler Road NE | Carrollton | 44615 | 0000 | Carroll | P009 | 1320 HP (14.52 mmBtu/hr) natural gas-fired, spark ignition, 4-cycle/rich burn, reciprocating pipeline compressor engine with non-selective catalytic reduction | 2010-08-31 | NSCR | Plant Services Dept of Tennessee Gas Pipeline |  |  |  |  | 7E | Nitrogen Dioxide | PASS | NA | Y | Tested pollutants:NO2, NO; Permitted Allowable Emission Rate = 2.0 grams/BHP-hr; Permitted Maximum Operating Rate = 1320 HP; Average Tested Emission Rate = 0.91 gram/BHP-hr; Average Tested Operating Rate = 1285 HP; Results = Passed; AFS Date = 2010-11-19 00:00:00.0; AFS ID = legacy) OAC rule 3745-14-12 (NOx SIP call) Ave catalyst inlet temp was 1082.7¿F. Ave catalyst differential pressure was 3.88" H2O.
2010 | 8 | 0656105002 | East Ohio Gas Company - Woodsfield Station | Bucks Lane | Woodsfield | 43793 |  | Monroe | P002 | 203hp Caterpillar G3306TA natural gas fired engine | 2010-09-23 | NA | Grace Consulting, Inc. |  |  |  |  | 7E | Nitrogen Oxide | PASS | NA | Y | Tested pollutants:NO2, NO; Permitted Allowable Emission Rate = 1.0 g/hp-hr; Permitted Maximum Operating Rate = 203 Hp; Average Tested Emission Rate = 1.164 g/hp-hr; Average Tested Operating Rate = 203 Hp; Results = Passed; AFS Date = 2011-02-23 00:00:00.0; AFS ID = legacy)
2010 | 9 | 0210000046 | Tennessee Gas Pipeline - Station 214 | 2029 Cobbler Road NE | Carrollton | 44615 | 0000 | Carroll | B002 | 1320 HP (14.52 mmBtu/hr) natural gas-fired, spark ignition, 4-cycle/rich burn, reciprocating pipeline compressor engine with non-selective catalytic reduction | 2010-08-26 | NSCR | Plant Services Dept of Tennessee Gas Pipeline |  |  |  |  | 7E | Nitrogen Oxide | PASS | NA | Y | Tested pollutants:NO2, NO; Permitted Allowable Emission Rate = 2.0 grams/BHP-hr; Permitted Maximum Operating Rate = 1320 HP; Average Tested Emission Rate = 1.25 gram/BHP-hr; Average Tested Operating Rate = 1324 HP; Results = Passed; AFS Date = 2010-11-19 00:00:00.0; AFS ID = legacy) OAC rule 3745-14-12 (NOx SIP call) Catalyst inlet temp was 1079.7¿F Catalyst differential pressure was 3.55" H2O
2010 | 10 | 0250000911 | East Ohio Gas Company - Austintown | 9686 NEW ROAD | Austintown Twp. | 44451 | 9708 | Mahoning | B003 | Natural gas-fired, 4-stroke, lean burn, reciprocating internal combustion engine (Caterpillar G3516TALE) rated at 1,340 HP, 11.9 mmBtu/hr equipped with a selective catalytic reduction system to control carbon monoxide (CO), volatile organic compounds (VOC) and formaldehyde. | 2010-09-28 | Selective catalytic reduction | Grace Consulting, Inc. |  |  |  |  | 7E | Nitrogen Dioxide | PASS | NA | Y | Tested pollutants:NO2, NO; Permitted Allowable Emission Rate = 160 ppmvd @ 15% O2, 2.0 g/HP-hr; Permitted Maximum Operating Rate = 1340 HP; Average Tested Emission Rate = 108.50 ppmvd @ 15% O2, 1.264 g/HPhr; Average Tested Operating Rate = 1270 HP; Results = Passed; AFS Date = 2010-11-19 00:00:00.0; AFS ID = legacy)
2010 | 11 | 0210000046 | Tennessee Gas Pipeline - Station 214 | 2029 Cobbler Road NE | Carrollton | 44615 | 0000 | Carroll | P008 | 1320 HP (14.52 mmBtu/hr) natural gas-fired, spark ignition, 4-cycle/rich burn, reciprocating pipeline compressor engine with non-selective catalytic reduction | 2010-08-25 | NSCR | Plant Services Dept of Tennessee Gas Pipeline |  |  |  |  | 7E | Nitrogen Oxide | PASS | NA | Y | Tested pollutants:NO2, NO; Permitted Allowable Emission Rate = 2.0 grams/BHP-hr; Permitted Maximum Operating Rate = 1320 HP; Average Tested Emission Rate = 1.31 gram/BHP-hr; Average Tested Operating Rate = 1315 HP; Results = Passed; AFS Date = 2010-11-19 00:00:00.0; AFS ID = legacy) OAC rule 3745-14-12 (NOx SIP call) Ave catalyst inlet temp was 1065.0¿F. Ave catalyst differential presssure was 3.83" H2O.
2010 | 12 | 0210000046 | Tennessee Gas Pipeline - Station 214 | 2029 Cobbler Road NE | Carrollton | 44615 | 0000 | Carroll | P006 | 1320 HP (14.52 mmBtu/hr) natural gas-fired, spark ignition, 4-cycle/rich burn, reciprocating pipeline compressor engine with non-selective catalytic reduction | 2010-08-31 | NSCR | Plant Services Dept of Tennessee Gas Pipeline |  |  |  |  | 7E | Nitrogen Oxide | PASS | NA | Y | Tested pollutants:NO2, NO; Permitted Allowable Emission Rate = 2.0 grams/BHP-hr; Permitted Maximum Operating Rate = 1320 HP; Average Tested Emission Rate = 1.34 gram/BHP-hr; Average Tested Operating Rate = 1305 HP; Results = Passed; AFS Date = 2010-11-19 00:00:00.0; AFS ID = legacy) OAC rule 3745-14-12 (NOx SIP call) Ave catalyst inlet temp was 1059.7¿F. Ave catalyst differential pressure was 3.78" H2O.
2010 | 13 | 0661005001 | East Ohio Gas Company - Carlisle Station | 27395 Pump Road Station | Summerfield | 43788 |  | Noble | P001 | Engine #1 - Stationary, simple cycle, natural gas fired engine (Caterpillar G3516TALE, 1,206 hp) equiped with a selective catalytic reduction system | 2010-01-08 | catalytic convertor | Air Compliance Testing, Inc. |  |  |  |  | 7E | Nitrogen Oxide | PASS | NA | Y | Tested pollutants:NO2, NO; Permitted Allowable Emission Rate = 2.0 g/HP-hr, 3.98 lbs/hr, 160 15% O2 ppmvd; Permitted Maximum Operating Rate = 1206 Hp; Average Tested Emission Rate = 1.34 g/HP-hr, 2.02 lbs/hr, 81.0 O2 ppmvd; Average Tested Operating Rate = 685 Hp; Results = Passed; AFS Date = 2010-03-26 00:00:00.0; AFS ID = legacy)
2010 | 16 | 0210000046 | Tennessee Gas Pipeline - Station 214 | 2029 Cobbler Road NE | Carrollton | 44615 | 0000 | Carroll | P007 | 1320 HP (14.52 mmBtu/hr) natural gas-fired, spark ignition, 4-cycle/rich burn, reciprocating pipeline compressor engine with non-selective catalytic reduction | 2010-08-26 | NSCR | Plant Services Dept of Tennessee Gas Pipeline |  |  |  |  | 7E | Nitrogen Dioxide | PASS | NA | Y | Tested pollutants:NO2, NO; Permitted Allowable Emission Rate = 2.0 grams/BHP-hr; Permitted Maximum Operating Rate = 1320 HP; Average Tested Emission Rate = 1.53 gram/BHP-hr; Average Tested Operating Rate = 1304 HP; Results = Passed; AFS Date = 2010-11-19 00:00:00.0; AFS ID = legacy) OAC rule 3745-14-12 (NOx SIP call) Ave catalyst inlet temp was 1069.8¿F. Ave catalyst differential pressure was 3.88" H2O.
2010 | 20 | 0605000020 | Tennessee Gas Pipeline Station 204 | 2335 US Route 50 West | Albany | 45710 | 0000 | Athens | B013 | Recip. Engine 12A - Clark Gas Engine TLA-10 3,400 hp | 2010-08-19 | N/A | El Paso Pipeline Group - Tennessee Gas |  |  |  |  | 7E | Nitrogen Dioxide | PASS | NA | Y | Tested pollutants:NO2, NO; Permitted Allowable Emission Rate = 11.0 grams/bhp-hr; Permitted Maximum Operating Rate = 3400 HP; Average Tested Emission Rate = 3.59 grams/bhp-hr; Average Tested Operating Rate = 3296 HP; Results = Passed; AFS Date = 2010-12-27 00:00:00.0; AFS ID = legacy)
2010 | 22 | 0605000020 | Tennessee Gas Pipeline Station 204 | 2335 US Route 50 West | Albany | 45710 | 0000 | Athens | B012 | Recip. Engine 11A - Clark Gas Engine TLA-10 3,400 hp | 2010-08-19 | N/A | El Paso Pipeline Group - Tennessee Gas |  |  |  |  | 7E | Nitrogen Oxide | PASS | NA | Y | Tested pollutants:NO2, NO; Permitted Allowable Emission Rate = 11.0 grams/bhp-hr; Permitted Maximum Operating Rate = 3400 HP; Average Tested Emission Rate = 7.95grams/bhp-hr; Average Tested Operating Rate = 3390 HP; Results = Passed; AFS Date = 2010-12-27 00:00:00.0; AFS ID = legacy)
2010 | 23 | 0210000046 | Tennessee Gas Pipeline - Station 214 | 2029 Cobbler Road NE | Carrollton | 44615 | 0000 | Carroll | P015 | 2000 HP (22 mmBtu/hr) natural gas-fired, spark ignition, 4-cycle/lean burn, reciprocating pipeline compressor engine | 2010-09-01 | electronic combustion controls | Plant Services Dept of Tennessee Gas Pipeline |  |  |  |  | 7E | Nitrogen Oxide | PASS | NA | Y | Tested pollutants:NO2, NO; Permitted Allowable Emission Rate = 26.5 grams/BHP-hr; Permitted Maximum Operating Rate = 2000 HP; Average Tested Emission Rate = 19.62 grams/BHP-hr; Average Tested Operating Rate = 1936 HP; Results = Passed; AFS Date = 2010-11-19 00:00:00.0; AFS ID = legacy) OAC rule 3745-14-12 (NOx SIP call)
2010 | 24 | 0210000046 | Tennessee Gas Pipeline - Station 214 | 2029 Cobbler Road NE | Carrollton | 44615 | 0000 | Carroll | P016 | 2000 HP (22 mmBtu/hr) natural gas-fired, spark ignition, 4-cycle/lean burn, reciprocating pipeline compressor engine | 2010-08-25 | electronic combustion controls | Plant Services Dept of Tennessee Gas Pipeline |  |  |  |  | 7E | Nitrogen Oxide | PASS | NA | Y | Tested pollutants:NO2, NO; Permitted Allowable Emission Rate = 26.5 grams/BHP-hr; Permitted Maximum Operating Rate = 2000 HP; Average Tested Emission Rate = 19.85 grams/BHP-hr; Average Tested Operating Rate = 2000 HP; Results = Passed; AFS Date = 2010-11-19 00:00:00.0; AFS ID = legacy) OAC rule 3745-14-12 (NOx SIP call)
2010 | 25 | 0210000046 | Tennessee Gas Pipeline - Station 214 | 2029 Cobbler Road NE | Carrollton | 44615 | 0000 | Carroll | P013 | 2000 HP (22 mmBtu/hr) natural gas-fired, spark ignition, 4-cycle/lean burn, reciprocating pipeline compressor engine | 2010-08-25 | electronic combustion controls | Plant Services Dept of Tennessee Gas Pipeline |  |  |  |  | 7E | Nitrogen Dioxide | PASS | NA | Y | Tested pollutants:NO2, NO; Permitted Allowable Emission Rate = 26.5 grams/BHP-hr; Permitted Maximum Operating Rate = 2000 HP; Average Tested Emission Rate = 22.35 grams/BHP-hr; Average Tested Operating Rate = 1990 HP; Results = Passed; AFS Date = 2010-11-19 00:00:00.0; AFS ID = legacy) OAC rule 3745-14-12 (NOx SIP call)
2010 | 26 | 0210000046 | Tennessee Gas Pipeline - Station 214 | 2029 Cobbler Road NE | Carrollton | 44615 | 0000 | Carroll | P014 | 2000 HP (22 mmBtu/hr) natural gas-fired, spark ignition, 4-cycle/lean burn, reciprocating pipeline compressor engine | 2010-08-24 | electronic combustion controls | Plant Services Dept of Tennessee Gas Pipeline |  |  |  |  | 7E | Nitrogen Dioxide | PASS | NA | Y | Tested pollutants:NO2, NO; Permitted Allowable Emission Rate = 26.5 grams/BHP-hr; Permitted Maximum Operating Rate = 2000 HP; Average Tested Emission Rate = 26.38 grams/BHP-hr; Average Tested Operating Rate = 2005 HP; Results = Passed; AFS Date = 2010-11-19 00:00:00.0; AFS ID = legacy) OAC rule 3745-14-12 (NOx SIP call)
2010 | 27 | 0285000366 | East Ohio Gas - Chippewa Station | 17045 Galehouse Road | Doylestown | 44230 |  | Wayne | B010 | 2,370 hp 4SLB SI ICE; CAT G3608 | 2010-07-01 | oxidation catalyst | Environmental Quality Management, Inc. |  |  |  |  | 7E | Nitrogen Dioxide | PASS | NA | Y | Tested pollutants:NO2, NO; Permitted Allowable Emission Rate = 3.66 lbs/hr; Permitted Maximum Operating Rate = 100% ¿10% load; Average Tested Emission Rate = 2.9 lb/hr; Average Tested Operating Rate = 94% load; Results = Passed; AFS Date = 2010-08-31 00:00:00.0; AFS ID = legacy) CMS audit was also conducted. Average temperature was 884¿F. MACT requires temp be maintained between 750¿F and 1250¿F. MACT also requires maintain catalyst so that the pressure drop across the catalyst does not change by more than 2 inches of water at 100% ¿10% load from the pressure drop across the catalyst measured during the initial performance test. The pressure drop across catalyst during this initial test was 1.9 inches water.
2010 | 29 | 0656105002 | East Ohio Gas Company - Woodsfield Station | Bucks Lane | Woodsfield | 43793 |  | Monroe | P002 | 203hp Caterpillar G3306TA natural gas fired engine | 2010-05-27 | NA | Air Compliance Testing |  |  |  |  | 7E | Nitrogen Oxide | INC | NA | N | Tested pollutants:NO2, NO; Permitted Allowable Emission Rate = 2.0 g/hp-hr; Permitted Maximum Operating Rate = 203 Hp; Average Tested Emission Rate = NA; Average Tested Operating Rate = NA; Results = Incomplete; AFS Date = ; AFS ID = ) Engine malfunctioned during the test and it was decided to end testing for the day prior to completing one full run
2010 | 30 | 0857103154 | PINNACLE GAS PRODUCERS LLC | 4220 PINNACLE RD | MORAINE | 45439 |  | Montgomery | B001 | 12 MMBtu/hour (1,626 bhp) pipeline quality gas/natural gas-fired compressor engine | 2010-11-18 | N/A | DERENZO & ASSOCIATES |  |  |  |  | 7E | Nitrogen Dioxide | PASS | NA | Y | Tested pollutants:NO2, NO; Permitted Allowable Emission Rate = 5.37 LB/HR NOX; Permitted Maximum Operating Rate = 1200 RPM; Average Tested Emission Rate = 3.83 LB/HR NOX; Average Tested Operating Rate = 1071 RPM; Results = Passed; AFS Date = 2011-03-23 00:00:00.0; AFS ID = legacy) FACILITY DID FAIL NMOC FROM B001 AND WILL RETET ALL PARAMETERS MARCH 2011.
2011 | 232 | 0210000046 | Tennessee Gas Pipeline - Station 214 | 2029 Cobbler Road NE | Carrollton | 44615 | 0000 | Carroll | P005 | 1320 HP (14.52 mmBtu/hr) natural gas-fired, spark ignition, 4-cycle/rich burn, reciprocating pipeline compressor engine with non-selective catalytic reduction | 2011-08-16 | Catalytic Converter | TGP/El Paso Co. technicians |  |  |  |  | 7E | Nitrogen Oxide | PASS | NA | Y | Tested pollutants: NO2, NO; Permitted Allowable Emission Rate = 2.0 gr/BHP-hr; Permitted Maximum Operating Rate = 1320 BHP; Average Tested Emission Rate = 0.82 gr/BHP-hr; Average Tested Operating Rate = 1159.3 BHP; Results = Passed; AFS Date = 2012-01-04 00:00:00.0; AFS ID = legacy) The NOx emisssions limit is based on the NOx SIP Call Rule.
2011 | 233 | 0210000046 | Tennessee Gas Pipeline - Station 214 | 2029 Cobbler Road NE | Carrollton | 44615 | 0000 | Carroll | P005 | 1320 HP (14.52 mmBtu/hr) natural gas-fired, spark ignition, 4-cycle/rich burn, reciprocating pipeline compressor engine with non-selective catalytic reduction | 2011-08-16 | Catalytic Converter | TGP/El Paso Co. technicians |  |  |  |  | 7E | Nitrogen Dioxide | PASS | NA | Y | Tested pollutants: NO2, NO; Permitted Allowable Emission Rate = 2.0 gr/BHP-hr; Permitted Maximum Operating Rate = 1320 BHP; Average Tested Emission Rate = 0.82 gr/BHP-hr; Average Tested Operating Rate = 1159.3 BHP; Results = Passed; AFS Date = 2012-01-04 00:00:00.0; AFS ID = legacy) The NOx emisssions limit is based on the NOx SIP Call Rule.
2011 | 234 | 0210000046 | Tennessee Gas Pipeline - Station 214 | 2029 Cobbler Road NE | Carrollton | 44615 | 0000 | Carroll | P006 | 1320 HP (14.52 mmBtu/hr) natural gas-fired, spark ignition, 4-cycle/rich burn, reciprocating pipeline compressor engine with non-selective catalytic reduction | 2011-08-16 | Catalytic Converter | TGP/El Paso Co. technicians |  |  |  |  | 7E | Nitrogen Dioxide | PASS | NA | Y | Tested pollutants: NO2, NO; Permitted Allowable Emission Rate = 2.0 gr/BHP-hr; Permitted Maximum Operating Rate = 1320 BHP; Average Tested Emission Rate = 0.78 gr/BHP-hr; Average Tested Operating Rate = 1159.0 BHP; Results = Passed; AFS Date = 2012-01-04 00:00:00.0; AFS ID = legacy) The NOx emisssions limit is based on the NOx SIP Call Rule.
2011 | 235 | 0210000046 | Tennessee Gas Pipeline - Station 214 | 2029 Cobbler Road NE | Carrollton | 44615 | 0000 | Carroll | P006 | 1320 HP (14.52 mmBtu/hr) natural gas-fired, spark ignition, 4-cycle/rich burn, reciprocating pipeline compressor engine with non-selective catalytic reduction | 2011-08-16 | Catalytic Converter | TGP/El Paso Co. technicians |  |  |  |  | 7E | Nitrogen Oxide | PASS | NA | Y | Tested pollutants: NO2, NO; Permitted Allowable Emission Rate = 2.0 gr/BHP-hr; Permitted Maximum Operating Rate = 1320 BHP; Average Tested Emission Rate = 0.78 gr/BHP-hr; Average Tested Operating Rate = 1159.0 BHP; Results = Passed; AFS Date = 2012-01-04 00:00:00.0; AFS ID = legacy) The NOx emisssions limit is based on the NOx SIP Call Rule.
2011 | 236 | 0210000046 | Tennessee Gas Pipeline - Station 214 | 2029 Cobbler Road NE | Carrollton | 44615 | 0000 | Carroll | P007 | 1320 HP (14.52 mmBtu/hr) natural gas-fired, spark ignition, 4-cycle/rich burn, reciprocating pipeline compressor engine with non-selective catalytic reduction | 2011-08-16 | Catalytic Converter | TGP/El Paso Co. technicians |  |  |  |  | 7E | Nitrogen Dioxide | PASS | NA | Y | Tested pollutants: NO2, NO; Permitted Allowable Emission Rate = 2.0 gr/BHP-hr; Permitted Maximum Operating Rate = 1320 BHP; Average Tested Emission Rate = 0.86 gr/BHP-hr; Average Tested Operating Rate = 1197.0 BHP; Results = Passed; AFS Date = 2012-01-04 00:00:00.0; AFS ID = legacy) The NOx emisssions limit is based on the NOx SIP Call Rule.
2011 | 237 | 0210000046 | Tennessee Gas Pipeline - Station 214 | 2029 Cobbler Road NE | Carrollton | 44615 | 0000 | Carroll | P007 | 1320 HP (14.52 mmBtu/hr) natural gas-fired, spark ignition, 4-cycle/rich burn, reciprocating pipeline compressor engine with non-selective catalytic reduction | 2011-08-16 | Catalytic Converter | TGP/El Paso Co. technicians |  |  |  |  | 7E | Nitrogen Oxide | PASS | NA | Y | Tested pollutants: NO2, NO; Permitted Allowable Emission Rate = 2.0 gr/BHP-hr; Permitted Maximum Operating Rate = 1320 BHP; Average Tested Emission Rate = 0.86 gr/BHP-hr; Average Tested Operating Rate = 1197.0 BHP; Results = Passed; AFS Date = 2012-01-04 00:00:00.0; AFS ID = legacy) The NOx emisssions limit is based on the NOx SIP Call Rule.
2011 | 238 | 0210000046 | Tennessee Gas Pipeline - Station 214 | 2029 Cobbler Road NE | Carrollton | 44615 | 0000 | Carroll | P010 | 1320 HP (14.52 mmBtu/hr) natural gas-fired, spark ignition, 4-cycle/rich burn, reciprocating pipeline compressor engine with non-selective catalytic reduction | 2011-08-17 | Catalytic Converter | TGP/El Paso Co. technicians |  |  |  |  | 7E | Nitrogen Dioxide | PASS | NA | Y | Tested pollutants: NO2, NO; Permitted Allowable Emission Rate = 2.0 gr/BHP-hr; Permitted Maximum Operating Rate = 1320 BHP; Average Tested Emission Rate = 1.62 gr/BHP-hr; Average Tested Operating Rate = 1312.3 BHP; Results = Passed; AFS Date = 2012-01-04 00:00:00.0; AFS ID = legacy) The NOx emisssions limit is based on the NOx SIP Call Rule.
2011 | 239 | 0210000046 | Tennessee Gas Pipeline - Station 214 | 2029 Cobbler Road NE | Carrollton | 44615 | 0000 | Carroll | P010 | 1320 HP (14.52 mmBtu/hr) natural gas-fired, spark ignition, 4-cycle/rich burn, reciprocating pipeline compressor engine with non-selective catalytic reduction | 2011-08-17 | Catalytic Converter | TGP/El Paso Co. technicians |  |  |  |  | 7E | Nitrogen Oxide | PASS | NA | Y | Tested pollutants: NO2, NO; Permitted Allowable Emission Rate = 2.0 gr/BHP-hr; Permitted Maximum Operating Rate = 1320 BHP; Average Tested Emission Rate = 1.62 gr/BHP-hr; Average Tested Operating Rate = 1312.3 BHP; Results = Passed; AFS Date = 2012-01-04 00:00:00.0; AFS ID = legacy) The NOx emisssions limit is based on the NOx SIP Call Rule.
2011 | 240 | 0210000046 | Tennessee Gas Pipeline - Station 214 | 2029 Cobbler Road NE | Carrollton | 44615 | 0000 | Carroll | P011 | 1320 HP (14.52 mmBtu/hr) natural gas-fired, spark ignition, 4-cycle/rich burn, reciprocating pipeline compressor engine with non-selective catalytic reduction | 2011-08-17 | Catalytic Converter | TGP/El Paso Co. technicians |  |  |  |  | 7E | Nitrogen Oxide | PASS | NA | Y | Tested pollutants: NO2, NO; Permitted Allowable Emission Rate = 2.0 gr/BHP-hr; Permitted Maximum Operating Rate = 1320 BHP; Average Tested Emission Rate = 1.23 gr/BHP-hr; Average Tested Operating Rate = 1275.7 BHP; Results = Passed; AFS Date = 2012-01-04 00:00:00.0; AFS ID = legacy) The NOx emisssions limit is based on the NOx SIP Call Rule.
2011 | 241 | 0210000046 | Tennessee Gas Pipeline - Station 214 | 2029 Cobbler Road NE | Carrollton | 44615 | 0000 | Carroll | P011 | 1320 HP (14.52 mmBtu/hr) natural gas-fired, spark ignition, 4-cycle/rich burn, reciprocating pipeline compressor engine with non-selective catalytic reduction | 2011-08-17 | Catalytic Converter | TGP/El Paso Co. technicians |  |  |  |  | 7E | Nitrogen Dioxide | PASS | NA | Y | Tested pollutants: NO2, NO; Permitted Allowable Emission Rate = 2.0 gr/BHP-hr; Permitted Maximum Operating Rate = 1320 BHP; Average Tested Emission Rate = 1.23 gr/BHP-hr; Average Tested Operating Rate = 1275.7 BHP; Results = Passed; AFS Date = 2012-01-04 00:00:00.0; AFS ID = legacy) The NOx emisssions limit is based on the NOx SIP Call Rule.
2011 | 242 | 0210000046 | Tennessee Gas Pipeline - Station 214 | 2029 Cobbler Road NE | Carrollton | 44615 | 0000 | Carroll | P013 | 2000 HP (22 mmBtu/hr) natural gas-fired, spark ignition, 4-cycle/lean burn, reciprocating pipeline compressor engine | 2011-08-17 | None | TGP/El Paso Co. technicians |  |  |  |  | 7E | Nitrogen Oxide | PASS | NA | Y | Tested pollutants: NO2, NO; Permitted Allowable Emission Rate = 26.5 gr/BHP-hr; Permitted Maximum Operating Rate = 2,000 BHP; Average Tested Emission Rate = 7.6 gr/BHP-hr; Average Tested Operating Rate = 1746.0 BHP; Results = Passed; AFS Date = 2012-01-04 00:00:00.0; AFS ID = legacy) The NOx emisssions limit is based on the NOx SIP Call Rule.
2011 | 243 | 0210000046 | Tennessee Gas Pipeline - Station 214 | 2029 Cobbler Road NE | Carrollton | 44615 | 0000 | Carroll | P013 | 2000 HP (22 mmBtu/hr) natural gas-fired, spark ignition, 4-cycle/lean burn, reciprocating pipeline compressor engine | 2011-08-17 | None | TGP/El Paso Co. technicians |  |  |  |  | 7E | Nitrogen Dioxide | PASS | NA | Y | Tested pollutants: NO2, NO; Permitted Allowable Emission Rate = 26.5 gr/BHP-hr; Permitted Maximum Operating Rate = 2,000 BHP; Average Tested Emission Rate = 7.6 gr/BHP-hr; Average Tested Operating Rate = 1746.0 BHP; Results = Passed; AFS Date = 2012-01-04 00:00:00.0; AFS ID = legacy) The NOx emisssions limit is based on the NOx SIP Call Rule.
2011 | 244 | 0210000046 | Tennessee Gas Pipeline - Station 214 | 2029 Cobbler Road NE | Carrollton | 44615 | 0000 | Carroll | P014 | 2000 HP (22 mmBtu/hr) natural gas-fired, spark ignition, 4-cycle/lean burn, reciprocating pipeline compressor engine | 2011-08-17 | None | TGP/El Paso Co. technicians |  |  |  |  | 7E | Nitrogen Oxide | PASS | NA | Y | Tested pollutants: NO2, NO; Permitted Allowable Emission Rate = 26.5 gr/BHP-hr; Permitted Maximum Operating Rate = 2,000 BHP; Average Tested Emission Rate = 7.16 gr/BHP-hr; Average Tested Operating Rate = 1746.0 BHP; Results = Passed; AFS Date = 2012-01-04 00:00:00.0; AFS ID = legacy) The NOx emisssions limit is based on the NOx SIP Call Rule.
2011 | 245 | 0210000046 | Tennessee Gas Pipeline - Station 214 | 2029 Cobbler Road NE | Carrollton | 44615 | 0000 | Carroll | P014 | 2000 HP (22 mmBtu/hr) natural gas-fired, spark ignition, 4-cycle/lean burn, reciprocating pipeline compressor engine | 2011-08-17 | None | TGP/El Paso Co. technicians |  |  |  |  | 7E | Nitrogen Dioxide | PASS | NA | Y | Tested pollutants: NO2, NO; Permitted Allowable Emission Rate = 26.5 gr/BHP-hr; Permitted Maximum Operating Rate = 2,000 BHP; Average Tested Emission Rate = 7.16 gr/BHP-hr; Average Tested Operating Rate = 1746.0 BHP; Results = Passed; AFS Date = 2012-01-04 00:00:00.0; AFS ID = legacy) The NOx emisssions limit is based on the NOx SIP Call Rule.
2011 | 246 | 0210000046 | Tennessee Gas Pipeline - Station 214 | 2029 Cobbler Road NE | Carrollton | 44615 | 0000 | Carroll | P012 | 1320 HP (14.52 mmBtu/hr) natural gas-fired, spark ignition, 4-cycle/rich burn, reciprocating pipeline compressor engine with non-selective catalytic reduction | 2011-08-18 | Catalytic Converter | TGP/El Paso Co. technicians |  |  |  |  | 7E | Nitrogen Oxide | PASS | NA | Y | Tested pollutants: NO2, NO; Permitted Allowable Emission Rate = 2.0 gr/BHP-hr; Permitted Maximum Operating Rate = 1320 BHP; Average Tested Emission Rate = 0.74 gr/BHP-hr; Average Tested Operating Rate = 1372.7 BHP; Results = Passed; AFS Date = 2012-01-04 00:00:00.0; AFS ID = legacy) The NOx emisssions limit is based on the NOx SIP Call Rule.
2011 | 247 | 0210000046 | Tennessee Gas Pipeline - Station 214 | 2029 Cobbler Road NE | Carrollton | 44615 | 0000 | Carroll | P012 | 1320 HP (14.52 mmBtu/hr) natural gas-fired, spark ignition, 4-cycle/rich burn, reciprocating pipeline compressor engine with non-selective catalytic reduction | 2011-08-18 | Catalytic Converter | TGP/El Paso Co. technicians |  |  |  |  | 7E | Nitrogen Dioxide | PASS | NA | Y | Tested pollutants: NO2, NO; Permitted Allowable Emission Rate = 2.0 gr/BHP-hr; Permitted Maximum Operating Rate = 1320 BHP; Average Tested Emission Rate = 0.74 gr/BHP-hr; Average Tested Operating Rate = 1372.7 BHP; Results = Passed; AFS Date = 2012-01-04 00:00:00.0; AFS ID = legacy) The NOx emisssions limit is based on the NOx SIP Call Rule.
2011 | 248 | 0210000046 | Tennessee Gas Pipeline - Station 214 | 2029 Cobbler Road NE | Carrollton | 44615 | 0000 | Carroll | P015 | 2000 HP (22 mmBtu/hr) natural gas-fired, spark ignition, 4-cycle/lean burn, reciprocating pipeline compressor engine | 2011-08-18 | None | TGP/El Paso Co. technicians |  |  |  |  | 7E | Nitrogen Dioxide | PASS | NA | Y | Tested pollutants: NO2, NO; Permitted Allowable Emission Rate = 26.5 gr/BHP-hr; Permitted Maximum Operating Rate = 2,000 BHP; Average Tested Emission Rate = 1.28 gr/BHP-hr; Average Tested Operating Rate = 1220.7 BHP; Results = Passed; AFS Date = 2012-01-04 00:00:00.0; AFS ID = legacy) The NOx emisssions limit is based on the NOx SIP Call Rule.
2011 | 249 | 0210000046 | Tennessee Gas Pipeline - Station 214 | 2029 Cobbler Road NE | Carrollton | 44615 | 0000 | Carroll | P015 | 2000 HP (22 mmBtu/hr) natural gas-fired, spark ignition, 4-cycle/lean burn, reciprocating pipeline compressor engine | 2011-08-18 | None | TGP/El Paso Co. technicians |  |  |  |  | 7E | Nitrogen Oxide | PASS | NA | Y | Tested pollutants: NO2, NO; Permitted Allowable Emission Rate = 26.5 gr/BHP-hr; Permitted Maximum Operating Rate = 2,000 BHP; Average Tested Emission Rate = 1.28 gr/BHP-hr; Average Tested Operating Rate = 1220.7 BHP; Results = Passed; AFS Date = 2012-01-04 00:00:00.0; AFS ID = legacy) The NOx emisssions limit is based on the NOx SIP Call Rule.
2011 | 250 | 0210000046 | Tennessee Gas Pipeline - Station 214 | 2029 Cobbler Road NE | Carrollton | 44615 | 0000 | Carroll | P016 | 2000 HP (22 mmBtu/hr) natural gas-fired, spark ignition, 4-cycle/lean burn, reciprocating pipeline compressor engine | 2011-08-18 | None | TGP/El Paso Co. technicians |  |  |  |  | 7E | Nitrogen Dioxide | PASS | NA | Y | Tested pollutants: NO2, NO; Permitted Allowable Emission Rate = 26.5 gr/BHP-hr; Permitted Maximum Operating Rate = 2,000 BHP; Average Tested Emission Rate = 3.56 gr/BHP-hr; Average Tested Operating Rate = 1232.7 BHP; Results = Passed; AFS Date = 2012-01-04 00:00:00.0; AFS ID = legacy) The NOx emisssions limit is based on the NOx SIP Call Rule.
2011 | 251 | 0210000046 | Tennessee Gas Pipeline - Station 214 | 2029 Cobbler Road NE | Carrollton | 44615 | 0000 | Carroll | P016 | 2000 HP (22 mmBtu/hr) natural gas-fired, spark ignition, 4-cycle/lean burn, reciprocating pipeline compressor engine | 2011-08-18 | None | TGP/El Paso Co. technicians |  |  |  |  | 7E | Nitrogen Oxide | PASS | NA | Y | Tested pollutants: NO2, NO; Permitted Allowable Emission Rate = 26.5 gr/BHP-hr; Permitted Maximum Operating Rate = 2,000 BHP; Average Tested Emission Rate = 3.56 gr/BHP-hr; Average Tested Operating Rate = 1232.7 BHP; Results = Passed; AFS Date = 2012-01-04 00:00:00.0; AFS ID = legacy) The NOx emisssions limit is based on the NOx SIP Call Rule.
2011 | 252 | 0210000046 | Tennessee Gas Pipeline - Station 214 | 2029 Cobbler Road NE | Carrollton | 44615 | 0000 | Carroll | B002 | 1320 HP (14.52 mmBtu/hr) natural gas-fired, spark ignition, 4-cycle/rich burn, reciprocating pipeline compressor engine with non-selective catalytic reduction | 2011-09-22 | Catalytic Converter | TGP/El Paso Co. technicians |  |  |  |  | 7E | Nitrogen Dioxide | PASS | NA | Y | Tested pollutants: NO2, NO; Permitted Allowable Emission Rate = 2.0 gr/BHP-hr; Permitted Maximum Operating Rate = 1320 BHP; Average Tested Emission Rate = 1.6 gr/BHP-hr; Average Tested Operating Rate = 1,273.3 BHP; Results = Passed; AFS Date = 2012-01-04 00:00:00.0; AFS ID = legacy) The NOx emisssions limit is based on the NOx SIP Call Rule.
2011 | 253 | 0210000046 | Tennessee Gas Pipeline - Station 214 | 2029 Cobbler Road NE | Carrollton | 44615 | 0000 | Carroll | B002 | 1320 HP (14.52 mmBtu/hr) natural gas-fired, spark ignition, 4-cycle/rich burn, reciprocating pipeline compressor engine with non-selective catalytic reduction | 2011-09-22 | Catalytic Converter | TGP/El Paso Co. technicians |  |  |  |  | 7E | Nitrogen Oxide | PASS | NA | Y | Tested pollutants: NO2, NO; Permitted Allowable Emission Rate = 2.0 gr/BHP-hr; Permitted Maximum Operating Rate = 1320 BHP; Average Tested Emission Rate = 1.6 gr/BHP-hr; Average Tested Operating Rate = 1,273.3 BHP; Results = Passed; AFS Date = 2012-01-04 00:00:00.0; AFS ID = legacy) The NOx emisssions limit is based on the NOx SIP Call Rule.
2011 | 254 | 0210000046 | Tennessee Gas Pipeline - Station 214 | 2029 Cobbler Road NE | Carrollton | 44615 | 0000 | Carroll | P008 | 1320 HP (14.52 mmBtu/hr) natural gas-fired, spark ignition, 4-cycle/rich burn, reciprocating pipeline compressor engine with non-selective catalytic reduction | 2011-09-22 | Catalytic Converter | TGP/El Paso Co. technicians |  |  |  |  | 7E | Nitrogen Dioxide | PASS | NA | Y | Tested pollutants: NO2, NO; Permitted Allowable Emission Rate = 2.0 gr/BHP-hr; Permitted Maximum Operating Rate = 1320 BHP; Average Tested Emission Rate = 1.71 gr/BHP-hr; Average Tested Operating Rate = 1277.0 BHP; Results = Passed; AFS Date = 2012-01-04 00:00:00.0; AFS ID = legacy) The NOx emisssions limit is based on the NOx SIP Call Rule.
2011 | 255 | 0210000046 | Tennessee Gas Pipeline - Station 214 | 2029 Cobbler Road NE | Carrollton | 44615 | 0000 | Carroll | P008 | 1320 HP (14.52 mmBtu/hr) natural gas-fired, spark ignition, 4-cycle/rich burn, reciprocating pipeline compressor engine with non-selective catalytic reduction | 2011-09-22 | Catalytic Converter | TGP/El Paso Co. technicians |  |  |  |  | 7E | Nitrogen Oxide | PASS | NA | Y | Tested pollutants: NO2, NO; Permitted Allowable Emission Rate = 2.0 gr/BHP-hr; Permitted Maximum Operating Rate = 1320 BHP; Average Tested Emission Rate = 1.71 gr/BHP-hr; Average Tested Operating Rate = 1277.0 BHP; Results = Passed; AFS Date = 2012-01-04 00:00:00.0; AFS ID = legacy) The NOx emisssions limit is based on the NOx SIP Call Rule.
2011 | 256 | 0210000046 | Tennessee Gas Pipeline - Station 214 | 2029 Cobbler Road NE | Carrollton | 44615 | 0000 | Carroll | P009 | 1320 HP (14.52 mmBtu/hr) natural gas-fired, spark ignition, 4-cycle/rich burn, reciprocating pipeline compressor engine with non-selective catalytic reduction | 2011-09-22 | Catalytic Converter | TGP/El Paso Co. technicians |  |  |  |  | 7E | Nitrogen Oxide | PASS | NA | Y | Tested pollutants: NO2, NO; Permitted Allowable Emission Rate = 2.0 gr/BHP-hr; Permitted Maximum Operating Rate = 1320 BHP; Average Tested Emission Rate = 1.71 gr/BHP-hr; Average Tested Operating Rate = 1,273.3 BHP; Results = Passed; AFS Date = 2012-01-04 00:00:00.0; AFS ID = legacy) The NOx emisssions limit is based on the NOx SIP Call Rule.
2011 | 257 | 0210000046 | Tennessee Gas Pipeline - Station 214 | 2029 Cobbler Road NE | Carrollton | 44615 | 0000 | Carroll | P009 | 1320 HP (14.52 mmBtu/hr) natural gas-fired, spark ignition, 4-cycle/rich burn, reciprocating pipeline compressor engine with non-selective catalytic reduction | 2011-09-22 | Catalytic Converter | TGP/El Paso Co. technicians |  |  |  |  | 7E | Nitrogen Dioxide | PASS | NA | Y | Tested pollutants: NO2, NO; Permitted Allowable Emission Rate = 2.0 gr/BHP-hr; Permitted Maximum Operating Rate = 1320 BHP; Average Tested Emission Rate = 1.71 gr/BHP-hr; Average Tested Operating Rate = 1,273.3 BHP; Results = Passed; AFS Date = 2012-01-04 00:00:00.0; AFS ID = legacy) The NOx emisssions limit is based on the NOx SIP Call Rule.
2011 | 320 | 0250000911 | East Ohio Gas Company - Austintown | 9686 NEW ROAD | Austintown Twp. | 44451 | 9708 | Mahoning | B003 | Natural gas-fired, 4-stroke, lean burn, reciprocating internal combustion engine (Caterpillar G3516TALE) rated at 1,340 HP, 11.9 mmBtu/hr equipped with a selective catalytic reduction system to control carbon monoxide (CO), volatile organic compounds (VOC) and formaldehyde. | 2011-04-28 | Selective catalytic reduction | Environmental Quality Management, Inc. |  |  |  |  | 7E | Nitrogen Dioxide | PASS | NA | Y | Tested pollutants: NO2, NO; Permitted Allowable Emission Rate = 160 ppmvd @ 15% O2, 2.0 g/HP-hr; Permitted Maximum Operating Rate = 1340 HP; Average Tested Emission Rate = 122.2 ppmvd @ 15% O2, 1.75 g/HPhr; Average Tested Operating Rate = 1270 HP; Results = Passed; AFS Date = 2011-06-27 00:00:00.0; AFS ID = legacy)
2011 | 321 | 0250000911 | East Ohio Gas Company - Austintown | 9686 NEW ROAD | Austintown Twp. | 44451 | 9708 | Mahoning | B003 | Natural gas-fired, 4-stroke, lean burn, reciprocating internal combustion engine (Caterpillar G3516TALE) rated at 1,340 HP, 11.9 mmBtu/hr equipped with a selective catalytic reduction system to control carbon monoxide (CO), volatile organic compounds (VOC) and formaldehyde. | 2011-04-28 | Selective catalytic reduction | Environmental Quality Management, Inc. |  |  |  |  | 7E | Nitrogen Oxide | PASS | NA | Y | Tested pollutants: NO2, NO; Permitted Allowable Emission Rate = 160 ppmvd @ 15% O2, 2.0 g/HP-hr; Permitted Maximum Operating Rate = 1340 HP; Average Tested Emission Rate = 122.2 ppmvd @ 15% O2, 1.75 g/HPhr; Average Tested Operating Rate = 1270 HP; Results = Passed; AFS Date = 2011-06-27 00:00:00.0; AFS ID = legacy)
2011 | 363 | 0285000366 | East Ohio Gas - Chippewa Station | 17045 Galehouse Road | Doylestown | 44230 |  | Wayne | B010 | 2,370 hp 4SLB SI ICE; CAT G3608 | 2011-06-28 | oxidation catalyst | Environmental Quality Management, Inc. |  |  |  |  | 7E | Nitrogen Dioxide | PASS | NA | Y | Tested pollutants: NO2, NO; Permitted Allowable Emission Rate = 3.66 lbs/hr; Permitted Maximum Operating Rate = 100% ¿10% load; Average Tested Emission Rate = 3.54 lb/hr; Average Tested Operating Rate = 100% +/- 10% load rating; Results = Passed; AFS Date = 2012-01-04 00:00:00.0; AFS ID = legacy)
2011 | 364 | 0285000366 | East Ohio Gas - Chippewa Station | 17045 Galehouse Road | Doylestown | 44230 |  | Wayne | B010 | 2,370 hp 4SLB SI ICE; CAT G3608 | 2011-06-28 | oxidation catalyst | Environmental Quality Management, Inc. |  |  |  |  | 7E | Nitrogen Oxide | PASS | NA | Y | Tested pollutants: NO2, NO; Permitted Allowable Emission Rate = 3.66 lbs/hr; Permitted Maximum Operating Rate = 100% ¿10% load; Average Tested Emission Rate = 3.54 lb/hr; Average Tested Operating Rate = 100% +/- 10% load rating; Results = Passed; AFS Date = 2012-01-04 00:00:00.0; AFS ID = legacy)
2011 | 705 | 0605000020 | Tennessee Gas Pipeline Station 204 | 2335 US Route 50 West | Albany | 45710 | 0000 | Athens | B012 | Recip. Engine 11A - Clark Gas Engine TLA-10 3,400 hp | 2011-08-23 | N/A | El Paso Pipeline Group - Tennessee Gas |  |  |  |  | 7E | Nitrogen Dioxide | INVALID | NA | Y | Tested pollutants: NO2, NO; Permitted Allowable Emission Rate = 11.0 grams/bhp-hr; Permitted Maximum Operating Rate = 3400 HP; Average Tested Emission Rate = 5.26 grams/bhp-hr; Average Tested Operating Rate = 3177 HP; Results = Invalid; AFS Date = ; AFS ID = ) Failed to conduct linearity and stability checks
2011 | 706 | 0605000020 | Tennessee Gas Pipeline Station 204 | 2335 US Route 50 West | Albany | 45710 | 0000 | Athens | B012 | Recip. Engine 11A - Clark Gas Engine TLA-10 3,400 hp | 2011-08-23 | N/A | El Paso Pipeline Group - Tennessee Gas |  |  |  |  | 7E | Nitrogen Oxide | INVALID | NA | Y | Tested pollutants: NO2, NO; Permitted Allowable Emission Rate = 11.0 grams/bhp-hr; Permitted Maximum Operating Rate = 3400 HP; Average Tested Emission Rate = 5.26 grams/bhp-hr; Average Tested Operating Rate = 3177 HP; Results = Invalid; AFS Date = ; AFS ID = ) Failed to conduct linearity and stability checks
2011 | 707 | 0605000020 | Tennessee Gas Pipeline Station 204 | 2335 US Route 50 West | Albany | 45710 | 0000 | Athens | B013 | Recip. Engine 12A - Clark Gas Engine TLA-10 3,400 hp | 2011-08-23 | N/A | El Paso Pipeline Group - Tennessee Gas |  |  |  |  | 7E | Nitrogen Oxide | INVALID | NA | Y | Tested pollutants: NO2, NO; Permitted Allowable Emission Rate = 11.0 grams/bhp-hr; Permitted Maximum Operating Rate = 3400 HP; Average Tested Emission Rate = 2.04 grams/bhp-hr; Average Tested Operating Rate = 3104 HP; Results = Invalid; AFS Date = ; AFS ID = ) Failed to conduct linearity and stability checks
2011 | 708 | 0605000020 | Tennessee Gas Pipeline Station 204 | 2335 US Route 50 West | Albany | 45710 | 0000 | Athens | B013 | Recip. Engine 12A - Clark Gas Engine TLA-10 3,400 hp | 2011-08-23 | N/A | El Paso Pipeline Group - Tennessee Gas |  |  |  |  | 7E | Nitrogen Dioxide | INVALID | NA | Y | Tested pollutants: NO2, NO; Permitted Allowable Emission Rate = 11.0 grams/bhp-hr; Permitted Maximum Operating Rate = 3400 HP; Average Tested Emission Rate = 2.04 grams/bhp-hr; Average Tested Operating Rate = 3104 HP; Results = Invalid; AFS Date = ; AFS ID = ) Failed to conduct linearity and stability checks
2011 | 709 | 0605000020 | Tennessee Gas Pipeline Station 204 | 2335 US Route 50 West | Albany | 45710 | 0000 | Athens | B012 | Recip. Engine 11A - Clark Gas Engine TLA-10 3,400 hp | 2011-09-21 | N/A | El Paso Pipeline Group - Tennessee Gas |  |  |  |  | 7E | Nitrogen Oxide | PASS | NA | Y | Tested pollutants: NO2, NO; Permitted Allowable Emission Rate = 11.0 grams/bhp-hr; Permitted Maximum Operating Rate = 3400 HP; Average Tested Emission Rate = 5.26 grams/bhp-hr; Average Tested Operating Rate = 3177 HP; Results = Passed; AFS Date = 2011-10-27 00:00:00.0; AFS ID = legacy) verified previous invalid test results
2011 | 710 | 0605000020 | Tennessee Gas Pipeline Station 204 | 2335 US Route 50 West | Albany | 45710 | 0000 | Athens | B012 | Recip. Engine 11A - Clark Gas Engine TLA-10 3,400 hp | 2011-09-21 | N/A | El Paso Pipeline Group - Tennessee Gas |  |  |  |  | 7E | Nitrogen Dioxide | PASS | NA | Y | Tested pollutants: NO2, NO; Permitted Allowable Emission Rate = 11.0 grams/bhp-hr; Permitted Maximum Operating Rate = 3400 HP; Average Tested Emission Rate = 5.26 grams/bhp-hr; Average Tested Operating Rate = 3177 HP; Results = Passed; AFS Date = 2011-10-27 00:00:00.0; AFS ID = legacy) verified previous invalid test results
2011 | 769 | 0661005002 | Summerfield Compressor Station | between CR-45 and HWY 233 | Caldwell | 43724 |  | Noble | P001 | Natural Gas Engine(1) 1,380 hp engine | 2011-03-29 | Catalytic Silencer | BCMJ Controls |  |  |  |  | 7E | Nitrogen Oxide | PASS | NA | Y | Tested pollutants: NO2, NO; Permitted Allowable Emission Rate = 1.0 g/Hp-hr, 82 -15% O2 ppmvd; Permitted Maximum Operating Rate = 1,380 Hp; Average Tested Emission Rate = 0.83 g/Hp-hr, 45.7 - 15% O2 ppmvd; Average Tested Operating Rate = 1,104 Hp; Results = Passed; AFS Date = 2011-08-26 00:00:00.0; AFS ID = legacy)
2011 | 771 | 0661005002 | Summerfield Compressor Station | between CR-45 and HWY 233 | Caldwell | 43724 |  | Noble | P001 | Natural Gas Engine(1) 1,380 hp engine | 2011-03-29 | Catalytic Silencer | BCMJ Controls |  |  |  |  | 7E | Nitrogen Dioxide | PASS | NA | Y | Tested pollutants: NO2, NO; Permitted Allowable Emission Rate = 1.0 g/Hp-hr, 82 -15% O2 ppmvd; Permitted Maximum Operating Rate = 1,380 Hp; Average Tested Emission Rate = 0.83 g/Hp-hr, 45.7 - 15% O2 ppmvd; Average Tested Operating Rate = 1,104 Hp; Results = Passed; AFS Date = 2011-08-26 00:00:00.0; AFS ID = legacy)
2011 | 774 | 0661005002 | Summerfield Compressor Station | between CR-45 and HWY 233 | Caldwell | 43724 |  | Noble | P002 | Natural Gas Engine (2) 1,380 hp | 2011-03-29 | Catalytic Silencer | BCMJ Controls |  |  |  |  | 7E | Nitrogen Oxide | PASS | NA | Y | Tested pollutants: NO2, NO; Permitted Allowable Emission Rate = 1.0 g/Hp-hr, 82 -15% O2 ppmvd; Permitted Maximum Operating Rate = 1,380 Hp; Average Tested Emission Rate = 0.98 g/Hp-hr, 52.2 - 15% O2 ppmvd; Average Tested Operating Rate = 1,104 Hp; Results = Passed; AFS Date = 2011-08-26 00:00:00.0; AFS ID = legacy)
2011 | 775 | 0661005002 | Summerfield Compressor Station | between CR-45 and HWY 233 | Caldwell | 43724 |  | Noble | P002 | Natural Gas Engine (2) 1,380 hp | 2011-03-29 | Catalytic Silencer | BCMJ Controls |  |  |  |  | 7E | Nitrogen Dioxide | PASS | NA | Y | Tested pollutants: NO2, NO; Permitted Allowable Emission Rate = 1.0 g/Hp-hr, 82 -15% O2 ppmvd; Permitted Maximum Operating Rate = 1,380 Hp; Average Tested Emission Rate = 0.98 g/Hp-hr, 52.2 - 15% O2 ppmvd; Average Tested Operating Rate = 1,104 Hp; Results = Passed; AFS Date = 2011-08-26 00:00:00.0; AFS ID = legacy)
2011 | 965 | 0857103154 | PINNACLE GAS PRODUCERS LLC | 4220 PINNACLE RD | MORAINE | 45439 |  | Montgomery | B001 | 12 MMBtu/hour (1,626 bhp) pipeline quality gas/natural gas-fired compressor engine | 2011-03-10 | N/A | DTE ENERGY |  |  |  |  | 7E | Nitrogen Oxide | PASS | NA | Y | Tested pollutants: NO2, NO; Permitted Allowable Emission Rate = 5.37 LB/HR NOX; Permitted Maximum Operating Rate = 1200 RPM; Average Tested Emission Rate = 3.47 LB/RH NOX; Average Tested Operating Rate = 1017 RPM; Results = Passed; AFS Date = 2011-06-27 00:00:00.0; AFS ID = legacy)
2011 | 966 | 0857103154 | PINNACLE GAS PRODUCERS LLC | 4220 PINNACLE RD | MORAINE | 45439 |  | Montgomery | B001 | 12 MMBtu/hour (1,626 bhp) pipeline quality gas/natural gas-fired compressor engine | 2011-03-10 | N/A | DTE ENERGY |  |  |  |  | 7E | Nitrogen Dioxide | PASS | NA | Y | Tested pollutants: NO2, NO; Permitted Allowable Emission Rate = 5.37 LB/HR NOX; Permitted Maximum Operating Rate = 1200 RPM; Average Tested Emission Rate = 3.47 LB/RH NOX; Average Tested Operating Rate = 1017 RPM; Results = Passed; AFS Date = 2011-06-27 00:00:00.0; AFS ID = legacy)
2011 | 1178 | 1576002033 | East Ohio Gas - Pike Compressor Station | 6024 Kieffer Ave., SW | Canton | 44706 |  | Stark | P001 | Caterpillar G3516-LE-AFR, 1340 hp, 9.9 mmbtu/hr capacity, natural gas fired engine. | 2011-07-08 | CAT-OX | Environmental Quality Management Inc. |  |  |  |  | 7E | Nitrogen Oxide | PASS | NA | Y | Tested pollutants: NO2, NO; Permitted Allowable Emission Rate = 4.43 lbs NOx/hr; Permitted Maximum Operating Rate = 1340 bhp; Average Tested Emission Rate = 4.03 lbs NOx/hr; Average Tested Operating Rate = 80.1, 93.2 & 92.0% max load; Results = Passed; AFS Date = 2011-08-26 00:00:00.0; AFS ID = legacy) Observed 90.9% of NOx limit
2011 | 1180 | 1576002033 | East Ohio Gas - Pike Compressor Station | 6024 Kieffer Ave., SW | Canton | 44706 |  | Stark | P001 | Caterpillar G3516-LE-AFR, 1340 hp, 9.9 mmbtu/hr capacity, natural gas fired engine. | 2011-07-08 | CAT-OX | Environmental Quality Management Inc. |  |  |  |  | 7E | Nitrogen Dioxide | PASS | NA | Y | Tested pollutants: NO2, NO; Permitted Allowable Emission Rate = 4.43 lbs NOx/hr; Permitted Maximum Operating Rate = 1340 bhp; Average Tested Emission Rate = 4.03 lbs NOx/hr; Average Tested Operating Rate = 80.1, 93.2 & 92.0% max load; Results = Passed; AFS Date = 2011-08-26 00:00:00.0; AFS ID = legacy) Observed 90.9% of NOx limit
2011 | 1181 | 1576002033 | East Ohio Gas - Pike Compressor Station | 6024 Kieffer Ave., SW | Canton | 44706 |  | Stark | P002 | Caterpillar G3516-LE-AFR, 1,340 hp, 9.9 mmbtu/hr capacity natural gas fired engine. | 2011-07-08 | CAT-OX | Environmental Quality Management Inc. |  |  |  |  | 7E | Nitrogen Oxide | PASS | NA | Y | Tested pollutants: NO2, NO; Permitted Allowable Emission Rate = 4.43 lbs NOx/hr; Permitted Maximum Operating Rate = 1340 bhp; Average Tested Emission Rate = 4.17 lbs NOx/hr; Average Tested Operating Rate = 94.5, 97.5 & 85.5% max load; Results = Passed; AFS Date = 2011-08-26 00:00:00.0; AFS ID = legacy) Observed 94.1% of NOx limit
2011 | 1183 | 1576002033 | East Ohio Gas - Pike Compressor Station | 6024 Kieffer Ave., SW | Canton | 44706 |  | Stark | P002 | Caterpillar G3516-LE-AFR, 1,340 hp, 9.9 mmbtu/hr capacity natural gas fired engine. | 2011-07-08 | CAT-OX | Environmental Quality Management Inc. |  |  |  |  | 7E | Nitrogen Dioxide | PASS | NA | Y | Tested pollutants: NO2, NO; Permitted Allowable Emission Rate = 4.43 lbs NOx/hr; Permitted Maximum Operating Rate = 1340 bhp; Average Tested Emission Rate = 4.17 lbs NOx/hr; Average Tested Operating Rate = 94.5, 97.5 & 85.5% max load; Results = Passed; AFS Date = 2011-08-26 00:00:00.0; AFS ID = legacy) Observed 94.1% of NOx limit
2012 | 273 | 0210012015 | Chesapeake Exploration LLC - Snoddy 11-13-5 Pad | Sorrel Road (TWP HWY 620) | Carrollton | 44615 |  | Carroll | P002 | Flash gas compressor with catalyst, 211 hp SI ICE | 2012-10-03 | Catalyst | Alliance Source Testing. | 211 hp | 160 oomvd@15% O2 | 116 hp | 40.7 ppmvd @ 15% O2 | 7E | Nitrogen Oxide | PASS | NA | Y
2012 | 294 | 0238000050 | MILEY COMPRESSOR STATION | 7531 State Rte 514 | Ripley Twp. | 44611 |  | Holmes | B003 | White Superior 8G-825, 4-cycle, rich burn, natural gas-fired reciprocating pipeline compressor engine, having a maximum capacity of 780hp, controlled by a Non-Selectivie Catalytic Reduction. (Compressor #07701 - B003) | 2012-05-10 | TWC | Windrock Environmental |  |  |  |  | 7E | Nitrogen Oxide | PASS | NA | Y | Tested pollutants: NO2, NO; Permitted Allowable Emission Rate = 29 tpy rolling; Permitted Maximum Operating Rate = 780 hp; Average Tested Emission Rate = 2.19 tpy; Average Tested Operating Rate = >702 hp; Results = Passed; AFS Date = 2012-09-27 00:00:00.0; AFS ID = legacy)
2012 | 296 | 0238000050 | MILEY COMPRESSOR STATION | 7531 State Rte 514 | Ripley Twp. | 44611 |  | Holmes | B003 | White Superior 8G-825, 4-cycle, rich burn, natural gas-fired reciprocating pipeline compressor engine, having a maximum capacity of 780hp, controlled by a Non-Selectivie Catalytic Reduction. (Compressor #07701 - B003) | 2012-05-10 | TWC | Windrock Environmental |  |  |  |  | 7E | Nitrogen Dioxide | PASS | NA | Y | Tested pollutants: NO2, NO; Permitted Allowable Emission Rate = 29 tpy rolling; Permitted Maximum Operating Rate = 780 hp; Average Tested Emission Rate = 2.19 tpy; Average Tested Operating Rate = >702 hp; Results = Passed; AFS Date = 2012-09-27 00:00:00.0; AFS ID = legacy)
2012 | 297 | 0238000050 | MILEY COMPRESSOR STATION | 7531 State Rte 514 | Ripley Twp. | 44611 |  | Holmes | B004 | White Superior 8G-825, 4-cycle, rich burn, natural gas-fired reciprocating pipeline compressor engine, having a maximum capacity of 780hp, controlled by a Non-Selective Catalytic Reduction. (Compressor #07702 - B004) | 2012-05-10 | TWC | Windrock Environmental |  |  |  |  | 7E | Nitrogen Dioxide | PASS | NA | Y | Tested pollutants: NO2, NO; Permitted Allowable Emission Rate = 29 tpy rolling; Permitted Maximum Operating Rate = 780 hp; Average Tested Emission Rate = .39 tpy; Average Tested Operating Rate = >702 hp; Results = Passed; AFS Date = 2012-09-27 00:00:00.0; AFS ID = legacy)
2012 | 299 | 0238000050 | MILEY COMPRESSOR STATION | 7531 State Rte 514 | Ripley Twp. | 44611 |  | Holmes | B004 | White Superior 8G-825, 4-cycle, rich burn, natural gas-fired reciprocating pipeline compressor engine, having a maximum capacity of 780hp, controlled by a Non-Selective Catalytic Reduction. (Compressor #07702 - B004) | 2012-05-10 | TWC | Windrock Environmental |  |  |  |  | 7E | Nitrogen Oxide | PASS | NA | Y | Tested pollutants: NO2, NO; Permitted Allowable Emission Rate = 29 tpy rolling; Permitted Maximum Operating Rate = 780 hp; Average Tested Emission Rate = .39 tpy; Average Tested Operating Rate = >702 hp; Results = Passed; AFS Date = 2012-09-27 00:00:00.0; AFS ID = legacy)
2012 | 321 | 0250000911 | East Ohio Gas Company - Austintown | 9686 NEW ROAD | Austintown Twp. | 44451 | 9708 | Mahoning | B003 | Natural gas-fired, 4-stroke, lean burn, reciprocating internal combustion engine (Caterpillar G3516TALE) rated at 1,340 HP, 11.9 mmBtu/hr equipped with a selective catalytic reduction system to control carbon monoxide (CO), volatile organic compounds (VOC) and formaldehyde. | 2012-03-19 | Selective catalytic reduction | Environmental Quality Management, Inc. |  |  |  |  | 7E | Nitrogen Dioxide | PASS | NA | Y | Tested pollutants: NO2, NO; Permitted Allowable Emission Rate = 160 ppmvd @ 15% O2, 2.0 g/HP-hr; Permitted Maximum Operating Rate = 1340 HP; Average Tested Emission Rate = 116.5 ppmvd @ 15% O2, 1.72 g/HPhr; Average Tested Operating Rate = 1264 HP; Results = Passed; AFS Date = 2013-01-22 00:00:00.0; AFS ID = legacy)
2012 | 322 | 0250000911 | East Ohio Gas Company - Austintown | 9686 NEW ROAD | Austintown Twp. | 44451 | 9708 | Mahoning | B003 | Natural gas-fired, 4-stroke, lean burn, reciprocating internal combustion engine (Caterpillar G3516TALE) rated at 1,340 HP, 11.9 mmBtu/hr equipped with a selective catalytic reduction system to control carbon monoxide (CO), volatile organic compounds (VOC) and formaldehyde. | 2012-03-19 | Selective catalytic reduction | Environmental Quality Management, Inc. |  |  |  |  | 7E | Nitrogen Oxide | PASS | NA | Y | Tested pollutants: NO2, NO; Permitted Allowable Emission Rate = 160 ppmvd @ 15% O2, 2.0 g/HP-hr; Permitted Maximum Operating Rate = 1340 HP; Average Tested Emission Rate = 116.5 ppmvd @ 15% O2, 1.72 g/HPhr; Average Tested Operating Rate = 1264 HP; Results = Passed; AFS Date = 2013-01-22 00:00:00.0; AFS ID = legacy)
2012 | 336 | 0250092002 | City of Struthers WWTP | 530 Lowellville Road | Struthers | 44471 |  | Mahoning | P001 | Stationary internal combustion engine | 2012-01-27 | None | Custom Stack Analysis, LLC |  |  |  |  | 7E | Nitrogen Oxide | PASS | NA | Y | Tested pollutants: NO2, NO; Permitted Allowable Emission Rate = 3.0 g/HP-hr, 220 ppmvd at 15% O2; Permitted Maximum Operating Rate = 585 HP; Average Tested Emission Rate = 0.24 g/HP-hr, 13.23 ppm at 15% O2; Average Tested Operating Rate = 247 HP; Results = Passed; AFS Date = 2013-01-22 00:00:00.0; AFS ID = legacy)
2012 | 337 | 0250092002 | City of Struthers WWTP | 530 Lowellville Road | Struthers | 44471 |  | Mahoning | P001 | Stationary internal combustion engine | 2012-01-27 | None | Custom Stack Analysis, LLC |  |  |  |  | 7E | Nitrogen Dioxide | PASS | NA | Y | Tested pollutants: NO2, NO; Permitted Allowable Emission Rate = 3.0 g/HP-hr, 220 ppmvd at 15% O2; Permitted Maximum Operating Rate = 585 HP; Average Tested Emission Rate = 0.24 g/HP-hr, 13.23 ppm at 15% O2; Average Tested Operating Rate = 247 HP; Results = Passed; AFS Date = 2013-01-22 00:00:00.0; AFS ID = legacy)
2012 | 340 | 0250092002 | City of Struthers WWTP | 530 Lowellville Road | Struthers | 44471 |  | Mahoning | P002 | Waukesha H24GLD Engine | 2012-01-30 | None | Custom Stack Analysis, LLC |  |  |  |  | 7E | Nitrogen Dioxide | PASS | NA | Y | Tested pollutants: NO2, NO; Permitted Allowable Emission Rate = 3.0 g/HP-hr, 220 ppmvd at 15% O2; Permitted Maximum Operating Rate = 585 HP; Average Tested Emission Rate = 0.40 g/HP-hr, 21.9 ppm at 15% O2; Average Tested Operating Rate = 247 HP; Results = Passed; AFS Date = 2013-01-22 00:00:00.0; AFS ID = legacy)
2012 | 341 | 0250092002 | City of Struthers WWTP | 530 Lowellville Road | Struthers | 44471 |  | Mahoning | P002 | Waukesha H24GLD Engine | 2012-01-30 | None | Custom Stack Analysis, LLC |  |  |  |  | 7E | Nitrogen Oxide | PASS | NA | Y | Tested pollutants: NO2, NO; Permitted Allowable Emission Rate = 3.0 g/HP-hr, 220 ppmvd at 15% O2; Permitted Maximum Operating Rate = 585 HP; Average Tested Emission Rate = 0.40 g/HP-hr, 21.9 ppm at 15% O2; Average Tested Operating Rate = 247 HP; Results = Passed; AFS Date = 2013-01-22 00:00:00.0; AFS ID = legacy)
2012 | 365 | 0285000366 | East Ohio Gas - Chippewa Station | 17045 Galehouse Road | Doylestown | 44230 |  | Wayne | B010 | 2,370 hp 4SLB SI ICE; CAT G3608 | 2012-06-12 | oxidation catalyst | Environmental Quality Management, Inc. |  |  |  |  | 7E | Nitrogen Dioxide | PASS | NA | Y | Tested pollutants: NO2, NO; Permitted Allowable Emission Rate = 2.0 grams/hp-hr; Permitted Maximum Operating Rate = 100% ¿10% load; Average Tested Emission Rate = .92 grams hp/hr; Average Tested Operating Rate = 100% +/- 10% load rating; Results = Passed; AFS Date = 2012-09-27 00:00:00.0; AFS ID = legacy)
2012 | 366 | 0285000366 | East Ohio Gas - Chippewa Station | 17045 Galehouse Road | Doylestown | 44230 |  | Wayne | B010 | 2,370 hp 4SLB SI ICE; CAT G3608 | 2012-06-12 | oxidation catalyst | Environmental Quality Management, Inc. |  |  |  |  | 7E | Nitrogen Oxide | PASS | NA | Y | Tested pollutants: NO2, NO; Permitted Allowable Emission Rate = 2.0 grams/hp-hr; Permitted Maximum Operating Rate = 100% ¿10% load; Average Tested Emission Rate = .92 grams hp/hr; Average Tested Operating Rate = 100% +/- 10% load rating; Results = Passed; AFS Date = 2012-09-27 00:00:00.0; AFS ID = legacy)
2012 | 368 | 0285000388 | East Ohio Gas Company - Paint | STATE RTE 250 | Wooster | 44624 |  | Wayne | B002 | Natural gas fired Internal Combustion Engine with max input capacity of 11.9 MMBtu/hr - Caterpillar G3516TALE with 1340 HP, 4-stroke, selective catalytic reduction (SCR) | 2012-08-29 | Three way Catalyst | Environmental Quality Management |  |  |  |  | 7E | Nitrogen Dioxide | PASS | NA | Y | Tested pollutants: NO2, NO; Permitted Allowable Emission Rate = 160 ppm @ 15% O2 and 2.0 g/hp-hr; Permitted Maximum Operating Rate = 1340 HP; Average Tested Emission Rate = 119.4 ppm @ 15% O2 and 1.62 g/hp-hr; Average Tested Operating Rate = 1233 HP-hr; Results = Passed; AFS Date = 2012-11-30 00:00:00.0; AFS ID = legacy)
2012 | 371 | 0285000388 | East Ohio Gas Company - Paint | STATE RTE 250 | Wooster | 44624 |  | Wayne | B002 | Natural gas fired Internal Combustion Engine with max input capacity of 11.9 MMBtu/hr - Caterpillar G3516TALE with 1340 HP, 4-stroke, selective catalytic reduction (SCR) | 2012-08-29 | Three way Catalyst | Environmental Quality Management |  |  |  |  | 7E | Nitrogen Oxide | PASS | NA | Y | Tested pollutants: NO2, NO; Permitted Allowable Emission Rate = 160 ppm @ 15% O2 and 2.0 g/hp-hr; Permitted Maximum Operating Rate = 1340 HP; Average Tested Emission Rate = 119.4 ppm @ 15% O2 and 1.62 g/hp-hr; Average Tested Operating Rate = 1233 HP-hr; Results = Passed; AFS Date = 2012-11-30 00:00:00.0; AFS ID = legacy)
2012 | 372 | 0285000421 | PIONEER EQUIPMENT, INC. | 16875 JERICHO RD. | DALTON | 44618 |  | Wayne | P004 | Stationary natural gas, spark ignition (SI) internal combustion engine (ICE); 440 horsepower (hp), used as primary power source | 2012-10-05 | None | Custom Stack Analysis |  |  |  |  | 7E | Nitrogen Dioxide | PASS | NA | Y | Tested pollutants: NO2, NO; Permitted Allowable Emission Rate = 250 ppm @15%O2 or 3.0 g/hp-hr; Permitted Maximum Operating Rate = 440 Hp; Average Tested Emission Rate = 242.35 and 1.54; Average Tested Operating Rate = 340 HP; Results = Passed; AFS Date = 2012-12-31 00:00:00.0; AFS ID = legacy) The Tested average emission rate comes from only runs two and three. Run one was omittted from the average because of an adjustment made after the test run was completed.
2012 | 375 | 0285000421 | PIONEER EQUIPMENT, INC. | 16875 JERICHO RD. | DALTON | 44618 |  | Wayne | P004 | Stationary natural gas, spark ignition (SI) internal combustion engine (ICE); 440 horsepower (hp), used as primary power source | 2012-10-05 | None | Custom Stack Analysis |  |  |  |  | 7E | Nitrogen Oxide | PASS | NA | Y | Tested pollutants: NO2, NO; Permitted Allowable Emission Rate = 250 ppm @15%O2 or 3.0 g/hp-hr; Permitted Maximum Operating Rate = 440 Hp; Average Tested Emission Rate = 242.35 and 1.54; Average Tested Operating Rate = 340 HP; Results = Passed; AFS Date = 2012-12-31 00:00:00.0; AFS ID = legacy) The Tested average emission rate comes from only runs two and three. Run one was omittted from the average because of an adjustment made after the test run was completed.
2012 | 628 | 0605000020 | Tennessee Gas Pipeline Station 204 | 2335 US Route 50 West | Albany | 45710 | 0000 | Athens | B012 | Recip. Engine 11A - Clark Gas Engine TLA-10 3,400 hp | 2012-06-14 | N/A | El Paso Pipeline Group - Tennessee Gas |  |  |  |  | 7E | Nitrogen Dioxide | PASS | NA | Y | Tested pollutants: NO2, NO; Permitted Allowable Emission Rate = 11.0 grams/bhp-hr; Permitted Maximum Operating Rate = 3,400 HP; Average Tested Emission Rate = 4.3 grams/bhp-hr; Average Tested Operating Rate = 3,346 HP; Results = Passed; AFS Date = 2012-09-27 00:00:00.0; AFS ID = legacy)
2012 | 629 | 0605000020 | Tennessee Gas Pipeline Station 204 | 2335 US Route 50 West | Albany | 45710 | 0000 | Athens | B012 | Recip. Engine 11A - Clark Gas Engine TLA-10 3,400 hp | 2012-06-14 | N/A | El Paso Pipeline Group - Tennessee Gas |  |  |  |  | 7E | Nitrogen Oxide | PASS | NA | Y | Tested pollutants: NO2, NO; Permitted Allowable Emission Rate = 11.0 grams/bhp-hr; Permitted Maximum Operating Rate = 3,400 HP; Average Tested Emission Rate = 4.3 grams/bhp-hr; Average Tested Operating Rate = 3,346 HP; Results = Passed; AFS Date = 2012-09-27 00:00:00.0; AFS ID = legacy)
2012 | 630 | 0605000020 | Tennessee Gas Pipeline Station 204 | 2335 US Route 50 West | Albany | 45710 | 0000 | Athens | B013 | Recip. Engine 12A - Clark Gas Engine TLA-10 3,400 hp | 2012-06-14 | N/A | El Paso Pipeline Group - Tennessee Gas |  |  |  |  | 7E | Nitrogen Oxide | PASS | NA | Y | Tested pollutants: NO2, NO; Permitted Allowable Emission Rate = 11.0 grams/bhp-hr; Permitted Maximum Operating Rate = 3,400 HP; Average Tested Emission Rate = 3.98 grams/bhp-hr; Average Tested Operating Rate = 3,345 HP; Results = Passed; AFS Date = 2012-09-27 00:00:00.0; AFS ID = legacy)
2012 | 631 | 0605000020 | Tennessee Gas Pipeline Station 204 | 2335 US Route 50 West | Albany | 45710 | 0000 | Athens | B013 | Recip. Engine 12A - Clark Gas Engine TLA-10 3,400 hp | 2012-06-14 | N/A | El Paso Pipeline Group - Tennessee Gas |  |  |  |  | 7E | Nitrogen Dioxide | PASS | NA | Y | Tested pollutants: NO2, NO; Permitted Allowable Emission Rate = 11.0 grams/bhp-hr; Permitted Maximum Operating Rate = 3,400 HP; Average Tested Emission Rate = 3.98 grams/bhp-hr; Average Tested Operating Rate = 3,345 HP; Results = Passed; AFS Date = 2012-09-27 00:00:00.0; AFS ID = legacy)
2012 | 728 | 0661005002 | Summerfield Compressor Station | between CR-45 and HWY 233 | Caldwell | 43724 |  | Noble | P001 | Natural Gas Engine(1) 1,380 hp engine | 2012-03-12 | Catalytic Silencer | BCMJ Controls |  |  |  |  | 7E | Nitrogen Dioxide | PASS | NA | Y | Tested pollutants: NO2, NO; Permitted Allowable Emission Rate = 1.0 g/Hp-hr, 82 -15% O2 ppmvd; Permitted Maximum Operating Rate = 1,380 Hp; Average Tested Emission Rate = 0.66 g/Hp-hr, 37.9 - 15% O2 ppmvd; Average Tested Operating Rate = 1,104 Hp; Results = Passed; AFS Date = 2012-08-01 00:00:00.0; AFS ID = legacy)
2012 | 731 | 0661005002 | Summerfield Compressor Station | between CR-45 and HWY 233 | Caldwell | 43724 |  | Noble | P001 | Natural Gas Engine(1) 1,380 hp engine | 2012-03-12 | Catalytic Silencer | BCMJ Controls |  |  |  |  | 7E | Nitrogen Oxide | PASS | NA | Y | Tested pollutants: NO2, NO; Permitted Allowable Emission Rate = 1.0 g/Hp-hr, 82 -15% O2 ppmvd; Permitted Maximum Operating Rate = 1,380 Hp; Average Tested Emission Rate = 0.66 g/Hp-hr, 37.9 - 15% O2 ppmvd; Average Tested Operating Rate = 1,104 Hp; Results = Passed; AFS Date = 2012-08-01 00:00:00.0; AFS ID = legacy)
2012 | 732 | 0661005002 | Summerfield Compressor Station | between CR-45 and HWY 233 | Caldwell | 43724 |  | Noble | P002 | Natural Gas Engine (2) 1,380 hp | 2012-03-12 | Catalytic Silencer | BCMJ Controls |  |  |  |  | 7E | Nitrogen Dioxide | PASS | NA | Y | Tested pollutants: NO2, NO; Permitted Allowable Emission Rate = 1.0 g/Hp-hr, 82 -15% O2 ppmvd; Permitted Maximum Operating Rate = 1,380 Hp; Average Tested Emission Rate = 0.68 g/Hp-hr, 37.7 - 15% O2 ppmvd; Average Tested Operating Rate = 1,104 Hp; Results = Passed; AFS Date = 2012-08-01 00:00:00.0; AFS ID = legacy)
2012 | 733 | 0661005002 | Summerfield Compressor Station | between CR-45 and HWY 233 | Caldwell | 43724 |  | Noble | P002 | Natural Gas Engine (2) 1,380 hp | 2012-03-12 | Catalytic Silencer | BCMJ Controls |  |  |  |  | 7E | Nitrogen Oxide | PASS | NA | Y | Tested pollutants: NO2, NO; Permitted Allowable Emission Rate = 1.0 g/Hp-hr, 82 -15% O2 ppmvd; Permitted Maximum Operating Rate = 1,380 Hp; Average Tested Emission Rate = 0.68 g/Hp-hr, 37.7 - 15% O2 ppmvd; Average Tested Operating Rate = 1,104 Hp; Results = Passed; AFS Date = 2012-08-01 00:00:00.0; AFS ID = legacy)
2013 | 149 | 0210012004 | Augusta Compressor Facility- Utica Gas Services, L.L.C. | 8034 Bane Rd NE | East Twp. | 44427 |  | Carroll | P012 | 1,775-hp Caterpillar G3606 Compressor Engine w/ Oxidation Catalyst | 2013-10-08 | Oxid. Cat. 3(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 4(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 5(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 6(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 7(Catalytic Converter): | Alliance Source Testing | 1775 Hp | 1.96 lbs/hr, 1.0 g/hp/hr, 82 ppmvd@15%O2 | 1703 Hp or 96% of Max | 0.7 lbs/hr, 0.2 g/hp/hr, 16.5 ppmvd@15%O2 | 7E | Nitrogen Oxide | PASS | NA | Y
2013 | 151 | 0210012004 | Augusta Compressor Facility- Utica Gas Services, L.L.C. | 8034 Bane Rd NE | East Twp. | 44427 |  | Carroll | P013 | 1,775-hp Caterpillar G3606 Compressor Engine w/ Oxidation Catalyst | 2013-10-08 | Oxid. Cat. 3(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 4(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 5(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 6(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 7(Catalytic Converter): | Alliance Source Testing | 1775 Hp | 1.96 lbs/hr, 1.0 g/hp/hr, 82 ppmvd@15%O2 | 1680 Hp or 95% of Max | 0.66 lbs/hr, 0.2 g/hp/hr, 15.6 ppmvd@15%O2 | 7E | Nitrogen Oxide | PASS | NA | Y
2013 | 161 | 0210012004 | Augusta Compressor Facility- Utica Gas Services, L.L.C. | 8034 Bane Rd NE | East Twp. | 44427 |  | Carroll | P006 | 1,775-hp Caterpillar G3606 Compressor Engine w/ Oxidation Catalyst | 2013-10-09 | Oxid. Cat. 3(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 4(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 5(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 6(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 7(Catalytic Converter): | Alliance Source Testing | 1775 Hp | 1.96 lbs/hr, 1.0 g/hp/hr, 82 ppmvd@15%O2 | 1651 Hp or 93% of Max | 0.86 lbs/hr, 0.2 g/hp/hr, 20.8 ppmvd@15%O2 | 7E | Nitrogen Oxide | PASS | NA | Y
2013 | 164 | 0210012004 | Augusta Compressor Facility- Utica Gas Services, L.L.C. | 8034 Bane Rd NE | East Twp. | 44427 |  | Carroll | P007 | 1,775-hp Caterpillar G3606 Compressor Engine w/ Oxidation Catalyst | 2013-10-09 | Oxid. Cat. 3(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 4(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 5(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 6(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 7(Catalytic Converter): | Alliance Source Testing | 1775 Hp | 1.96 lbs/hr, 1.0 g/hp/hr, 82 ppmvd@15%O2 | 1624 Hp or 91% of Max | 0.97 lbs/hr, 0.3 g/hp/hr, 23.2 ppmvd@15%O2 | 7E | Nitrogen Oxide | PASS | NA | Y
2013 | 165 | 0210012004 | Augusta Compressor Facility- Utica Gas Services, L.L.C. | 8034 Bane Rd NE | East Twp. | 44427 |  | Carroll | P008 | 1,775-hp Caterpillar G3606 Compressor Engine w/ Oxidation Catalyst | 2013-10-09 | Oxid. Cat. 3(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 4(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 5(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 6(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 7(Catalytic Converter): | Alliance Source Testing | 1775 Hp | 1.96 lbs/hr, 1.0 g/hp/hr, 82 ppmvd@15%O2 | 1610 Hp or 91% of Max | 0.95 lbs/hr, 0.3 g/hp/hr, 23.2 ppmvd@15%O2 | 7E | Nitrogen Oxide | PASS | NA | Y
2013 | 188 | 0210002013 | Chesapeake Exploration LLC - Slates 16-12-5 | County Highway 59 | Kilgore | 43903 |  | Carroll | P002 | 211 hp CAT G3306TA Flash Gas Compressor equipped with catalyst. For this EU, GP12.1 covers one or multiple stationary natural gas-fired spark ignition (SI) internal combustion engines (ICE) with a combined total horsepower (HP) of no more than 1,800 HP for the site. Includes 2007 and later model year engines manufactured after the applicable effective date identified in 40 CFR 60.4230(a)(3) and engines manufactured before the effective date of the NSPS, where compliance with the Part 60 Subpart JJJJ emissions standards for the same size engine can be met by retrofitting the engine with a control device and demonstrated through stack testing. | 2013-08-08 | N/A | Alliance Source Testing, Inc. | 211 bhp | 82 ppmvd@15%O2 | 202 bhp or 96% | 21.3 ppmvd@15%O2 | 7E | Nitrogen Oxide | PASS | NA | Y | Caterpillar 215 bhp Natural Gas Engine G6X08478
2013 | 191 | 0210002014 | Chesapeake Exploration LLC - Scott 24-12-5 Pad | Ponder Rd | Kilgore | 44615 |  | Carroll | P002 | 211 hp CAT G3306TA flash gas compressor equipped with catalyst. For this EU, GP12.1 covers one or multiple stationary natural gas-fired spark ignition (SI) internal combustion engines (ICE) with a combined total horsepower (HP) of no more than 1,800 HP for the site. Includes 2007 and later model year engines manufactured after the applicable effective date identified in 40 CFR 60.4230(a)(3) and engines manufactured before the effective date of the NSPS, where compliance with the Part 60 Subpart JJJJ emissions standards for the same size engine can be met by retrofitting the engine with a control device and demonstrated through stack testing. | 2013-05-22 | Catalyst | Alliance Source Testing, Inc. | 215 hp | 5.73 lb/hr or 2.0 g/hp-hr | 176=75% | 0.08 lb/hr and 0.2 g/hp-hr | 7E | Nitrogen Oxide | PASS | NA | Y | Testing was accepted a the rate of 75% of max given that the facility is aware if they increase above this rate by more than 10% of the tested rate they will have to test again.
2013 | 194 | 0210012002 | Utica Gas Services, LLC-Carrollton Compressor Facility | 2098 Panda Road SE | Carrollton | 44615 |  | Carroll | P009 | 1,775 HP natural gas-fired Caterpillar G3606 engine #6 equipped with an oxidation catalyst | 2013-03-06 | Oxid. Cat.(Catalytic Converter): Oxidative Catalyst | Air Hygiene Inc. | 1775 Hp | NOX< 82 ppmvd@15% or O2 and 1.0 g/hp-hr | 1652 Hp | 20.55 ppmvd @ 15% O2 and 0.21g/hp-hr | 7E | Nitrogen Oxide | PASS | NA | Y
2013 | 197 | 0210012002 | Utica Gas Services, LLC-Carrollton Compressor Facility | 2098 Panda Road SE | Carrollton | 44615 |  | Carroll | P010 | 1,775 HP natural gas-fired Caterpillar G3606 engine #7 equipped with an oxidation catalyst | 2013-03-06 | Oxid. Cat.(Catalytic Converter): Oxidative Catalyst | Air Hygiene, Inc. | 1775 Hp | NOX< 82 ppmvd@15% or O2 and 1.0 g/hp-hr | 1608 Hp | 20.18 ppmvd @ 15% O2 and 0.22 g/hp-hr | 7E | Nitrogen Oxide | PASS | NA | Y | Method 320 utilized to provide the NMHC numbers in place of 25A. 320 pollutant designation is not applicable to this test event. Using the 25A tab for VOC reporting purposes.
2013 | 198 | 0210012002 | Utica Gas Services, LLC-Carrollton Compressor Facility | 2098 Panda Road SE | Carrollton | 44615 |  | Carroll | P006 | 1,775 HP natural gas-fired Caterpillar G3606 engine #3 equipped with an oxidation catalyst | 2013-03-07 | Oxid. Cat.(Catalytic Converter): Oxidative Catalyst | Alliance Source Testing | 1775 Hp | NOX< 82 ppmvd@15% or O2 and 1.0 g/hp-hr | 1666 Hp | 27.0 ppmvd @ 15% O2 and 0.2 g/hp-hr | 7E | Nitrogen Oxide | PASS | NA | Y
2013 | 201 | 0210012002 | Utica Gas Services, LLC-Carrollton Compressor Facility | 2098 Panda Road SE | Carrollton | 44615 |  | Carroll | P007 | 1,775 HP natural gas-fired Caterpillar G3606 engine #4 equipped with an oxidation catalyst | 2013-03-07 | Oxid. Cat.(Catalytic Converter): Oxidative Catalyst | Alliance Source Testing | 1775 Hp | NOX< 82 ppmvd@15% or O2 and 1.0 g/hp-hr | 1690 Hp | 17.1 ppmvd @ 15% O2 and 0.2 g/hp-hr | 7E | Nitrogen Oxide | PASS | NA | Y
2013 | 204 | 0210012002 | Utica Gas Services, LLC-Carrollton Compressor Facility | 2098 Panda Road SE | Carrollton | 44615 |  | Carroll | P008 | 1,775 HP natural gas-fired Caterpillar G3606 engine #5 equipped with an oxidation catalyst | 2013-03-07 | Oxid. Cat.(Catalytic Converter): Oxidative Catalyst | Air Hygiene Inc. | 1775 hp | NOX< 82 ppmvd@15% or O2 and 1.0 g/hp-hr | 1657 Hp | 21.10 ppmvd @ 15% O2 and 0.22 g/hp-hr | 7E | Nitrogen Oxide | PASS | NA | Y | Method 320 utilized to provide the NMHC numbers in place of 25A. 320 pollutant designation is not applicable to this test event. Using the 25A tab for VOC reporting purposes.
2013 | 207 | 0210012002 | Utica Gas Services, LLC-Carrollton Compressor Facility | 2098 Panda Road SE | Carrollton | 44615 |  | Carroll | P011 | 1,775 HP natural gas-fired Caterpillar G3606 engine #8 equipped with an oxidation catalyst | 2013-03-07 | Oxid. Cat.(Catalytic Converter): Oxidative Catalyst | Air Hygiene, Inc. | 1775 hp | NOX< 82 ppmvd@15% or O2 and 1.0 g/hp-hr | 1654 hp | 30.64 ppmvd @ 15% O2 and 0.3 g/hp-hr | 7E | Nitrogen Oxide | PASS | NA | Y
2013 | 212 | 0210012002 | Utica Gas Services, LLC-Carrollton Compressor Facility | 2098 Panda Road SE | Carrollton | 44615 |  | Carroll | P012 | 1,775 HP natural gas-fired Caterpillar G3606 engine #9 equipped with an oxidation catalyst | 2013-03-08 | Oxid. Cat.(Catalytic Converter): Oxidative Catalyst | Air Hygiene, Inc | 1775 Hp | NOX< 82 ppmvd@15% or O2 and 1.0 g/hp-hr | 1661 | 30.14 ppmvd @ 15% O2 and 0..32 g/hp-hr | 7E | Nitrogen Oxide | PASS | NA | Y
2013 | 213 | 0210012002 | Utica Gas Services, LLC-Carrollton Compressor Facility | 2098 Panda Road SE | Carrollton | 44615 |  | Carroll | P004 | 1,775 HP natural gas-fired Caterpillar G3606 engine #1 equipped with an oxidation catalyst. | 2013-05-01 | Oxid. Cat.(Catalytic Converter): Oxidative Catalyst | Air Hygiene Inc. | 1775Hp | 160 ppmvd @15 % O2 and 2 g/hp-hr | 1678Hp | 39.12 ppmvd @ 15% O2 and .2 g/hp-hr | 7E | Nitrogen Oxide | PASS | NA | Y
2013 | 216 | 0210012002 | Utica Gas Services, LLC-Carrollton Compressor Facility | 2098 Panda Road SE | Carrollton | 44615 |  | Carroll | P005 | 1,775 HP natural gas-fired Caterpillar G3606 engine #2 equipped with an oxidation catalyst | 2013-05-01 | Oxid. Cat.(Catalytic Converter): Oxidative Catalyst | Air Hygiene Inc. | 1775 hp | 160 ppmvd @15 % O2 and 2 g/hp-hr | 1620 Hp | 28.18 ppmvd @ 15 % O2 and .01 g/hp-hr | 7E | Nitrogen Oxide | PASS | NA | Y
2013 | 220 | 0210012002 | Utica Gas Services, LLC-Carrollton Compressor Facility | 2098 Panda Road SE | Carrollton | 44615 |  | Carroll | P013 | 1,775 HP natural gas-fired Caterpillar G3606 engine #10equipped with an oxidation catalyst | 2013-05-01 | Oxid. Cat.(Catalytic Converter): Oxidative Catalyst | Air Hygiene Inc. | 1775Hp | 160 ppmvd @15 % O2 and 2 g/hp-hr | 1625 Hp | 35.61ppmvd @ 15% O2 and .21 g/hp-hr | 7E | Nitrogen Oxide | PASS | NA | Y
2013 | 226 | 0210012004 | Augusta Compressor Facility- Utica Gas Services, L.L.C. | 8034 Bane Rd NE | East Twp. | 44427 |  | Carroll | P006 | 1,775-hp Caterpillar G3606 Compressor Engine w/ Oxidation Catalyst | 2013-10-08 | Oxid. Cat. 3(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 4(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 5(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 6(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 7(Catalytic Converter): | Alliance Source Testing | 1775 Hp | 1.96 lbs/hr, 1.0 g/hp/hr, 82 ppmvd@15%O2 | 1651 Hp or 93% of Max | 0.86 lbs/hr, 0.2 g/hp/hr, 20.8 ppmvd@15%O2 | 7E | Nitrogen Oxide | PASS | NA | Y
2013 | 229 | 0210012004 | Augusta Compressor Facility- Utica Gas Services, L.L.C. | 8034 Bane Rd NE | East Twp. | 44427 |  | Carroll | P007 | 1,775-hp Caterpillar G3606 Compressor Engine w/ Oxidation Catalyst | 2013-10-08 | Oxid. Cat. 3(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 4(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 5(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 6(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 7(Catalytic Converter): | Alliance Source Testing | 1775 Hp | 1.96 lbs/hr, 1.0 g/hp/hr, 82 ppmvd@15%O2 | 1624 Hp or 91% of Max | 0.97 lbs/hr, 0.3 g/hp/hr, 23.2 ppmvd@15%O2 | 7E | Nitrogen Oxide | PASS | NA | Y
2013 | 232 | 0210012004 | Augusta Compressor Facility- Utica Gas Services, L.L.C. | 8034 Bane Rd NE | East Twp. | 44427 |  | Carroll | P008 | 1,775-hp Caterpillar G3606 Compressor Engine w/ Oxidation Catalyst | 2013-10-08 | Oxid. Cat. 3(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 4(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 5(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 6(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 7(Catalytic Converter): | Alliance Source Testing | 1775 Hp | 1.96 lbs/hr, 1.0 g/hp/hr, 82 ppmvd@15%O2 | 1610 Hp or 91% of Max | 0.95 lbs/hr, 0.3 g/hp/hr, 23.2 ppmvd@15%O2 | 7E | Nitrogen Oxide | PASS | NA | Y
2013 | 236 | 0210012004 | Augusta Compressor Facility- Utica Gas Services, L.L.C. | 8034 Bane Rd NE | East Twp. | 44427 |  | Carroll | P009 | 1,775-hp Caterpillar G3606 Compressor Engine w/ Oxidation Catalyst | 2013-10-08 | Oxid. Cat. 3(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 4(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 5(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 6(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 7(Catalytic Converter): | Alliance Source Testing | 1775 Hp | 1.96 lbs/hr, 1.0 g/hp/hr, 82 ppmvd@15%O2 | 1724 Hp or 97% of Max | 0.65 lbs/hr, 0.2 g/hp/hr, 15.5 ppmvd@15%O2 | 7E | Nitrogen Oxide | PASS | NA | Y
2013 | 239 | 0210012004 | Augusta Compressor Facility- Utica Gas Services, L.L.C. | 8034 Bane Rd NE | East Twp. | 44427 |  | Carroll | P010 | 1,775-hp Caterpillar G3606 Compressor Engine w/ Oxidation Catalyst | 2013-10-08 | Oxid. Cat. 3(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 4(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 5(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 6(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 7(Catalytic Converter): | Alliance Source Testing | 1775 Hp | 1.96 lbs/hr, 1.0 g/hp/hr, 82 ppmvd@15%O2 | 1621 Hp or 91% of Max | 1.05 lbs/hr, 0.3 g/hp/hr, 26.0 ppmvd@15%O2 | 7E | Nitrogen Oxide | PASS | NA | Y
2013 | 242 | 0210012004 | Augusta Compressor Facility- Utica Gas Services, L.L.C. | 8034 Bane Rd NE | East Twp. | 44427 |  | Carroll | P011 | 1,775-hp Caterpillar G3606 Compressor Engine w/ Oxidation Catalyst | 2013-10-08 | Oxid. Cat. 3(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 4(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 5(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 6(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 7(Catalytic Converter): | Alliance Source Testing | 1775 Hp | 1.96 lbs/hr, 1.0 g/hp/hr, 82 ppmvd@15%O2 | 1632 Hp or 92% of Max | 0.78 lbs/hr, 0.2 g/hp/hr, 19 ppmvd@15%O2 | 7E | Nitrogen Oxide | PASS | NA | Y
2013 | 244 | 0210012004 | Augusta Compressor Facility- Utica Gas Services, L.L.C. | 8034 Bane Rd NE | East Twp. | 44427 |  | Carroll | P009 | 1,775-hp Caterpillar G3606 Compressor Engine w/ Oxidation Catalyst | 2013-10-09 | Oxid. Cat. 3(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 4(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 5(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 6(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 7(Catalytic Converter): | Alliance Source Testing | 1775 Hp | 1.96 lbs/hr, 1.0 g/hp/hr, 82 ppmvd@15%O2 | 1724 Hp or 97% of Max | 0.65 lbs/hr, 0.2 g/hp/hr, 15.5 ppmvd@15%O2 | 7E | Nitrogen Oxide | PASS | NA | Y
2013 | 278 | 0210012004 | Augusta Compressor Facility- Utica Gas Services, L.L.C. | 8034 Bane Rd NE | East Twp. | 44427 |  | Carroll | P010 | 1,775-hp Caterpillar G3606 Compressor Engine w/ Oxidation Catalyst | 2013-10-09 | Oxid. Cat. 3(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 4(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 5(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 6(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 7(Catalytic Converter): | Alliance Source Testing | 1775 Hp | 1.96 lbs/hr, 1.0 g/hp/hr, 82 ppmvd@15%O2 | 1621 Hp or 91% of Max | 1.05 lbs/hr, 0.3 g/hp/hr, 26.0 ppmvd@15%O2 | 7E | Nitrogen Oxide | PASS | NA | Y
2013 | 281 | 0210012004 | Augusta Compressor Facility- Utica Gas Services, L.L.C. | 8034 Bane Rd NE | East Twp. | 44427 |  | Carroll | P011 | 1,775-hp Caterpillar G3606 Compressor Engine w/ Oxidation Catalyst | 2013-10-09 | Oxid. Cat. 3(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 4(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 5(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 6(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 7(Catalytic Converter): | Alliance Source Testing | 1775 Hp | 1.96 lbs/hr, 1.0 g/hp/hr, 82 ppmvd@15%O2 | 1632 Hp or 92% of Max | 0.78 lbs/hr, 0.2 g/hp/hr, 19 ppmvd@15%O2 | 7E | Nitrogen Oxide | PASS | NA | Y
2013 | 283 | 0210012004 | Augusta Compressor Facility- Utica Gas Services, L.L.C. | 8034 Bane Rd NE | East Twp. | 44427 |  | Carroll | P012 | 1,775-hp Caterpillar G3606 Compressor Engine w/ Oxidation Catalyst | 2013-10-09 | Oxid. Cat. 3(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 4(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 5(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 6(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 7(Catalytic Converter): | Alliance Source Testing | 1775 Hp | 1.96 lbs/hr, 1.0 g/hp/hr, 82 ppmvd@15%O2 | 1703 Hp or 96% of Max | 0.7 lbs/hr, 0.2 g/hp/hr, 16.5 ppmvd@15%O2 | 7E | Nitrogen Oxide | PASS | NA | Y
2013 | 286 | 0210012004 | Augusta Compressor Facility- Utica Gas Services, L.L.C. | 8034 Bane Rd NE | East Twp. | 44427 |  | Carroll | P013 | 1,775-hp Caterpillar G3606 Compressor Engine w/ Oxidation Catalyst | 2013-10-09 | Oxid. Cat. 3(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 4(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 5(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 6(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 7(Catalytic Converter): | Alliance Source Testing | 1775 Hp | 1.96 lbs/hr, 1.0 g/hp/hr, 82 ppmvd@15%O2 | 1680 Hp or 95% of Max | 0.66 lbs/hr, 0.2 g/hp/hr, 15.6 ppmvd@15%O2 | 7E | Nitrogen Oxide | PASS | NA | Y
2013 | 297 | 0210012004 | Augusta Compressor Facility- Utica Gas Services, L.L.C. | 8034 Bane Rd NE | East Twp. | 44427 |  | Carroll | P006 | 1,775-hp Caterpillar G3606 Compressor Engine w/ Oxidation Catalyst | 2013-10-10 | Oxid. Cat. 3(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 4(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 5(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 6(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 7(Catalytic Converter): | Alliance Source Testing | 1775 Hp | 1.96 lbs/hr, 1.0 g/hp/hr, 82 ppmvd@15%O2 | 1651 Hp or 93% of Max | 0.86 lbs/hr, 0.2 g/hp/hr, 20.8 ppmvd@15%O2 | 7E | Nitrogen Oxide | PASS | NA | Y
2013 | 298 | 0210012004 | Augusta Compressor Facility- Utica Gas Services, L.L.C. | 8034 Bane Rd NE | East Twp. | 44427 |  | Carroll | P007 | 1,775-hp Caterpillar G3606 Compressor Engine w/ Oxidation Catalyst | 2013-10-10 | Oxid. Cat. 3(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 4(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 5(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 6(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 7(Catalytic Converter): | Alliance Source Testing | 1775 Hp | 1.96 lbs/hr, 1.0 g/hp/hr, 82 ppmvd@15%O2 | 1624 Hp or 91% of Max | 0.97 lbs/hr, 0.3 g/hp/hr, 23.2 ppmvd@15%O2 | 7E | Nitrogen Oxide | PASS | NA | Y
2013 | 302 | 0210012004 | Augusta Compressor Facility- Utica Gas Services, L.L.C. | 8034 Bane Rd NE | East Twp. | 44427 |  | Carroll | P008 | 1,775-hp Caterpillar G3606 Compressor Engine w/ Oxidation Catalyst | 2013-10-10 | Oxid. Cat. 3(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 4(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 5(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 6(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 7(Catalytic Converter): | Alliance Source Testing | 1775 Hp | 1.96 lbs/hr, 1.0 g/hp/hr, 82 ppmvd@15%O2 | 1610 Hp or 91% of Max | 0.95 lbs/hr, 0.3 g/hp/hr, 23.2 ppmvd@15%O2 | 7E | Nitrogen Oxide | PASS | NA | Y
2013 | 304 | 0210012004 | Augusta Compressor Facility- Utica Gas Services, L.L.C. | 8034 Bane Rd NE | East Twp. | 44427 |  | Carroll | P009 | 1,775-hp Caterpillar G3606 Compressor Engine w/ Oxidation Catalyst | 2013-10-10 | Oxid. Cat. 3(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 4(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 5(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 6(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 7(Catalytic Converter): | Alliance Source Testing | 1775 Hp | 1.96 lbs/hr, 1.0 g/hp/hr, 82 ppmvd@15%O2 | 1724 Hp or 97% of Max | 0.65 lbs/hr, 0.2 g/hp/hr, 15.5 ppmvd@15%O2 | 7E | Nitrogen Oxide | PASS | NA | Y
2013 | 307 | 0210012004 | Augusta Compressor Facility- Utica Gas Services, L.L.C. | 8034 Bane Rd NE | East Twp. | 44427 |  | Carroll | P010 | 1,775-hp Caterpillar G3606 Compressor Engine w/ Oxidation Catalyst | 2013-10-10 | Oxid. Cat. 3(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 4(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 5(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 6(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 7(Catalytic Converter): | Alliance Source Testing | 1775 Hp | 1.96 lbs/hr, 1.0 g/hp/hr, 82 ppmvd@15%O2 | 1621 Hp or 91% of Max | 1.05 lbs/hr, 0.3 g/hp/hr, 26.0 ppmvd@15%O2 | 7E | Nitrogen Oxide | PASS | NA | Y
2013 | 312 | 0210012004 | Augusta Compressor Facility- Utica Gas Services, L.L.C. | 8034 Bane Rd NE | East Twp. | 44427 |  | Carroll | P011 | 1,775-hp Caterpillar G3606 Compressor Engine w/ Oxidation Catalyst | 2013-10-10 | Oxid. Cat. 3(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 4(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 5(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 6(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 7(Catalytic Converter): | Alliance Source Testing | 1775 Hp | 1.96 lbs/hr, 1.0 g/hp/hr, 82 ppmvd@15%O2 | 1632 Hp or 92% of Max | 0.78 lbs/hr, 0.2 g/hp/hr, 19 ppmvd@15%O2 | 7E | Nitrogen Oxide | PASS | NA | Y
2013 | 315 | 0210012004 | Augusta Compressor Facility- Utica Gas Services, L.L.C. | 8034 Bane Rd NE | East Twp. | 44427 |  | Carroll | P012 | 1,775-hp Caterpillar G3606 Compressor Engine w/ Oxidation Catalyst | 2013-10-10 | Oxid. Cat. 3(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 4(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 5(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 6(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 7(Catalytic Converter): | Alliance Source Testing | 1775 Hp | 1.96 lbs/hr, 1.0 g/hp/hr, 82 ppmvd@15%O2 | 1703 Hp or 96% of Max | 0.7 lbs/hr, 0.2 g/hp/hr, 16.5 ppmvd@15%O2 | 7E | Nitrogen Oxide | PASS | NA | Y
2013 | 316 | 0210012004 | Augusta Compressor Facility- Utica Gas Services, L.L.C. | 8034 Bane Rd NE | East Twp. | 44427 |  | Carroll | P013 | 1,775-hp Caterpillar G3606 Compressor Engine w/ Oxidation Catalyst | 2013-10-10 | Oxid. Cat. 3(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 4(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 5(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 6(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 7(Catalytic Converter): | Alliance Source Testing | 1775 Hp | 1.96 lbs/hr, 1.0 g/hp/hr, 82 ppmvd@15%O2 | 1680 Hp or 95% of Max | 0.66 lbs/hr, 0.2 g/hp/hr, 15.6 ppmvd@15%O2 | 7E | Nitrogen Oxide | PASS | NA | Y
2013 | 329 | 0210012008 | Chesapeake Exploration LLC - Mangun 22-15-5 Pad | Lustre Rd NE | Carrollton | 44607 |  | Carroll | P002 | 145 hp Spark Ignition Internal Combustion Engine | 2013-03-06 | Catalyst | Alliance Source Testing | 145 HP | 82 ppmvd @ 15% O2 | 130 HP | 2.1 ppmvd @ 15% O2 | 7E | Nitrogen Oxide | PASS | NA | Y
2013 | 339 | 0210012020 | Chesapeake Exploration LLC - Rutledge 10-14-6 Pad | Canyon Rd SW | Carrollton | 44615 |  | Carroll | P002 | Natural Gas Engines | 2013-05-22 | Catalyst | Alliance Source Testing, Inc. | 215 hp | 5.73 lb/hr and 2.0 g-hp/hr | 194 = 90% | 0.05 lb/hr and 0.1 g-hp/hr | 7E | Nitrogen Oxide | PASS | NA | Y
2013 | 344 | 0210012024 | Chesapeake Exploration LLC - Brunk 32-13-5 Pad | Pinto Rd SE | Carrollton | 44615 |  | Carroll | P002 | Natural Gas Engines | 2013-08-09 | N/A | Alliance Source Testing | 215 bhp | 82 ppmvd@15%O2 | 91% or 196 bhp | 47.6 ppmvd@15%O2 | 7E | Nitrogen Oxide | PASS | NA | Y | Caterpillar 215 hp Natural Gas engine serial# 4FD04197
2013 | 347 | 0210012025 | Chesapeake Exploration LLC - Davis Farms 2-14-6 Pad | Pillar Rd SW | Carrollton | 44615 |  | Carroll | P002 | Natural Gas Engines | 2013-08-08 | N/A | Alliance Source Testing, Inc. | 215 bhp | 82 ppmvd@15%O2 | 91% or 197 bhp | 29.7 ppmvd@15%O2 | 7E | Nitrogen Oxide | PASS | NA | Y | Caterpillar 215 hp Natural Gas Engine serial# 4FD04263
2013 | 671 | 0285000366 | East Ohio Gas - Chippewa Station | 17045 Galehouse Road | Doylestown | 44230 |  | Wayne | B010 | 2,370 hp 4SLB SI ICE; CAT G3608 | 2013-06-11 | Engine 5 Converter(Catalytic Converter): Engine #5; Cat B010(Catalytic Converter): Catalytic Converter for B010, engine #6 | Environmental Quality Management, Inc. | 2370 Hp | 160 ppmvd@15%O2 or 2.0 g/hp-hr | 98% | 71.3 ppmvd@15%O2 and 1.01 g/hp-hr | 7E | Nitrogen Oxide | PASS | NA | Y
2013 | 681 | 0285012009 | Aspire Energy of Ohio LLC - AEO-C06 | County Rd 40 | Penn Twp. | 43758 |  | Morgan | P001 | Portable 276 bhp (@1,800 RPM), 2.05 MMBtu/hr Caterpillar Model G3406 TA, 4-stroke rich burn (4SRB), spark ignition (SI), natural gas-fired internal combustion engine, driving a pump or compressor, manufactured April 2012 and installed in October 2012. | 2013-10-10 | Converter(Catalytic Converter): Catalytic Converter | Custom Stack Analysis, LLC. | 276 hp | 1.0 g/hp-hr 82 ppm @ 15% O2 | 179 hp | 0.42 g/hp-hr 28.79 ppm @ 15% O2 | 7E | Nitrogen Oxide | PASS | NA | Y | Averages: 104.95ppm 0.1659 lbs/hr 28.79 ppm @ 15% O2 0.420 g/hp-hr
2013 | 1047 | 0607015001 | Tri-County Compressor Station (MarkWest / Ohio Oil Gath | North of intersection of Hwy 379 and Town | Barnesville | 43713 |  | Belmont | P003 | Compressor Engine #3 - 1980 HP (15.43 MMBtu/hr) Waukesha P9390 - natural gas-fired four-stroke rich burn internal combustion engine equipped with a three-way oxidation catalyst controlling CH2O, CO, NOx, & VOCs by 80, 97, 98.5 & 66 percent respectively | 2013-11-15 | CC002(Catalytic Converter): Compressor Engine #2 - 3-way Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - 3-way Catalyst; CC004(Catalytic Converter): Compressor Engine #4 - 3-way Catalyst; CC005(Catalytic Converter): Compressor Engine #5 - 3-w | Air Hygiene International | 1980 Hp | 1.0 g/hp-hr | 1861 Hp | 0.06 g/hp-hr | 7E | Nitrogen Dioxide | PASS | NA | Y | testing November 15th and 16th, 2013
2013 | 1048 | 0607015001 | Tri-County Compressor Station (MarkWest / Ohio Oil Gath | North of intersection of Hwy 379 and Town | Barnesville | 43713 |  | Belmont | P004 | Compressor Engine #4 - 1980 HP (15.43 MMBtu/hr) Waukesha P9390 - natural gas-fired four-stroke rich burn internal combustion engine equipped with a three-way oxidation catalyst controlling CH2O, CO, NOx, & VOCs by 80, 97, 98.5 & 66 percent respectively | 2013-11-15 | CC002(Catalytic Converter): Compressor Engine #2 - 3-way Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - 3-way Catalyst; CC004(Catalytic Converter): Compressor Engine #4 - 3-way Catalyst; CC005(Catalytic Converter): Compressor Engine #5 - 3-w | Air Hygiene International | 1980 Hp | 1.0 g/hp-hr | 1881 Hp | 0.08 g/hp-hr | 7E | Nitrogen Dioxide | PASS | NA | Y | testing November 15th and 16th, 2013
2013 | 1073 | 0679000330 | East Ohio Gas Jefferson Compressor Sta. | 4378 Williams Lake Rd SW | New Philadelphia | 44663 |  | Tuscarawas | P001 | 1340 HP 4 stroke lean burn natural gas fired reciprocating engine with catalytic oxidation | 2013-09-25 | S001(Catalytic Converter): Catalytic Converter for P001 | Environmental Quality Management, Inc. | 1340 HP | 2.0 g/HP-hr; 160 ppmvd @ 15% O2 | 1134 HP | 0.636 g/HP-hr; 121.6 ppmvd @ 15% O2 | 7E | Nitrogen Dioxide | PASS | NA | Y | PTIO P0110413 and NSPS JJJJ testing requirements.
2013 | 1154 | 0607015001 | Tri-County Compressor Station (MarkWest / Ohio Oil Gath | North of intersection of Hwy 379 and Town | Barnesville | 43713 |  | Belmont | P005 | Compressor Engine #5 - 1980 HP (15.43 MMBtu/hr) Waukesha P9390 - natural gas-fired four-stroke rich burn internal combustion engine equipped with a three-way oxidation catalyst controlling CH2O, CO, NOx, & VOCs by 80, 97, 98.5 & 66 percent respectively | 2013-11-15 | CC002(Catalytic Converter): Compressor Engine #2 - 3-way Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - 3-way Catalyst; CC004(Catalytic Converter): Compressor Engine #4 - 3-way Catalyst; CC005(Catalytic Converter): Compressor Engine #5 - 3-w | Air Hygiene International | 1980 Hp | 1.0 g/hp-hr | 1881 Hp | 0.04 g/hp-hr | 7E | Nitrogen Dioxide | PASS | NA | Y | testing November 15th and 16th, 2013
2013 | 1157 | 0607015001 | Tri-County Compressor Station (MarkWest / Ohio Oil Gath | North of intersection of Hwy 379 and Town | Barnesville | 43713 |  | Belmont | P006 | Compressor Engine #6 - 1980 HP (15.43 MMBtu/hr) Waukesha P9390 - natural gas-fired four-stroke rich burn internal combustion engine equipped with a three-way oxidation catalyst controlling CH2O, CO, NOx, & VOCs by 80, 97, 98.5 & 66 percent respectively | 2013-11-15 | CC002(Catalytic Converter): Compressor Engine #2 - 3-way Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - 3-way Catalyst; CC004(Catalytic Converter): Compressor Engine #4 - 3-way Catalyst; CC005(Catalytic Converter): Compressor Engine #5 - 3-w | Air Hygiene International | 1980 Hp | 1.0 g/hp-hr | 1861 Hp | 0.02 g/hp-hr | 7E | Nitrogen Dioxide | PASS | NA | Y | testing November 15th and 16th, 2013
2013 | 1177 | 0634005029 | Cadiz Gas Plant | 43071 Industrial Park Rd | Cadiz | 43907 |  | Harrison | P007 | Compressor Engine #7 - 4735 HP Caterpillar G3616 engine (CM-1206-7) - natural gas-fired four-stroke lean burn internal combustion engine equipped with an oxidation catalyst controlling CO, VOC and formaldehyde 95, 75, and 90 percent respectively. | 2013-11-14 | CC007(Catalytic Converter): oxidation catalyst | Air Hygiene International | 4,735 hp | 82.0 ppm | 4,715 hp | 5.1 ppm | 7E | Nitrogen Dioxide | PASS | NA | Y
2013 | 1179 | 0634005029 | Cadiz Gas Plant | 43071 Industrial Park Rd | Cadiz | 43907 |  | Harrison | P008 | Compressor Engine #8 - 4735 HP Caterpillar G3616 engine (CM-1206-8) - natural gas-fired four-stroke lean burn internal combustion engine equipped with an oxidation catalyst controlling CO, VOC and formaldehyde 95, 75, and 90 percent respectively. | 2013-11-14 | CC008(Catalytic Converter): oxidation catalyst | Air Hygiene International | 4,735 hp | 82.0 ppm | 4,725 | 6.5 ppm | 7E | Nitrogen Dioxide | PASS | NA | Y
2013 | 1181 | 0634005035 | Chesapeake Exploration LLC- Henderson South 10-12-6 Pad | Township Highway 225 | Scio | 43988 |  | Harrison | P002 | Flash Gas Compressor equipped with catalyst, 145 hp, Cat G3306 NA (Spark Ignition Internal Combustion Engine, P002) Flash Gas Compressor equipped with catalyst, 211 hp, CAT G3306 TA (Spark Ignition Internal Combustion Engine, P002) | 2013-08-23 | none | Alliance Source Testing | 211 Hp | 82 ppm | 185 Hp | 31.6 ppm | 7E | Nitrogen Dioxide | PASS | NA | Y
2013 | 1192 | 0634005040 | Archer Compressor Facility | County Highway 45 | Cadiz | 43907 |  | Harrison | P002 | Compressor Engine #2 - 1775 HP Caterpillar G3606 (4S-LB) - natural gas-fired four-cycle lean burn internal combustion engine rated equipped with an oxidation catalyst controlling CO and VOC emissions. | 2013-12-12 | OxidCat-102(Catalytic Converter): Oxidative Catalyst; OxidCat-102(Catalytic Converter): Oxidative Catalyst | Alliance Source Testing, LLC | 1775 HP | 1.96 lb/hr | 1621 | 0.71 lb/hr | 7E | Nitrogen Dioxide | PASS | NA | Y | PTIO P0113393 and NSPS JJJJ testing requirements.
2013 | 1193 | 0634005040 | Archer Compressor Facility | County Highway 45 | Cadiz | 43907 |  | Harrison | P003 | Compressor Engine #3 - 1775 HP Caterpillar G3606 (4S-LB) - natural gas-fired four-cycle lean burn internal combustion engine rated equipped with an oxidation catalyst controlling CO and VOC emissions. | 2013-12-12 | OxidCat-102(Catalytic Converter): Oxidative Catalyst; OxidCat-102(Catalytic Converter): Oxidative Catalyst | Alliance Source Testing, LLC | 1775 HP | 1.96 lb/hr | 1598 | 0.83 lb/hr | 7E | Nitrogen Dioxide | PASS | NA | Y | PTIO P0113393 and NSPS JJJJ testing requirements.
2013 | 1197 | 0634005040 | Archer Compressor Facility | County Highway 45 | Cadiz | 43907 |  | Harrison | P004 | Compressor Engine #4 - 1775 HP Caterpillar G3606 (4S-LB) - natural gas-fired four-cycle lean burn internal combustion engine rated equipped with an oxidation catalyst controlling CO and VOC emissions. | 2013-12-12 | OxidCat-102(Catalytic Converter): Oxidative Catalyst; OxidCat-102(Catalytic Converter): Oxidative Catalyst | Alliance Source Testing, LLC | 1775 HP | 1.96 lb/hr | 1609 | 0.68 lb/hr | 7E | Nitrogen Dioxide | PASS | NA | Y | PTIO P0113393 and NSPS JJJJ testing requirements.
2013 | 1199 | 0634005040 | Archer Compressor Facility | County Highway 45 | Cadiz | 43907 |  | Harrison | P005 | Compressor Engine #5 - 1775 HP Caterpillar G3606 (4S-LB) - natural gas-fired four-cycle lean burn internal combustion engine rated equipped with an oxidation catalyst controlling CO and VOC emissions. | 2013-12-12 | OxidCat-102(Catalytic Converter): Oxidative Catalyst; OxidCat-102(Catalytic Converter): Oxidative Catalyst | Alliance Source Testing, LLC | 1775 HP | 1.96 lb/hr | 1615 | 0.89 lb/hr | 7E | Nitrogen Dioxide | PASS | NA | Y | PTIO P0113393 and NSPS JJJJ testing requirements.
2013 | 1203 | 0634005040 | Archer Compressor Facility | County Highway 45 | Cadiz | 43907 |  | Harrison | P001 | Compressor Engine #1 - 1775 HP Caterpillar G3606 (4S-LB) - natural gas-fired four-cycle lean burn internal combustion engine rated equipped with an oxidation catalyst controlling CO and VOC emissions. | 2013-12-13 | OxidCat-101(Catalytic Converter): Oxidative Catalyst | Alliance Source Testing, LLC | 1775 HP | 1.96 lb/hr | 1632 HP | 0.79 lb/hr | 7E | Nitrogen Dioxide | PASS | NA | Y | PTIO P0113393 and NSPS JJJJ testing requirements.
2013 | 1239 | 0656035002 | Statoil - Eisenbarth Pad | 42240 Long Ridge Road | Clarington | 43931 |  | Monroe | P002 | (1) - 860 Hp, 6.5 mmBTU/hr, 4 stroke, lean burn, catalytic oxidation, Caterpillar G 3512 LE natural gas-fired internal combustion engine. | 2013-04-11 | Oxidative catalyst | Air Hygiene international, Inc. | 860 hp | 2.0 g/hp-hr 160 ppmvd @ 15% O2 | 860 Hp | 0.52 g/hp-hr 48.94 ppmvd @ 15% O2 | 7E | Nitrogen Dioxide | PASS | NA | Y
2013 | 1251 | 0661005002 | Summerfield Compressor Station | between CR-45 and HWY 233 | Caldwell | 43724 |  | Noble | P001 | Natural Gas Engine(1) 1,380 hp engine | 2013-03-12 | Catalyst 1(Catalytic Converter): Oxidation Catalyst 1 | BCMJ Controls | 1380 Hp | 1.0 g/Hp-hr | 1173 Hp | 0.7 g/Hp-hr | 7E | Nitrogen Dioxide | PASS | NA | Y
2013 | 1254 | 0661005002 | Summerfield Compressor Station | between CR-45 and HWY 233 | Caldwell | 43724 |  | Noble | P002 | Natural Gas Engine (2) 1,380 hp | 2013-03-12 | Catalyst 1(Catalytic Converter): Oxidation Catalyst 1 | BCMJ Controls | 1380 Hp | 1.0 g/Hp-hr | 1173 Hp | 0.6 g/Hp-hr | 7E | Nitrogen Dioxide | PASS | NA | Y
2014 | 48 | 0125102034 | Dominion - Groveport Compressor Station | 5509 Berger Road | Groveport | 43125 |  | Franklin | B001 | 4200 HP Engine-spark ignition, 2-stroke, lean burn | 2014-09-09 | None | Dominion Transmission, Inc. | 4200 HP | 18.52 lbs NOx/hr | 3931 HP | 12.75 lbs NOx/hr | 7E | Nitrogen Oxide | PASS | NA | Y | ITT Methods were approved by staff that no longer works at Ohio EPA and did not call attention to it. Tested both NO/NO2 for NOx.
2014 | 51 | 0125102034 | Dominion - Groveport Compressor Station | 5509 Berger Road | Groveport | 43125 |  | Franklin | B002 | 4200 HP Engine-spark ignition, 2-stroke, lean burn | 2014-09-09 | None | Dominion Transmission, Inc. | 4200 HP | 18.52 lbs NOx/hr | 3919 HP | 13.94 lbs NOx/hr | 7E | Nitrogen Oxide | PASS | NA | Y | ITT Methods were approved by staff that no longer works at Ohio EPA and did not call attention to it. Tested both NO/NO2 for NOx.
2014 | 56 | 0125102034 | Dominion - Groveport Compressor Station | 5509 Berger Road | Groveport | 43125 |  | Franklin | B003 | 3200 HP Engine-spark ignition, 2-stroke, lean burn | 2014-09-09 | None | Dominion Transmission, Inc. | 3200 HP | 14.11 lbs NOx/hr | 2988.7 HP | 5.93 lbs NOx/hr | 7E | Nitrogen Oxide | PASS | NA | Y | ITT Methods were approved by staff that no longer works at Ohio EPA and did not call attention to it. Tested both NO/NO2 for NOx.
2014 | 57 | 0125102034 | Dominion - Groveport Compressor Station | 5509 Berger Road | Groveport | 43125 |  | Franklin | B001 | 4200 HP Engine-spark ignition, 2-stroke, lean burn | 2014-09-10 | None | Dominion Transmission, Inc. | 4200 HP | 18.52 lbs NOx/hr | 3931 HP | 12.75 lbs NOx/hr | 7E | Nitrogen Oxide | PASS | NA | Y | ITT Methods were approved by staff that no longer works at Ohio EPA and did not call attention to it. Tested both NO/NO2 for NOx.
2014 | 60 | 0125102034 | Dominion - Groveport Compressor Station | 5509 Berger Road | Groveport | 43125 |  | Franklin | B002 | 4200 HP Engine-spark ignition, 2-stroke, lean burn | 2014-09-10 | None | Dominion Transmission, Inc. | 4200 HP | 18.52 lbs NOx/hr | 3919 HP | 13.94 lbs NOx/hr | 7E | Nitrogen Oxide | PASS | NA | Y | ITT Methods were approved by staff that no longer works at Ohio EPA and did not call attention to it. Tested both NO/NO2 for NOx.
2014 | 63 | 0125102034 | Dominion - Groveport Compressor Station | 5509 Berger Road | Groveport | 43125 |  | Franklin | B003 | 3200 HP Engine-spark ignition, 2-stroke, lean burn | 2014-09-10 | None | Dominion Transmission, Inc. | 3200 HP | 14.11 lbs NOx/hr | 2988.7 HP | 5.93 lbs NOx/hr | 7E | Nitrogen Oxide | PASS | NA | Y | ITT Methods were approved by staff that no longer works at Ohio EPA and did not call attention to it. Tested both NO/NO2 for NOx.
2014 | 184 | 0210002039 | Kilgore Compressor Station-Utica Gas Services, LLC | Pontiff Rd | Kilgore | 43988 |  | Carroll | P010 | 1,775 hp NG-fired 4SLB Stationary ICE equipped w/catalyst Caterpillar G3606: Serial Number: 4ZS01814 | 2014-01-14 | CC001(Catalytic Converter): Compressor Engine #1 - Oxidation Catalyst; CC002(Catalytic Converter): Compressor Engine #2 - Oxidation Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - Oxidation Catalyst; CC004(Catalytic Converter): Compressor Eng | Alliance Source Testing, Inc. | 1775 | NSPS 1.0 g/Hp-hr & 82ppm @ 15%O2, TV 1.96lb/hr | 1663 | NSPS 0.4 g/Hp-hr & 30.7ppm @ 15%O2, TV 1.35lb/hr | 7E | Nitrogen Oxide | PASS | NA | Y | The report was accepted as verification of compliance by the OEPA. However a few instances onsite were witnessed and variances were allowed to the testers for only accepting two runs as verification of compliance for P005 (NOx) and P009 (CO). Many issues could be attributed to the cold weather, however are preventable, and all efforts to prevent these issues from happening in the future will, and have been, taken into account for future test acceptance.
2014 | 189 | 0210012004 | Augusta Compressor Facility- Utica Gas Services, L.L.C. | 8034 Bane Rd NE | East Twp. | 44427 |  | Carroll | P013 | 1,775-hp Caterpillar G3606 Compressor Engine w/ Oxidation Catalyst | 2014-09-17 | Oxid. Cat. 3(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 4(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 5(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 6(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 7(Catalytic Converter): | Great Plains Analytics | 1775 Hp | 1.96 lbs/hr, 1.0 g/hp/hr, 82 ppmvd@15%O2 | 1780 | 1.84 lbs/hr, 0..46 g/hp/hr, 42.81 ppmvd@15%O2 | 7E | Nitrogen Oxide | PASS | NA | Y
2014 | 192 | 0210012004 | Augusta Compressor Facility- Utica Gas Services, L.L.C. | 8034 Bane Rd NE | East Twp. | 44427 |  | Carroll | P006 | 1,775-hp Caterpillar G3606 Compressor Engine w/ Oxidation Catalyst | 2014-09-18 | Oxid. Cat. 3(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 4(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 5(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 6(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 7(Catalytic Converter): | Great Plains Analytics | 1775 Hp | 1.96 lbs/hr, 1.0 g/hp/hr, 82 ppmvd@15%O2 | 1831 | 1.18 lbs/hr, 0.29 g/hp/hr, 27.9 ppmvd@15%O2 | 7E | Nitrogen Oxide | PASS | NA | Y
2014 | 196 | 0210012004 | Augusta Compressor Facility- Utica Gas Services, L.L.C. | 8034 Bane Rd NE | East Twp. | 44427 |  | Carroll | P007 | 1,775-hp Caterpillar G3606 Compressor Engine w/ Oxidation Catalyst | 2014-09-18 | Oxid. Cat. 3(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 4(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 5(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 6(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 7(Catalytic Converter): | Great Plains Analytics | 1775 Hp | 1.96 lbs/hr, 1.0 g/hp/hr, 82 ppmvd@15%O2 | 1839 | 1.52 lbs/hr, 0.37 g/hp/hr, 34.41 ppmvd@15%O2 | 7E | Nitrogen Oxide | PASS | NA | Y
2014 | 198 | 0210012004 | Augusta Compressor Facility- Utica Gas Services, L.L.C. | 8034 Bane Rd NE | East Twp. | 44427 |  | Carroll | P008 | 1,775-hp Caterpillar G3606 Compressor Engine w/ Oxidation Catalyst | 2014-09-18 | Oxid. Cat. 3(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 4(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 5(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 6(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 7(Catalytic Converter): | Great Plains Analytics | 1775 Hp | 1.96 lbs/hr, 1.0 g/hp/hr, 82 ppmvd@15%O2 | 1809 | 1.5 lbs/hr, 0.38 g/hp/hr, 36.46 ppmvd@15%O2 | 7E | Nitrogen Oxide | PASS | NA | Y
2014 | 223 | 0210002026 | Chesapeake Exploration LLC - Gartrell 23-13-6 Pad | Ohio 164 | Orange Twp. | 44695 |  | Carroll | P002 | 215 hp CAT G3406NA natural gas engine flash gas compressor equipped with catalyst. | 2014-04-08 | Catalyst | Alliance Source Testing | 211 HP | 82ppmvd@15%O2 | 175 HP or 83% of Max | 23.9 ppmvd@15%O2 | 7E | Nitrogen Oxide | PASS | NA | Y | If engine exceeds 10% of the tested rate the engine will require a retest.
2014 | 227 | 0210002029 | Chesapeake Exploration LLC - Colescott 11-12-5 Pad | Branch Rd | Kilgore | 44615 |  | Carroll | P002 | 215 hp CAT G3406NA flash gas compressor using natural gas engines and equipped with a catalyst. | 2014-04-08 | Catalyst | Alliance Source Testing | 211HP | 82 ppmvd@ 15%O2 | 165 HP or 78% of Max | 4.8 ppmvd@15%O2 | 7E | Nitrogen Oxide | PASS | NA | Y | Engine will have to retest if the engine exceed 10% operation of the tested rate.
2014 | 237 | 0210002039 | Kilgore Compressor Station-Utica Gas Services, LLC | Pontiff Rd | Kilgore | 43988 |  | Carroll | P001 | 1,775 hp NG-fired 4SLB Stationary ICE equipped w/catalyst Caterpillar G3606 Serial Number: 4ZS01713 | 2014-01-14 | CC001(Catalytic Converter): Compressor Engine #1 - Oxidation Catalyst; CC002(Catalytic Converter): Compressor Engine #2 - Oxidation Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - Oxidation Catalyst; CC004(Catalytic Converter): Compressor Eng | Alliance Source Testing, Inc. | 1775 | NSPS 1.0 g/Hp-hr & 82ppm @ 15%O2, TV 1.96lb/hr | 1722 | NSPS 0.2 g/Hp-hr & 15.9ppm @ 15%O2, TV .72lb/hr | 7E | Nitrogen Oxide | PASS | NA | Y | The report was accepted as verification of compliance by the OEPA. However a few instances onsite were witnessed and variances were allowed to the testers for only accepting two runs as verification of compliance for P005 (NOx) and P009 (CO). Many issues could be attributed to the cold weather, however are preventable, and all efforts to prevent these issues from happening in the future will, and have been, taken into account for future test acceptance.
2014 | 239 | 0210002039 | Kilgore Compressor Station-Utica Gas Services, LLC | Pontiff Rd | Kilgore | 43988 |  | Carroll | P002 | 1,775 hp NG-fired 4SLB Stationary ICE equipped w/catalyst Caterpillar G3606: Serial Number: 4ZS01796 | 2014-01-14 | CC001(Catalytic Converter): Compressor Engine #1 - Oxidation Catalyst; CC002(Catalytic Converter): Compressor Engine #2 - Oxidation Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - Oxidation Catalyst; CC004(Catalytic Converter): Compressor Eng | Alliance Source Testing, Inc. | 1775 | NSPS 1.0 g/Hp-hr & 82ppm @ 15%O2, TV 1.96lb/hr | 1698 | NSPS 0.3 g/Hp-hr & 24.1ppm @ 15%O2, TV 1.08lb/hr | 7E | Nitrogen Oxide | PASS | NA | Y | The report was accepted as verification of compliance by the OEPA. However a few instances onsite were witnessed and variances were allowed to the testers for only accepting two runs as verification of compliance for P005 (NOx) and P009 (CO). Many issues could be attributed to the cold weather, however are preventable, and all efforts to prevent these issues from happening in the future will, and have been, taken into account for future test acceptance.
2014 | 243 | 0210002039 | Kilgore Compressor Station-Utica Gas Services, LLC | Pontiff Rd | Kilgore | 43988 |  | Carroll | P003 | 1,775 hp NG-fired 4SLB Stationary ICE equipped w/catalyst Caterpillar G3606: Serial Number: 4ZS01797 | 2014-01-14 | CC001(Catalytic Converter): Compressor Engine #1 - Oxidation Catalyst; CC002(Catalytic Converter): Compressor Engine #2 - Oxidation Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - Oxidation Catalyst; CC004(Catalytic Converter): Compressor Eng | Alliance Source Testing, Inc. | 1775 | NSPS 1.0 g/Hp-hr & 82ppm @ 15%O2, TV 1.96lb/hr | 1669 | NSPS 0.3 g/Hp-hr & 22.6ppm @ 15%O2, TV 1.00lb/hr | 7E | Nitrogen Oxide | PASS | NA | Y | The report was accepted as verification of compliance by the OEPA. However a few instances onsite were witnessed and variances were allowed to the testers for only accepting two runs as verification of compliance for P005 (NOx) and P009 (CO). Many issues could be attributed to the cold weather, however are preventable, and all efforts to prevent these issues from happening in the future will, and have been, taken into account for future test acceptance.
2014 | 246 | 0210002039 | Kilgore Compressor Station-Utica Gas Services, LLC | Pontiff Rd | Kilgore | 43988 |  | Carroll | P004 | 1,775 hp NG-fired 4SLB Stationary ICE equipped w/catalyst Caterpillar G3606: Serial Number: 4ZS01800 | 2014-01-14 | CC001(Catalytic Converter): Compressor Engine #1 - Oxidation Catalyst; CC002(Catalytic Converter): Compressor Engine #2 - Oxidation Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - Oxidation Catalyst; CC004(Catalytic Converter): Compressor Eng | Alliance Source Testing, Inc. | 1775 | NSPS 1.0 g/Hp-hr & 82ppm @ 15%O2, TV 1.96lb/hr | 1698 | NSPS 0.3 g/Hp-hr & 25.3ppm @ 15%O2, TV 1.15lb/hr | 7E | Nitrogen Oxide | PASS | NA | Y | The report was accepted as verification of compliance by the OEPA. However a few instances onsite were witnessed and variances were allowed to the testers for only accepting two runs as verification of compliance for P005 (NOx) and P009 (CO). Many issues could be attributed to the cold weather, however are preventable, and all efforts to prevent these issues from happening in the future will, and have been, taken into account for future test acceptance.
2014 | 249 | 0210002039 | Kilgore Compressor Station-Utica Gas Services, LLC | Pontiff Rd | Kilgore | 43988 |  | Carroll | P005 | 1,775 hp NG-fired 4SLB Stationary ICE equipped w/catalyst Caterpillar G3606: Serial Number: 4ZS01804 | 2014-01-14 | CC001(Catalytic Converter): Compressor Engine #1 - Oxidation Catalyst; CC002(Catalytic Converter): Compressor Engine #2 - Oxidation Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - Oxidation Catalyst; CC004(Catalytic Converter): Compressor Eng | Alliance Source Testing, Inc. | 1775 | NSPS 1.0 g/Hp-hr & 82ppm @ 15%O2, TV 1.96lb/hr | 1698 *all NOx are 2 run average (P005) | NSPS .3 g/Hp-hr & 23.85ppm @ 15%O2, TV 1.05lb/hr | 7E | Nitrogen Oxide | PASS | NA | Y | The report was accepted as verification of compliance by the OEPA. However a few instances onsite were witnessed and variances were allowed to the testers for only accepting two runs as verification of compliance for P005 (NOx) and P009 (CO). Many issues could be attributed to the cold weather, however are preventable, and all efforts to prevent these issues from happening in the future will, and have been, taken into account for future test acceptance.
2014 | 251 | 0210002039 | Kilgore Compressor Station-Utica Gas Services, LLC | Pontiff Rd | Kilgore | 43988 |  | Carroll | P006 | 1,775 hp NG-fired 4SLB Stationary ICE equipped w/catalyst Caterpillar G3606: Serial Number: 4ZS01805 | 2014-01-14 | CC001(Catalytic Converter): Compressor Engine #1 - Oxidation Catalyst; CC002(Catalytic Converter): Compressor Engine #2 - Oxidation Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - Oxidation Catalyst; CC004(Catalytic Converter): Compressor Eng | Alliance Source Testing, Inc. | 1775 | NSPS 1.0 g/Hp-hr & 82ppm @ 15%O2, TV 1.96lb/hr | 1698 | NSPS .3 g/Hp-hr & 23.0ppm @ 15%O2, TV 1.04lb/hr | 7E | Nitrogen Oxide | PASS | NA | Y | The report was accepted as verification of compliance by the OEPA. However a few instances onsite were witnessed and variances were allowed to the testers for only accepting two runs as verification of compliance for P005 (NOx) and P009 (CO). Many issues could be attributed to the cold weather, however are preventable, and all efforts to prevent these issues from happening in the future will, and have been, taken into account for future test acceptance.
2014 | 255 | 0210002039 | Kilgore Compressor Station-Utica Gas Services, LLC | Pontiff Rd | Kilgore | 43988 |  | Carroll | P007 | 1,775 hp NG-fired 4SLB Stationary ICE equipped w/catalyst Caterpillar G3606: Serial Number: 4ZS01807 | 2014-01-14 | CC001(Catalytic Converter): Compressor Engine #1 - Oxidation Catalyst; CC002(Catalytic Converter): Compressor Engine #2 - Oxidation Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - Oxidation Catalyst; CC004(Catalytic Converter): Compressor Eng | Alliance Source Testing, Inc. | 1775 | NSPS 1.0 g/Hp-hr & 82ppm @ 15%O2, TV 1.96lb/hr | 1716 | NSPS 0.2 g/Hp-hr & 20.2ppm @ 15%O2, TV .91lb/hr | 7E | Nitrogen Oxide | PASS | NA | Y | The report was accepted as verification of compliance by the OEPA. However a few instances onsite were witnessed and variances were allowed to the testers for only accepting two runs as verification of compliance for P005 (NOx) and P009 (CO). Many issues could be attributed to the cold weather, however are preventable, and all efforts to prevent these issues from happening in the future will, and have been, taken into account for future test acceptance.
2014 | 256 | 0210002039 | Kilgore Compressor Station-Utica Gas Services, LLC | Pontiff Rd | Kilgore | 43988 |  | Carroll | P008 | 1,775 hp NG-fired 4SLB Stationary ICE equipped w/catalyst Caterpillar G3606: Serial Number: 4ZS01808 | 2014-01-14 | CC001(Catalytic Converter): Compressor Engine #1 - Oxidation Catalyst; CC002(Catalytic Converter): Compressor Engine #2 - Oxidation Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - Oxidation Catalyst; CC004(Catalytic Converter): Compressor Eng | Alliance Source Testing, Inc. | 1775 | NSPS 1.0 g/Hp-hr & 82ppm @ 15%O2, TV 1.96lb/hr | 1769 | NSPS 0.3 g/Hp-hr & 21.4ppm @ 15%O2, TV .96lb/hr | 7E | Nitrogen Oxide | PASS | NA | Y | The report was accepted as verification of compliance by the OEPA. However a few instances onsite were witnessed and variances were allowed to the testers for only accepting two runs as verification of compliance for P005 (NOx) and P009 (CO). Many issues could be attributed to the cold weather, however are preventable, and all efforts to prevent these issues from happening in the future will, and have been, taken into account for future test acceptance.
2014 | 259 | 0210002039 | Kilgore Compressor Station-Utica Gas Services, LLC | Pontiff Rd | Kilgore | 43988 |  | Carroll | P009 | 1,775 hp NG-fired 4SLB Stationary ICE equipped w/catalyst Caterpillar G3606: Serial Number: 4ZS01776 | 2014-01-14 | CC001(Catalytic Converter): Compressor Engine #1 - Oxidation Catalyst; CC002(Catalytic Converter): Compressor Engine #2 - Oxidation Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - Oxidation Catalyst; CC004(Catalytic Converter): Compressor Eng | Alliance Source Testing, Inc. | 1775 | NSPS 1.0 g/Hp-hr & 82ppm @ 15%O2, TV 1.96lb/hr | 1722 | NSPS 0.3 g/Hp-hr & 23.9ppm @ 15%O2, TV 1.07lb/hr | 7E | Nitrogen Oxide | PASS | NA | Y | The report was accepted as verification of compliance by the OEPA. However a few instances onsite were witnessed and variances were allowed to the testers for only accepting two runs as verification of compliance for P005 (NOx) and P009 (CO). Many issues could be attributed to the cold weather, however are preventable, and all efforts to prevent these issues from happening in the future will, and have been, taken into account for future test acceptance.
2014 | 268 | 0210002039 | Kilgore Compressor Station-Utica Gas Services, LLC | Pontiff Rd | Kilgore | 43988 |  | Carroll | P001 | 1,775 hp NG-fired 4SLB Stationary ICE equipped w/catalyst Caterpillar G3606 Serial Number: 4ZS01713 | 2014-01-15 | CC001(Catalytic Converter): Compressor Engine #1 - Oxidation Catalyst; CC002(Catalytic Converter): Compressor Engine #2 - Oxidation Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - Oxidation Catalyst; CC004(Catalytic Converter): Compressor Eng | Alliance Source Testing, Inc. | 1775 | NSPS 1.0 g/Hp-hr & 82ppm @ 15%O2, TV 1.96lb/hr | 1722 | NSPS 0.2 g/Hp-hr & 15.9ppm @ 15%O2, TV .72lb/hr | 7E | Nitrogen Oxide | PASS | NA | Y | The report was accepted as verification of compliance by the OEPA. However a few instances onsite were witnessed and variances were allowed to the testers for only accepting two runs as verification of compliance for P005 (NOx) and P009 (CO). Many issues could be attributed to the cold weather, however are preventable, and all efforts to prevent these issues from happening in the future will, and have been, taken into account for future test acceptance.
2014 | 273 | 0210002039 | Kilgore Compressor Station-Utica Gas Services, LLC | Pontiff Rd | Kilgore | 43988 |  | Carroll | P002 | 1,775 hp NG-fired 4SLB Stationary ICE equipped w/catalyst Caterpillar G3606: Serial Number: 4ZS01796 | 2014-01-15 | CC001(Catalytic Converter): Compressor Engine #1 - Oxidation Catalyst; CC002(Catalytic Converter): Compressor Engine #2 - Oxidation Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - Oxidation Catalyst; CC004(Catalytic Converter): Compressor Eng | Alliance Source Testing, Inc. | 1775 | NSPS 1.0 g/Hp-hr & 82ppm @ 15%O2, TV 1.96lb/hr | 1698 | NSPS 0.3 g/Hp-hr & 24.1ppm @ 15%O2, TV 1.08lb/hr | 7E | Nitrogen Oxide | PASS | NA | Y | The report was accepted as verification of compliance by the OEPA. However a few instances onsite were witnessed and variances were allowed to the testers for only accepting two runs as verification of compliance for P005 (NOx) and P009 (CO). Many issues could be attributed to the cold weather, however are preventable, and all efforts to prevent these issues from happening in the future will, and have been, taken into account for future test acceptance.
2014 | 275 | 0210002039 | Kilgore Compressor Station-Utica Gas Services, LLC | Pontiff Rd | Kilgore | 43988 |  | Carroll | P003 | 1,775 hp NG-fired 4SLB Stationary ICE equipped w/catalyst Caterpillar G3606: Serial Number: 4ZS01797 | 2014-01-15 | CC001(Catalytic Converter): Compressor Engine #1 - Oxidation Catalyst; CC002(Catalytic Converter): Compressor Engine #2 - Oxidation Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - Oxidation Catalyst; CC004(Catalytic Converter): Compressor Eng | Alliance Source Testing, Inc. | 1775 | NSPS 1.0 g/Hp-hr & 82ppm @ 15%O2, TV 1.96lb/hr | 1669 | NSPS 0.3 g/Hp-hr & 22.6ppm @ 15%O2, TV 1.00lb/hr | 7E | Nitrogen Oxide | PASS | NA | Y | The report was accepted as verification of compliance by the OEPA. However a few instances onsite were witnessed and variances were allowed to the testers for only accepting two runs as verification of compliance for P005 (NOx) and P009 (CO). Many issues could be attributed to the cold weather, however are preventable, and all efforts to prevent these issues from happening in the future will, and have been, taken into account for future test acceptance.
2014 | 278 | 0210002039 | Kilgore Compressor Station-Utica Gas Services, LLC | Pontiff Rd | Kilgore | 43988 |  | Carroll | P004 | 1,775 hp NG-fired 4SLB Stationary ICE equipped w/catalyst Caterpillar G3606: Serial Number: 4ZS01800 | 2014-01-15 | CC001(Catalytic Converter): Compressor Engine #1 - Oxidation Catalyst; CC002(Catalytic Converter): Compressor Engine #2 - Oxidation Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - Oxidation Catalyst; CC004(Catalytic Converter): Compressor Eng | Alliance Source Testing, Inc. | 1775 | NSPS 1.0 g/Hp-hr & 82ppm @ 15%O2, TV 1.96lb/hr | 1698 | NSPS 0.3 g/Hp-hr & 25.3ppm @ 15%O2, TV 1.15lb/hr | 7E | Nitrogen Oxide | PASS | NA | Y | The report was accepted as verification of compliance by the OEPA. However a few instances onsite were witnessed and variances were allowed to the testers for only accepting two runs as verification of compliance for P005 (NOx) and P009 (CO). Many issues could be attributed to the cold weather, however are preventable, and all efforts to prevent these issues from happening in the future will, and have been, taken into account for future test acceptance.
2014 | 282 | 0210002039 | Kilgore Compressor Station-Utica Gas Services, LLC | Pontiff Rd | Kilgore | 43988 |  | Carroll | P005 | 1,775 hp NG-fired 4SLB Stationary ICE equipped w/catalyst Caterpillar G3606: Serial Number: 4ZS01804 | 2014-01-15 | CC001(Catalytic Converter): Compressor Engine #1 - Oxidation Catalyst; CC002(Catalytic Converter): Compressor Engine #2 - Oxidation Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - Oxidation Catalyst; CC004(Catalytic Converter): Compressor Eng | Alliance Source Testing, Inc. | 1775 | NSPS 1.0 g/Hp-hr & 82ppm @ 15%O2, TV 1.96lb/hr | 1698 *all NOx are 2 run average (P005) | NSPS .3 g/Hp-hr & 23.85ppm @ 15%O2, TV 1.05lb/hr | 7E | Nitrogen Oxide | PASS | NA | Y | The report was accepted as verification of compliance by the OEPA. However a few instances onsite were witnessed and variances were allowed to the testers for only accepting two runs as verification of compliance for P005 (NOx) and P009 (CO). Many issues could be attributed to the cold weather, however are preventable, and all efforts to prevent these issues from happening in the future will, and have been, taken into account for future test acceptance.
2014 | 285 | 0210002039 | Kilgore Compressor Station-Utica Gas Services, LLC | Pontiff Rd | Kilgore | 43988 |  | Carroll | P006 | 1,775 hp NG-fired 4SLB Stationary ICE equipped w/catalyst Caterpillar G3606: Serial Number: 4ZS01805 | 2014-01-15 | CC001(Catalytic Converter): Compressor Engine #1 - Oxidation Catalyst; CC002(Catalytic Converter): Compressor Engine #2 - Oxidation Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - Oxidation Catalyst; CC004(Catalytic Converter): Compressor Eng | Alliance Source Testing, Inc. | 1775 | NSPS 1.0 g/Hp-hr & 82ppm @ 15%O2, TV 1.96lb/hr | 1698 | NSPS .3 g/Hp-hr & 23.0ppm @ 15%O2, TV 1.04lb/hr | 7E | Nitrogen Oxide | PASS | NA | Y | The report was accepted as verification of compliance by the OEPA. However a few instances onsite were witnessed and variances were allowed to the testers for only accepting two runs as verification of compliance for P005 (NOx) and P009 (CO). Many issues could be attributed to the cold weather, however are preventable, and all efforts to prevent these issues from happening in the future will, and have been, taken into account for future test acceptance.
2014 | 288 | 0210002039 | Kilgore Compressor Station-Utica Gas Services, LLC | Pontiff Rd | Kilgore | 43988 |  | Carroll | P007 | 1,775 hp NG-fired 4SLB Stationary ICE equipped w/catalyst Caterpillar G3606: Serial Number: 4ZS01807 | 2014-01-15 | CC001(Catalytic Converter): Compressor Engine #1 - Oxidation Catalyst; CC002(Catalytic Converter): Compressor Engine #2 - Oxidation Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - Oxidation Catalyst; CC004(Catalytic Converter): Compressor Eng | Alliance Source Testing, Inc. | 1775 | NSPS 1.0 g/Hp-hr & 82ppm @ 15%O2, TV 1.96lb/hr | 1716 | NSPS 0.2 g/Hp-hr & 20.2ppm @ 15%O2, TV .91lb/hr | 7E | Nitrogen Oxide | PASS | NA | Y | The report was accepted as verification of compliance by the OEPA. However a few instances onsite were witnessed and variances were allowed to the testers for only accepting two runs as verification of compliance for P005 (NOx) and P009 (CO). Many issues could be attributed to the cold weather, however are preventable, and all efforts to prevent these issues from happening in the future will, and have been, taken into account for future test acceptance.
2014 | 291 | 0210002039 | Kilgore Compressor Station-Utica Gas Services, LLC | Pontiff Rd | Kilgore | 43988 |  | Carroll | P008 | 1,775 hp NG-fired 4SLB Stationary ICE equipped w/catalyst Caterpillar G3606: Serial Number: 4ZS01808 | 2014-01-15 | CC001(Catalytic Converter): Compressor Engine #1 - Oxidation Catalyst; CC002(Catalytic Converter): Compressor Engine #2 - Oxidation Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - Oxidation Catalyst; CC004(Catalytic Converter): Compressor Eng | Alliance Source Testing, Inc. | 1775 | NSPS 1.0 g/Hp-hr & 82ppm @ 15%O2, TV 1.96lb/hr | 1769 | NSPS 0.3 g/Hp-hr & 21.4ppm @ 15%O2, TV .96lb/hr | 7E | Nitrogen Oxide | PASS | NA | Y | The report was accepted as verification of compliance by the OEPA. However a few instances onsite were witnessed and variances were allowed to the testers for only accepting two runs as verification of compliance for P005 (NOx) and P009 (CO). Many issues could be attributed to the cold weather, however are preventable, and all efforts to prevent these issues from happening in the future will, and have been, taken into account for future test acceptance.
2014 | 294 | 0210002039 | Kilgore Compressor Station-Utica Gas Services, LLC | Pontiff Rd | Kilgore | 43988 |  | Carroll | P009 | 1,775 hp NG-fired 4SLB Stationary ICE equipped w/catalyst Caterpillar G3606: Serial Number: 4ZS01776 | 2014-01-15 | CC001(Catalytic Converter): Compressor Engine #1 - Oxidation Catalyst; CC002(Catalytic Converter): Compressor Engine #2 - Oxidation Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - Oxidation Catalyst; CC004(Catalytic Converter): Compressor Eng | Alliance Source Testing, Inc. | 1775 | NSPS 1.0 g/Hp-hr & 82ppm @ 15%O2, TV 1.96lb/hr | 1722 | NSPS 0.3 g/Hp-hr & 23.9ppm @ 15%O2, TV 1.07lb/hr | 7E | Nitrogen Oxide | PASS | NA | Y | The report was accepted as verification of compliance by the OEPA. However a few instances onsite were witnessed and variances were allowed to the testers for only accepting two runs as verification of compliance for P005 (NOx) and P009 (CO). Many issues could be attributed to the cold weather, however are preventable, and all efforts to prevent these issues from happening in the future will, and have been, taken into account for future test acceptance.
2014 | 297 | 0210002039 | Kilgore Compressor Station-Utica Gas Services, LLC | Pontiff Rd | Kilgore | 43988 |  | Carroll | P010 | 1,775 hp NG-fired 4SLB Stationary ICE equipped w/catalyst Caterpillar G3606: Serial Number: 4ZS01814 | 2014-01-15 | CC001(Catalytic Converter): Compressor Engine #1 - Oxidation Catalyst; CC002(Catalytic Converter): Compressor Engine #2 - Oxidation Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - Oxidation Catalyst; CC004(Catalytic Converter): Compressor Eng | Alliance Source Testing, Inc. | 1775 | NSPS 1.0 g/Hp-hr & 82ppm @ 15%O2, TV 1.96lb/hr | 1663 | NSPS 0.4 g/Hp-hr & 30.7ppm @ 15%O2, TV 1.35lb/hr | 7E | Nitrogen Oxide | PASS | NA | Y | The report was accepted as verification of compliance by the OEPA. However a few instances onsite were witnessed and variances were allowed to the testers for only accepting two runs as verification of compliance for P005 (NOx) and P009 (CO). Many issues could be attributed to the cold weather, however are preventable, and all efforts to prevent these issues from happening in the future will, and have been, taken into account for future test acceptance.
2014 | 308 | 0210002039 | Kilgore Compressor Station-Utica Gas Services, LLC | Pontiff Rd | Kilgore | 43988 |  | Carroll | P001 | 1,775 hp NG-fired 4SLB Stationary ICE equipped w/catalyst Caterpillar G3606 Serial Number: 4ZS01713 | 2014-01-16 | CC001(Catalytic Converter): Compressor Engine #1 - Oxidation Catalyst; CC002(Catalytic Converter): Compressor Engine #2 - Oxidation Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - Oxidation Catalyst; CC004(Catalytic Converter): Compressor Eng | Alliance Source Testing, Inc. | 1775 | NSPS 1.0 g/Hp-hr & 82ppm @ 15%O2, TV 1.96lb/hr | 1722 | NSPS 0.2 g/Hp-hr & 15.9ppm @ 15%O2, TV .72lb/hr | 7E | Nitrogen Oxide | PASS | NA | Y | The report was accepted as verification of compliance by the OEPA. However a few instances onsite were witnessed and variances were allowed to the testers for only accepting two runs as verification of compliance for P005 (NOx) and P009 (CO). Many issues could be attributed to the cold weather, however are preventable, and all efforts to prevent these issues from happening in the future will, and have been, taken into account for future test acceptance.
2014 | 311 | 0210002039 | Kilgore Compressor Station-Utica Gas Services, LLC | Pontiff Rd | Kilgore | 43988 |  | Carroll | P002 | 1,775 hp NG-fired 4SLB Stationary ICE equipped w/catalyst Caterpillar G3606: Serial Number: 4ZS01796 | 2014-01-16 | CC001(Catalytic Converter): Compressor Engine #1 - Oxidation Catalyst; CC002(Catalytic Converter): Compressor Engine #2 - Oxidation Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - Oxidation Catalyst; CC004(Catalytic Converter): Compressor Eng | Alliance Source Testing, Inc. | 1775 | NSPS 1.0 g/Hp-hr & 82ppm @ 15%O2, TV 1.96lb/hr | 1698 | NSPS 0.3 g/Hp-hr & 24.1ppm @ 15%O2, TV 1.08lb/hr | 7E | Nitrogen Oxide | PASS | NA | Y | The report was accepted as verification of compliance by the OEPA. However a few instances onsite were witnessed and variances were allowed to the testers for only accepting two runs as verification of compliance for P005 (NOx) and P009 (CO). Many issues could be attributed to the cold weather, however are preventable, and all efforts to prevent these issues from happening in the future will, and have been, taken into account for future test acceptance.
2014 | 314 | 0210002039 | Kilgore Compressor Station-Utica Gas Services, LLC | Pontiff Rd | Kilgore | 43988 |  | Carroll | P003 | 1,775 hp NG-fired 4SLB Stationary ICE equipped w/catalyst Caterpillar G3606: Serial Number: 4ZS01797 | 2014-01-16 | CC001(Catalytic Converter): Compressor Engine #1 - Oxidation Catalyst; CC002(Catalytic Converter): Compressor Engine #2 - Oxidation Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - Oxidation Catalyst; CC004(Catalytic Converter): Compressor Eng | Alliance Source Testing, Inc. | 1775 | NSPS 1.0 g/Hp-hr & 82ppm @ 15%O2, TV 1.96lb/hr | 1669 | NSPS 0.3 g/Hp-hr & 22.6ppm @ 15%O2, TV 1.00lb/hr | 7E | Nitrogen Oxide | PASS | NA | Y | The report was accepted as verification of compliance by the OEPA. However a few instances onsite were witnessed and variances were allowed to the testers for only accepting two runs as verification of compliance for P005 (NOx) and P009 (CO). Many issues could be attributed to the cold weather, however are preventable, and all efforts to prevent these issues from happening in the future will, and have been, taken into account for future test acceptance.
2014 | 317 | 0210002039 | Kilgore Compressor Station-Utica Gas Services, LLC | Pontiff Rd | Kilgore | 43988 |  | Carroll | P004 | 1,775 hp NG-fired 4SLB Stationary ICE equipped w/catalyst Caterpillar G3606: Serial Number: 4ZS01800 | 2014-01-16 | CC001(Catalytic Converter): Compressor Engine #1 - Oxidation Catalyst; CC002(Catalytic Converter): Compressor Engine #2 - Oxidation Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - Oxidation Catalyst; CC004(Catalytic Converter): Compressor Eng | Alliance Source Testing, Inc. | 1775 | NSPS 1.0 g/Hp-hr & 82ppm @ 15%O2, TV 1.96lb/hr | 1698 | NSPS 0.3 g/Hp-hr & 25.3ppm @ 15%O2, TV 1.15lb/hr | 7E | Nitrogen Oxide | PASS | NA | Y | The report was accepted as verification of compliance by the OEPA. However a few instances onsite were witnessed and variances were allowed to the testers for only accepting two runs as verification of compliance for P005 (NOx) and P009 (CO). Many issues could be attributed to the cold weather, however are preventable, and all efforts to prevent these issues from happening in the future will, and have been, taken into account for future test acceptance.
2014 | 320 | 0210002039 | Kilgore Compressor Station-Utica Gas Services, LLC | Pontiff Rd | Kilgore | 43988 |  | Carroll | P005 | 1,775 hp NG-fired 4SLB Stationary ICE equipped w/catalyst Caterpillar G3606: Serial Number: 4ZS01804 | 2014-01-16 | CC001(Catalytic Converter): Compressor Engine #1 - Oxidation Catalyst; CC002(Catalytic Converter): Compressor Engine #2 - Oxidation Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - Oxidation Catalyst; CC004(Catalytic Converter): Compressor Eng | Alliance Source Testing, Inc. | 1775 | NSPS 1.0 g/Hp-hr & 82ppm @ 15%O2, TV 1.96lb/hr | 1698 *all NOx are 2 run average (P005) | NSPS .3 g/Hp-hr & 23.85ppm @ 15%O2, TV 1.05lb/hr | 7E | Nitrogen Oxide | PASS | NA | Y | The report was accepted as verification of compliance by the OEPA. However a few instances onsite were witnessed and variances were allowed to the testers for only accepting two runs as verification of compliance for P005 (NOx) and P009 (CO). Many issues could be attributed to the cold weather, however are preventable, and all efforts to prevent these issues from happening in the future will, and have been, taken into account for future test acceptance.
2014 | 324 | 0210002039 | Kilgore Compressor Station-Utica Gas Services, LLC | Pontiff Rd | Kilgore | 43988 |  | Carroll | P006 | 1,775 hp NG-fired 4SLB Stationary ICE equipped w/catalyst Caterpillar G3606: Serial Number: 4ZS01805 | 2014-01-16 | CC001(Catalytic Converter): Compressor Engine #1 - Oxidation Catalyst; CC002(Catalytic Converter): Compressor Engine #2 - Oxidation Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - Oxidation Catalyst; CC004(Catalytic Converter): Compressor Eng | Alliance Source Testing, Inc. | 1775 | NSPS 1.0 g/Hp-hr & 82ppm @ 15%O2, TV 1.96lb/hr | 1698 | NSPS .3 g/Hp-hr & 23.0ppm @ 15%O2, TV 1.04lb/hr | 7E | Nitrogen Oxide | PASS | NA | Y | The report was accepted as verification of compliance by the OEPA. However a few instances onsite were witnessed and variances were allowed to the testers for only accepting two runs as verification of compliance for P005 (NOx) and P009 (CO). Many issues could be attributed to the cold weather, however are preventable, and all efforts to prevent these issues from happening in the future will, and have been, taken into account for future test acceptance.
2014 | 327 | 0210002039 | Kilgore Compressor Station-Utica Gas Services, LLC | Pontiff Rd | Kilgore | 43988 |  | Carroll | P007 | 1,775 hp NG-fired 4SLB Stationary ICE equipped w/catalyst Caterpillar G3606: Serial Number: 4ZS01807 | 2014-01-16 | CC001(Catalytic Converter): Compressor Engine #1 - Oxidation Catalyst; CC002(Catalytic Converter): Compressor Engine #2 - Oxidation Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - Oxidation Catalyst; CC004(Catalytic Converter): Compressor Eng | Alliance Source Testing, Inc. | 1775 | NSPS 1.0 g/Hp-hr & 82ppm @ 15%O2, TV 1.96lb/hr | 1716 | NSPS 0.2 g/Hp-hr & 20.2ppm @ 15%O2, TV .91lb/hr | 7E | Nitrogen Oxide | PASS | NA | Y | The report was accepted as verification of compliance by the OEPA. However a few instances onsite were witnessed and variances were allowed to the testers for only accepting two runs as verification of compliance for P005 (NOx) and P009 (CO). Many issues could be attributed to the cold weather, however are preventable, and all efforts to prevent these issues from happening in the future will, and have been, taken into account for future test acceptance.
2014 | 328 | 0210002039 | Kilgore Compressor Station-Utica Gas Services, LLC | Pontiff Rd | Kilgore | 43988 |  | Carroll | P008 | 1,775 hp NG-fired 4SLB Stationary ICE equipped w/catalyst Caterpillar G3606: Serial Number: 4ZS01808 | 2014-01-16 | CC001(Catalytic Converter): Compressor Engine #1 - Oxidation Catalyst; CC002(Catalytic Converter): Compressor Engine #2 - Oxidation Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - Oxidation Catalyst; CC004(Catalytic Converter): Compressor Eng | Alliance Source Testing, Inc. | 1775 | NSPS 1.0 g/Hp-hr & 82ppm @ 15%O2, TV 1.96lb/hr | 1769 | NSPS 0.3 g/Hp-hr & 21.4ppm @ 15%O2, TV .96lb/hr | 7E | Nitrogen Oxide | PASS | NA | Y | The report was accepted as verification of compliance by the OEPA. However a few instances onsite were witnessed and variances were allowed to the testers for only accepting two runs as verification of compliance for P005 (NOx) and P009 (CO). Many issues could be attributed to the cold weather, however are preventable, and all efforts to prevent these issues from happening in the future will, and have been, taken into account for future test acceptance.
2014 | 333 | 0210002039 | Kilgore Compressor Station-Utica Gas Services, LLC | Pontiff Rd | Kilgore | 43988 |  | Carroll | P009 | 1,775 hp NG-fired 4SLB Stationary ICE equipped w/catalyst Caterpillar G3606: Serial Number: 4ZS01776 | 2014-01-16 | CC001(Catalytic Converter): Compressor Engine #1 - Oxidation Catalyst; CC002(Catalytic Converter): Compressor Engine #2 - Oxidation Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - Oxidation Catalyst; CC004(Catalytic Converter): Compressor Eng | Alliance Source Testing, Inc. | 1775 | NSPS 1.0 g/Hp-hr & 82ppm @ 15%O2, TV 1.96lb/hr | 1722 | NSPS 0.3 g/Hp-hr & 23.9ppm @ 15%O2, TV 1.07lb/hr | 7E | Nitrogen Oxide | PASS | NA | Y | The report was accepted as verification of compliance by the OEPA. However a few instances onsite were witnessed and variances were allowed to the testers for only accepting two runs as verification of compliance for P005 (NOx) and P009 (CO). Many issues could be attributed to the cold weather, however are preventable, and all efforts to prevent these issues from happening in the future will, and have been, taken into account for future test acceptance.
2014 | 335 | 0210002039 | Kilgore Compressor Station-Utica Gas Services, LLC | Pontiff Rd | Kilgore | 43988 |  | Carroll | P010 | 1,775 hp NG-fired 4SLB Stationary ICE equipped w/catalyst Caterpillar G3606: Serial Number: 4ZS01814 | 2014-01-16 | CC001(Catalytic Converter): Compressor Engine #1 - Oxidation Catalyst; CC002(Catalytic Converter): Compressor Engine #2 - Oxidation Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - Oxidation Catalyst; CC004(Catalytic Converter): Compressor Eng | Alliance Source Testing, Inc. | 1775 | NSPS 1.0 g/Hp-hr & 82ppm @ 15%O2, TV 1.96lb/hr | 1663 | NSPS 0.4 g/Hp-hr & 30.7ppm @ 15%O2, TV 1.35lb/hr | 7E | Nitrogen Oxide | PASS | NA | Y | The report was accepted as verification of compliance by the OEPA. However a few instances onsite were witnessed and variances were allowed to the testers for only accepting two runs as verification of compliance for P005 (NOx) and P009 (CO). Many issues could be attributed to the cold weather, however are preventable, and all efforts to prevent these issues from happening in the future will, and have been, taken into account for future test acceptance.
2014 | 348 | 0210002039 | Kilgore Compressor Station-Utica Gas Services, LLC | Pontiff Rd | Kilgore | 43988 |  | Carroll | P001 | 1,775 hp NG-fired 4SLB Stationary ICE equipped w/catalyst Caterpillar G3606 Serial Number: 4ZS01713 | 2014-01-17 | CC001(Catalytic Converter): Compressor Engine #1 - Oxidation Catalyst; CC002(Catalytic Converter): Compressor Engine #2 - Oxidation Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - Oxidation Catalyst; CC004(Catalytic Converter): Compressor Eng | Alliance Source Testing, Inc. | 1775 | NSPS 1.0 g/Hp-hr & 82ppm @ 15%O2, TV 1.96lb/hr | 1722 | NSPS 0.2 g/Hp-hr & 15.9ppm @ 15%O2, TV .72lb/hr | 7E | Nitrogen Oxide | PASS | NA | Y | The report was accepted as verification of compliance by the OEPA. However a few instances onsite were witnessed and variances were allowed to the testers for only accepting two runs as verification of compliance for P005 (NOx) and P009 (CO). Many issues could be attributed to the cold weather, however are preventable, and all efforts to prevent these issues from happening in the future will, and have been, taken into account for future test acceptance.
2014 | 350 | 0210002039 | Kilgore Compressor Station-Utica Gas Services, LLC | Pontiff Rd | Kilgore | 43988 |  | Carroll | P002 | 1,775 hp NG-fired 4SLB Stationary ICE equipped w/catalyst Caterpillar G3606: Serial Number: 4ZS01796 | 2014-01-17 | CC001(Catalytic Converter): Compressor Engine #1 - Oxidation Catalyst; CC002(Catalytic Converter): Compressor Engine #2 - Oxidation Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - Oxidation Catalyst; CC004(Catalytic Converter): Compressor Eng | Alliance Source Testing, Inc. | 1775 | NSPS 1.0 g/Hp-hr & 82ppm @ 15%O2, TV 1.96lb/hr | 1698 | NSPS 0.3 g/Hp-hr & 24.1ppm @ 15%O2, TV 1.08lb/hr | 7E | Nitrogen Oxide | PASS | NA | Y | The report was accepted as verification of compliance by the OEPA. However a few instances onsite were witnessed and variances were allowed to the testers for only accepting two runs as verification of compliance for P005 (NOx) and P009 (CO). Many issues could be attributed to the cold weather, however are preventable, and all efforts to prevent these issues from happening in the future will, and have been, taken into account for future test acceptance.
2014 | 353 | 0210002039 | Kilgore Compressor Station-Utica Gas Services, LLC | Pontiff Rd | Kilgore | 43988 |  | Carroll | P003 | 1,775 hp NG-fired 4SLB Stationary ICE equipped w/catalyst Caterpillar G3606: Serial Number: 4ZS01797 | 2014-01-17 | CC001(Catalytic Converter): Compressor Engine #1 - Oxidation Catalyst; CC002(Catalytic Converter): Compressor Engine #2 - Oxidation Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - Oxidation Catalyst; CC004(Catalytic Converter): Compressor Eng | Alliance Source Testing, Inc. | 1775 | NSPS 1.0 g/Hp-hr & 82ppm @ 15%O2, TV 1.96lb/hr | 1669 | NSPS 0.3 g/Hp-hr & 22.6ppm @ 15%O2, TV 1.00lb/hr | 7E | Nitrogen Oxide | PASS | NA | Y | The report was accepted as verification of compliance by the OEPA. However a few instances onsite were witnessed and variances were allowed to the testers for only accepting two runs as verification of compliance for P005 (NOx) and P009 (CO). Many issues could be attributed to the cold weather, however are preventable, and all efforts to prevent these issues from happening in the future will, and have been, taken into account for future test acceptance.
2014 | 356 | 0210002039 | Kilgore Compressor Station-Utica Gas Services, LLC | Pontiff Rd | Kilgore | 43988 |  | Carroll | P004 | 1,775 hp NG-fired 4SLB Stationary ICE equipped w/catalyst Caterpillar G3606: Serial Number: 4ZS01800 | 2014-01-17 | CC001(Catalytic Converter): Compressor Engine #1 - Oxidation Catalyst; CC002(Catalytic Converter): Compressor Engine #2 - Oxidation Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - Oxidation Catalyst; CC004(Catalytic Converter): Compressor Eng | Alliance Source Testing, Inc. | 1775 | NSPS 1.0 g/Hp-hr & 82ppm @ 15%O2, TV 1.96lb/hr | 1698 | NSPS 0.3 g/Hp-hr & 25.3ppm @ 15%O2, TV 1.15lb/hr | 7E | Nitrogen Oxide | PASS | NA | Y | The report was accepted as verification of compliance by the OEPA. However a few instances onsite were witnessed and variances were allowed to the testers for only accepting two runs as verification of compliance for P005 (NOx) and P009 (CO). Many issues could be attributed to the cold weather, however are preventable, and all efforts to prevent these issues from happening in the future will, and have been, taken into account for future test acceptance.
2014 | 359 | 0210002039 | Kilgore Compressor Station-Utica Gas Services, LLC | Pontiff Rd | Kilgore | 43988 |  | Carroll | P005 | 1,775 hp NG-fired 4SLB Stationary ICE equipped w/catalyst Caterpillar G3606: Serial Number: 4ZS01804 | 2014-01-17 | CC001(Catalytic Converter): Compressor Engine #1 - Oxidation Catalyst; CC002(Catalytic Converter): Compressor Engine #2 - Oxidation Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - Oxidation Catalyst; CC004(Catalytic Converter): Compressor Eng | Alliance Source Testing, Inc. | 1775 | NSPS 1.0 g/Hp-hr & 82ppm @ 15%O2, TV 1.96lb/hr | 1698 *all NOx are 2 run average (P005) | NSPS .3 g/Hp-hr & 23.85ppm @ 15%O2, TV 1.05lb/hr | 7E | Nitrogen Oxide | PASS | NA | Y | The report was accepted as verification of compliance by the OEPA. However a few instances onsite were witnessed and variances were allowed to the testers for only accepting two runs as verification of compliance for P005 (NOx) and P009 (CO). Many issues could be attributed to the cold weather, however are preventable, and all efforts to prevent these issues from happening in the future will, and have been, taken into account for future test acceptance.
2014 | 363 | 0210002039 | Kilgore Compressor Station-Utica Gas Services, LLC | Pontiff Rd | Kilgore | 43988 |  | Carroll | P006 | 1,775 hp NG-fired 4SLB Stationary ICE equipped w/catalyst Caterpillar G3606: Serial Number: 4ZS01805 | 2014-01-17 | CC001(Catalytic Converter): Compressor Engine #1 - Oxidation Catalyst; CC002(Catalytic Converter): Compressor Engine #2 - Oxidation Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - Oxidation Catalyst; CC004(Catalytic Converter): Compressor Eng | Alliance Source Testing, Inc. | 1775 | NSPS 1.0 g/Hp-hr & 82ppm @ 15%O2, TV 1.96lb/hr | 1698 | NSPS .3 g/Hp-hr & 23.0ppm @ 15%O2, TV 1.04lb/hr | 7E | Nitrogen Oxide | PASS | NA | Y | The report was accepted as verification of compliance by the OEPA. However a few instances onsite were witnessed and variances were allowed to the testers for only accepting two runs as verification of compliance for P005 (NOx) and P009 (CO). Many issues could be attributed to the cold weather, however are preventable, and all efforts to prevent these issues from happening in the future will, and have been, taken into account for future test acceptance.
2014 | 364 | 0210002039 | Kilgore Compressor Station-Utica Gas Services, LLC | Pontiff Rd | Kilgore | 43988 |  | Carroll | P007 | 1,775 hp NG-fired 4SLB Stationary ICE equipped w/catalyst Caterpillar G3606: Serial Number: 4ZS01807 | 2014-01-17 | CC001(Catalytic Converter): Compressor Engine #1 - Oxidation Catalyst; CC002(Catalytic Converter): Compressor Engine #2 - Oxidation Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - Oxidation Catalyst; CC004(Catalytic Converter): Compressor Eng | Alliance Source Testing, Inc. | 1775 | NSPS 1.0 g/Hp-hr & 82ppm @ 15%O2, TV 1.96lb/hr | 1716 | NSPS 0.2 g/Hp-hr & 20.2ppm @ 15%O2, TV .91lb/hr | 7E | Nitrogen Oxide | PASS | NA | Y | The report was accepted as verification of compliance by the OEPA. However a few instances onsite were witnessed and variances were allowed to the testers for only accepting two runs as verification of compliance for P005 (NOx) and P009 (CO). Many issues could be attributed to the cold weather, however are preventable, and all efforts to prevent these issues from happening in the future will, and have been, taken into account for future test acceptance.
2014 | 368 | 0210002039 | Kilgore Compressor Station-Utica Gas Services, LLC | Pontiff Rd | Kilgore | 43988 |  | Carroll | P008 | 1,775 hp NG-fired 4SLB Stationary ICE equipped w/catalyst Caterpillar G3606: Serial Number: 4ZS01808 | 2014-01-17 | CC001(Catalytic Converter): Compressor Engine #1 - Oxidation Catalyst; CC002(Catalytic Converter): Compressor Engine #2 - Oxidation Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - Oxidation Catalyst; CC004(Catalytic Converter): Compressor Eng | Alliance Source Testing, Inc. | 1775 | NSPS 1.0 g/Hp-hr & 82ppm @ 15%O2, TV 1.96lb/hr | 1769 | NSPS 0.3 g/Hp-hr & 21.4ppm @ 15%O2, TV .96lb/hr | 7E | Nitrogen Oxide | PASS | NA | Y | The report was accepted as verification of compliance by the OEPA. However a few instances onsite were witnessed and variances were allowed to the testers for only accepting two runs as verification of compliance for P005 (NOx) and P009 (CO). Many issues could be attributed to the cold weather, however are preventable, and all efforts to prevent these issues from happening in the future will, and have been, taken into account for future test acceptance.
2014 | 371 | 0210002039 | Kilgore Compressor Station-Utica Gas Services, LLC | Pontiff Rd | Kilgore | 43988 |  | Carroll | P009 | 1,775 hp NG-fired 4SLB Stationary ICE equipped w/catalyst Caterpillar G3606: Serial Number: 4ZS01776 | 2014-01-17 | CC001(Catalytic Converter): Compressor Engine #1 - Oxidation Catalyst; CC002(Catalytic Converter): Compressor Engine #2 - Oxidation Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - Oxidation Catalyst; CC004(Catalytic Converter): Compressor Eng | Alliance Source Testing, Inc. | 1775 | NSPS 1.0 g/Hp-hr & 82ppm @ 15%O2, TV 1.96lb/hr | 1722 | NSPS 0.3 g/Hp-hr & 23.9ppm @ 15%O2, TV 1.07lb/hr | 7E | Nitrogen Oxide | PASS | NA | Y | The report was accepted as verification of compliance by the OEPA. However a few instances onsite were witnessed and variances were allowed to the testers for only accepting two runs as verification of compliance for P005 (NOx) and P009 (CO). Many issues could be attributed to the cold weather, however are preventable, and all efforts to prevent these issues from happening in the future will, and have been, taken into account for future test acceptance.
2014 | 375 | 0210002039 | Kilgore Compressor Station-Utica Gas Services, LLC | Pontiff Rd | Kilgore | 43988 |  | Carroll | P010 | 1,775 hp NG-fired 4SLB Stationary ICE equipped w/catalyst Caterpillar G3606: Serial Number: 4ZS01814 | 2014-01-17 | CC001(Catalytic Converter): Compressor Engine #1 - Oxidation Catalyst; CC002(Catalytic Converter): Compressor Engine #2 - Oxidation Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - Oxidation Catalyst; CC004(Catalytic Converter): Compressor Eng | Alliance Source Testing, Inc. | 1775 | NSPS 1.0 g/Hp-hr & 82ppm @ 15%O2, TV 1.96lb/hr | 1663 | NSPS 0.4 g/Hp-hr & 30.7ppm @ 15%O2, TV 1.35lb/hr | 7E | Nitrogen Oxide | PASS | NA | Y | The report was accepted as verification of compliance by the OEPA. However a few instances onsite were witnessed and variances were allowed to the testers for only accepting two runs as verification of compliance for P005 (NOx) and P009 (CO). Many issues could be attributed to the cold weather, however are preventable, and all efforts to prevent these issues from happening in the future will, and have been, taken into account for future test acceptance.
2014 | 385 | 0210002039 | Kilgore Compressor Station-Utica Gas Services, LLC | Pontiff Rd | Kilgore | 43988 |  | Carroll | P001 | 1,775 hp NG-fired 4SLB Stationary ICE equipped w/catalyst Caterpillar G3606 Serial Number: 4ZS01713 | 2014-01-18 | CC001(Catalytic Converter): Compressor Engine #1 - Oxidation Catalyst; CC002(Catalytic Converter): Compressor Engine #2 - Oxidation Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - Oxidation Catalyst; CC004(Catalytic Converter): Compressor Eng | Alliance Source Testing, Inc. | 1775 | NSPS 1.0 g/Hp-hr & 82ppm @ 15%O2, TV 1.96lb/hr | 1722 | NSPS 0.2 g/Hp-hr & 15.9ppm @ 15%O2, TV .72lb/hr | 7E | Nitrogen Oxide | PASS | NA | Y | The report was accepted as verification of compliance by the OEPA. However a few instances onsite were witnessed and variances were allowed to the testers for only accepting two runs as verification of compliance for P005 (NOx) and P009 (CO). Many issues could be attributed to the cold weather, however are preventable, and all efforts to prevent these issues from happening in the future will, and have been, taken into account for future test acceptance.
2014 | 388 | 0210002039 | Kilgore Compressor Station-Utica Gas Services, LLC | Pontiff Rd | Kilgore | 43988 |  | Carroll | P002 | 1,775 hp NG-fired 4SLB Stationary ICE equipped w/catalyst Caterpillar G3606: Serial Number: 4ZS01796 | 2014-01-18 | CC001(Catalytic Converter): Compressor Engine #1 - Oxidation Catalyst; CC002(Catalytic Converter): Compressor Engine #2 - Oxidation Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - Oxidation Catalyst; CC004(Catalytic Converter): Compressor Eng | Alliance Source Testing, Inc. | 1775 | NSPS 1.0 g/Hp-hr & 82ppm @ 15%O2, TV 1.96lb/hr | 1698 | NSPS 0.3 g/Hp-hr & 24.1ppm @ 15%O2, TV 1.08lb/hr | 7E | Nitrogen Oxide | PASS | NA | Y | The report was accepted as verification of compliance by the OEPA. However a few instances onsite were witnessed and variances were allowed to the testers for only accepting two runs as verification of compliance for P005 (NOx) and P009 (CO). Many issues could be attributed to the cold weather, however are preventable, and all efforts to prevent these issues from happening in the future will, and have been, taken into account for future test acceptance.
2014 | 393 | 0210002039 | Kilgore Compressor Station-Utica Gas Services, LLC | Pontiff Rd | Kilgore | 43988 |  | Carroll | P003 | 1,775 hp NG-fired 4SLB Stationary ICE equipped w/catalyst Caterpillar G3606: Serial Number: 4ZS01797 | 2014-01-18 | CC001(Catalytic Converter): Compressor Engine #1 - Oxidation Catalyst; CC002(Catalytic Converter): Compressor Engine #2 - Oxidation Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - Oxidation Catalyst; CC004(Catalytic Converter): Compressor Eng | Alliance Source Testing, Inc. | 1775 | NSPS 1.0 g/Hp-hr & 82ppm @ 15%O2, TV 1.96lb/hr | 1669 | NSPS 0.3 g/Hp-hr & 22.6ppm @ 15%O2, TV 1.00lb/hr | 7E | Nitrogen Oxide | PASS | NA | Y | The report was accepted as verification of compliance by the OEPA. However a few instances onsite were witnessed and variances were allowed to the testers for only accepting two runs as verification of compliance for P005 (NOx) and P009 (CO). Many issues could be attributed to the cold weather, however are preventable, and all efforts to prevent these issues from happening in the future will, and have been, taken into account for future test acceptance.
2014 | 396 | 0210002039 | Kilgore Compressor Station-Utica Gas Services, LLC | Pontiff Rd | Kilgore | 43988 |  | Carroll | P004 | 1,775 hp NG-fired 4SLB Stationary ICE equipped w/catalyst Caterpillar G3606: Serial Number: 4ZS01800 | 2014-01-18 | CC001(Catalytic Converter): Compressor Engine #1 - Oxidation Catalyst; CC002(Catalytic Converter): Compressor Engine #2 - Oxidation Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - Oxidation Catalyst; CC004(Catalytic Converter): Compressor Eng | Alliance Source Testing, Inc. | 1775 | NSPS 1.0 g/Hp-hr & 82ppm @ 15%O2, TV 1.96lb/hr | 1698 | NSPS 0.3 g/Hp-hr & 25.3ppm @ 15%O2, TV 1.15lb/hr | 7E | Nitrogen Oxide | PASS | NA | Y | The report was accepted as verification of compliance by the OEPA. However a few instances onsite were witnessed and variances were allowed to the testers for only accepting two runs as verification of compliance for P005 (NOx) and P009 (CO). Many issues could be attributed to the cold weather, however are preventable, and all efforts to prevent these issues from happening in the future will, and have been, taken into account for future test acceptance.
2014 | 397 | 0210002039 | Kilgore Compressor Station-Utica Gas Services, LLC | Pontiff Rd | Kilgore | 43988 |  | Carroll | P005 | 1,775 hp NG-fired 4SLB Stationary ICE equipped w/catalyst Caterpillar G3606: Serial Number: 4ZS01804 | 2014-01-18 | CC001(Catalytic Converter): Compressor Engine #1 - Oxidation Catalyst; CC002(Catalytic Converter): Compressor Engine #2 - Oxidation Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - Oxidation Catalyst; CC004(Catalytic Converter): Compressor Eng | Alliance Source Testing, Inc. | 1775 | NSPS 1.0 g/Hp-hr & 82ppm @ 15%O2, TV 1.96lb/hr | 1698 *all NOx are 2 run average (P005) | NSPS .3 g/Hp-hr & 23.85ppm @ 15%O2, TV 1.05lb/hr | 7E | Nitrogen Oxide | PASS | NA | Y | The report was accepted as verification of compliance by the OEPA. However a few instances onsite were witnessed and variances were allowed to the testers for only accepting two runs as verification of compliance for P005 (NOx) and P009 (CO). Many issues could be attributed to the cold weather, however are preventable, and all efforts to prevent these issues from happening in the future will, and have been, taken into account for future test acceptance.
2014 | 402 | 0210002039 | Kilgore Compressor Station-Utica Gas Services, LLC | Pontiff Rd | Kilgore | 43988 |  | Carroll | P006 | 1,775 hp NG-fired 4SLB Stationary ICE equipped w/catalyst Caterpillar G3606: Serial Number: 4ZS01805 | 2014-01-18 | CC001(Catalytic Converter): Compressor Engine #1 - Oxidation Catalyst; CC002(Catalytic Converter): Compressor Engine #2 - Oxidation Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - Oxidation Catalyst; CC004(Catalytic Converter): Compressor Eng | Alliance Source Testing, Inc. | 1775 | NSPS 1.0 g/Hp-hr & 82ppm @ 15%O2, TV 1.96lb/hr | 1698 | NSPS .3 g/Hp-hr & 23.0ppm @ 15%O2, TV 1.04lb/hr | 7E | Nitrogen Oxide | PASS | NA | Y | The report was accepted as verification of compliance by the OEPA. However a few instances onsite were witnessed and variances were allowed to the testers for only accepting two runs as verification of compliance for P005 (NOx) and P009 (CO). Many issues could be attributed to the cold weather, however are preventable, and all efforts to prevent these issues from happening in the future will, and have been, taken into account for future test acceptance.
2014 | 403 | 0210002039 | Kilgore Compressor Station-Utica Gas Services, LLC | Pontiff Rd | Kilgore | 43988 |  | Carroll | P007 | 1,775 hp NG-fired 4SLB Stationary ICE equipped w/catalyst Caterpillar G3606: Serial Number: 4ZS01807 | 2014-01-18 | CC001(Catalytic Converter): Compressor Engine #1 - Oxidation Catalyst; CC002(Catalytic Converter): Compressor Engine #2 - Oxidation Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - Oxidation Catalyst; CC004(Catalytic Converter): Compressor Eng | Alliance Source Testing, Inc. | 1775 | NSPS 1.0 g/Hp-hr & 82ppm @ 15%O2, TV 1.96lb/hr | 1716 | NSPS 0.2 g/Hp-hr & 20.2ppm @ 15%O2, TV .91lb/hr | 7E | Nitrogen Oxide | PASS | NA | Y | The report was accepted as verification of compliance by the OEPA. However a few instances onsite were witnessed and variances were allowed to the testers for only accepting two runs as verification of compliance for P005 (NOx) and P009 (CO). Many issues could be attributed to the cold weather, however are preventable, and all efforts to prevent these issues from happening in the future will, and have been, taken into account for future test acceptance.
2014 | 408 | 0210002039 | Kilgore Compressor Station-Utica Gas Services, LLC | Pontiff Rd | Kilgore | 43988 |  | Carroll | P008 | 1,775 hp NG-fired 4SLB Stationary ICE equipped w/catalyst Caterpillar G3606: Serial Number: 4ZS01808 | 2014-01-18 | CC001(Catalytic Converter): Compressor Engine #1 - Oxidation Catalyst; CC002(Catalytic Converter): Compressor Engine #2 - Oxidation Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - Oxidation Catalyst; CC004(Catalytic Converter): Compressor Eng | Alliance Source Testing, Inc. | 1775 | NSPS 1.0 g/Hp-hr & 82ppm @ 15%O2, TV 1.96lb/hr | 1769 | NSPS 0.3 g/Hp-hr & 21.4ppm @ 15%O2, TV .96lb/hr | 7E | Nitrogen Oxide | PASS | NA | Y | The report was accepted as verification of compliance by the OEPA. However a few instances onsite were witnessed and variances were allowed to the testers for only accepting two runs as verification of compliance for P005 (NOx) and P009 (CO). Many issues could be attributed to the cold weather, however are preventable, and all efforts to prevent these issues from happening in the future will, and have been, taken into account for future test acceptance.
2014 | 410 | 0210002039 | Kilgore Compressor Station-Utica Gas Services, LLC | Pontiff Rd | Kilgore | 43988 |  | Carroll | P009 | 1,775 hp NG-fired 4SLB Stationary ICE equipped w/catalyst Caterpillar G3606: Serial Number: 4ZS01776 | 2014-01-18 | CC001(Catalytic Converter): Compressor Engine #1 - Oxidation Catalyst; CC002(Catalytic Converter): Compressor Engine #2 - Oxidation Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - Oxidation Catalyst; CC004(Catalytic Converter): Compressor Eng | Alliance Source Testing, Inc. | 1775 | NSPS 1.0 g/Hp-hr & 82ppm @ 15%O2, TV 1.96lb/hr | 1722 | NSPS 0.3 g/Hp-hr & 23.9ppm @ 15%O2, TV 1.07lb/hr | 7E | Nitrogen Oxide | PASS | NA | Y | The report was accepted as verification of compliance by the OEPA. However a few instances onsite were witnessed and variances were allowed to the testers for only accepting two runs as verification of compliance for P005 (NOx) and P009 (CO). Many issues could be attributed to the cold weather, however are preventable, and all efforts to prevent these issues from happening in the future will, and have been, taken into account for future test acceptance.
2014 | 413 | 0210002039 | Kilgore Compressor Station-Utica Gas Services, LLC | Pontiff Rd | Kilgore | 43988 |  | Carroll | P010 | 1,775 hp NG-fired 4SLB Stationary ICE equipped w/catalyst Caterpillar G3606: Serial Number: 4ZS01814 | 2014-01-18 | CC001(Catalytic Converter): Compressor Engine #1 - Oxidation Catalyst; CC002(Catalytic Converter): Compressor Engine #2 - Oxidation Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - Oxidation Catalyst; CC004(Catalytic Converter): Compressor Eng | Alliance Source Testing, Inc. | 1775 | NSPS 1.0 g/Hp-hr & 82ppm @ 15%O2, TV 1.96lb/hr | 1663 | NSPS 0.4 g/Hp-hr & 30.7ppm @ 15%O2, TV 1.35lb/hr | 7E | Nitrogen Oxide | PASS | NA | Y | The report was accepted as verification of compliance by the OEPA. However a few instances onsite were witnessed and variances were allowed to the testers for only accepting two runs as verification of compliance for P005 (NOx) and P009 (CO). Many issues could be attributed to the cold weather, however are preventable, and all efforts to prevent these issues from happening in the future will, and have been, taken into account for future test acceptance.
2014 | 426 | 0210002039 | Kilgore Compressor Station-Utica Gas Services, LLC | Pontiff Rd | Kilgore | 43988 |  | Carroll | P001 | 1,775 hp NG-fired 4SLB Stationary ICE equipped w/catalyst Caterpillar G3606 Serial Number: 4ZS01713 | 2014-12-15 | CC001(Catalytic Converter): Compressor Engine #1 - Oxidation Catalyst; CC002(Catalytic Converter): Compressor Engine #2 - Oxidation Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - Oxidation Catalyst; CC004(Catalytic Converter): Compressor Eng | Alliance Source Testing, Inc. | 1775 | 1.0 g/Hp-hr & 1.96lb/hr | 1651 | 0.4 g/Hp-hr & 1.36lb/hr | 7E | Nitrogen Oxide | PASS | NA | Y
2014 | 429 | 0210002039 | Kilgore Compressor Station-Utica Gas Services, LLC | Pontiff Rd | Kilgore | 43988 |  | Carroll | P002 | 1,775 hp NG-fired 4SLB Stationary ICE equipped w/catalyst Caterpillar G3606: Serial Number: 4ZS01796 | 2014-12-15 | CC001(Catalytic Converter): Compressor Engine #1 - Oxidation Catalyst; CC002(Catalytic Converter): Compressor Engine #2 - Oxidation Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - Oxidation Catalyst; CC004(Catalytic Converter): Compressor Eng | Alliance Source Testing, Inc. | 1775 | 1.0 g/Hp-hr & 1.96lb/hr | 1633 | 0.3 g/Hp-hr & 1.05lb/hr | 7E | Nitrogen Oxide | PASS | NA | Y
2014 | 432 | 0210002039 | Kilgore Compressor Station-Utica Gas Services, LLC | Pontiff Rd | Kilgore | 43988 |  | Carroll | P003 | 1,775 hp NG-fired 4SLB Stationary ICE equipped w/catalyst Caterpillar G3606: Serial Number: 4ZS01797 | 2014-12-15 | CC001(Catalytic Converter): Compressor Engine #1 - Oxidation Catalyst; CC002(Catalytic Converter): Compressor Engine #2 - Oxidation Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - Oxidation Catalyst; CC004(Catalytic Converter): Compressor Eng | Alliance Source Testing, Inc. | 1775 | 1.0 g/Hp-hr & 1.96lb/hr | 1598 | 0.4 g/Hp-hr & 1.33lb/hr | 7E | Nitrogen Oxide | PASS | NA | Y
2014 | 434 | 0210002039 | Kilgore Compressor Station-Utica Gas Services, LLC | Pontiff Rd | Kilgore | 43988 |  | Carroll | P004 | 1,775 hp NG-fired 4SLB Stationary ICE equipped w/catalyst Caterpillar G3606: Serial Number: 4ZS01800 | 2014-12-15 | CC001(Catalytic Converter): Compressor Engine #1 - Oxidation Catalyst; CC002(Catalytic Converter): Compressor Engine #2 - Oxidation Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - Oxidation Catalyst; CC004(Catalytic Converter): Compressor Eng | Alliance Source Testing, Inc. | 1775 | 1.0 g/Hp-hr & 1.96lb/hr | 1651 | 0.4 g/Hp-hr & 1.26lb/hr | 7E | Nitrogen Oxide | PASS | NA | Y
2014 | 437 | 0210002039 | Kilgore Compressor Station-Utica Gas Services, LLC | Pontiff Rd | Kilgore | 43988 |  | Carroll | P005 | 1,775 hp NG-fired 4SLB Stationary ICE equipped w/catalyst Caterpillar G3606: Serial Number: 4ZS01804 | 2014-12-15 | CC001(Catalytic Converter): Compressor Engine #1 - Oxidation Catalyst; CC002(Catalytic Converter): Compressor Engine #2 - Oxidation Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - Oxidation Catalyst; CC004(Catalytic Converter): Compressor Eng | Alliance Source Testing, Inc. | 1775 | 1.0 g/Hp-hr & 1.96lb/hr | 1604 | 0.5 g/Hp-hr & 1.57lb/hr | 7E | Nitrogen Oxide | PASS | NA | Y
2014 | 440 | 0210002039 | Kilgore Compressor Station-Utica Gas Services, LLC | Pontiff Rd | Kilgore | 43988 |  | Carroll | P006 | 1,775 hp NG-fired 4SLB Stationary ICE equipped w/catalyst Caterpillar G3606: Serial Number: 4ZS01805 | 2014-12-15 | CC001(Catalytic Converter): Compressor Engine #1 - Oxidation Catalyst; CC002(Catalytic Converter): Compressor Engine #2 - Oxidation Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - Oxidation Catalyst; CC004(Catalytic Converter): Compressor Eng | Alliance Source Testing, Inc. | 1775 | 1.0 g/Hp-hr & 1.96lb/hr | 1604 | 0.4 g/Hp-hr & 1.35lb/hr | 7E | Nitrogen Oxide | PASS | NA | Y
2014 | 444 | 0210002039 | Kilgore Compressor Station-Utica Gas Services, LLC | Pontiff Rd | Kilgore | 43988 |  | Carroll | P007 | 1,775 hp NG-fired 4SLB Stationary ICE equipped w/catalyst Caterpillar G3606: Serial Number: 4ZS01807 | 2014-12-15 | CC001(Catalytic Converter): Compressor Engine #1 - Oxidation Catalyst; CC002(Catalytic Converter): Compressor Engine #2 - Oxidation Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - Oxidation Catalyst; CC004(Catalytic Converter): Compressor Eng | Alliance Source Testing, Inc. | 1775 | 1.0 g/Hp-hr & 1.96lb/hr | 1610 | 0.4 g/Hp-hr & 1.41lb/hr | 7E | Nitrogen Oxide | PASS | NA | Y
2014 | 446 | 0210002039 | Kilgore Compressor Station-Utica Gas Services, LLC | Pontiff Rd | Kilgore | 43988 |  | Carroll | P008 | 1,775 hp NG-fired 4SLB Stationary ICE equipped w/catalyst Caterpillar G3606: Serial Number: 4ZS01808 | 2014-12-15 | CC001(Catalytic Converter): Compressor Engine #1 - Oxidation Catalyst; CC002(Catalytic Converter): Compressor Engine #2 - Oxidation Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - Oxidation Catalyst; CC004(Catalytic Converter): Compressor Eng | Alliance Source Testing, Inc. | 1775 | 1.0 g/Hp-hr & 1.96lb/hr | 1687 | 0.4 g/Hp-hr & 1.30lb/hr | 7E | Nitrogen Oxide | PASS | NA | Y
2014 | 448 | 0210002039 | Kilgore Compressor Station-Utica Gas Services, LLC | Pontiff Rd | Kilgore | 43988 |  | Carroll | P009 | 1,775 hp NG-fired 4SLB Stationary ICE equipped w/catalyst Caterpillar G3606: Serial Number: 4ZS01776 | 2014-12-15 | CC001(Catalytic Converter): Compressor Engine #1 - Oxidation Catalyst; CC002(Catalytic Converter): Compressor Engine #2 - Oxidation Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - Oxidation Catalyst; CC004(Catalytic Converter): Compressor Eng | Alliance Source Testing, Inc. | 1775 | 1.0 g/Hp-hr & 1.96lb/hr | 1616 | 0.3 g/Hp-hr & 1.18lb/hr | 7E | Nitrogen Oxide | PASS | NA | Y
2014 | 451 | 0210002039 | Kilgore Compressor Station-Utica Gas Services, LLC | Pontiff Rd | Kilgore | 43988 |  | Carroll | P010 | 1,775 hp NG-fired 4SLB Stationary ICE equipped w/catalyst Caterpillar G3606: Serial Number: 4ZS01814 | 2014-12-15 | CC001(Catalytic Converter): Compressor Engine #1 - Oxidation Catalyst; CC002(Catalytic Converter): Compressor Engine #2 - Oxidation Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - Oxidation Catalyst; CC004(Catalytic Converter): Compressor Eng | Alliance Source Testing, Inc. | 1775 | 1.0 g/Hp-hr & 1.96lb/hr | 1616 | 0.4 g/Hp-hr & 1.38lb/hr | 7E | Nitrogen Oxide | PASS | NA | Y
2014 | 456 | 0210002039 | Kilgore Compressor Station-Utica Gas Services, LLC | Pontiff Rd | Kilgore | 43988 |  | Carroll | P001 | 1,775 hp NG-fired 4SLB Stationary ICE equipped w/catalyst Caterpillar G3606 Serial Number: 4ZS01713 | 2014-12-16 | CC001(Catalytic Converter): Compressor Engine #1 - Oxidation Catalyst; CC002(Catalytic Converter): Compressor Engine #2 - Oxidation Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - Oxidation Catalyst; CC004(Catalytic Converter): Compressor Eng | Alliance Source Testing, Inc. | 1775 | 1.0 g/Hp-hr & 1.96lb/hr | 1651 | 0.4 g/Hp-hr & 1.36lb/hr | 7E | Nitrogen Oxide | PASS | NA | Y
2014 | 459 | 0210002039 | Kilgore Compressor Station-Utica Gas Services, LLC | Pontiff Rd | Kilgore | 43988 |  | Carroll | P002 | 1,775 hp NG-fired 4SLB Stationary ICE equipped w/catalyst Caterpillar G3606: Serial Number: 4ZS01796 | 2014-12-16 | CC001(Catalytic Converter): Compressor Engine #1 - Oxidation Catalyst; CC002(Catalytic Converter): Compressor Engine #2 - Oxidation Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - Oxidation Catalyst; CC004(Catalytic Converter): Compressor Eng | Alliance Source Testing, Inc. | 1775 | 1.0 g/Hp-hr & 1.96lb/hr | 1633 | 0.3 g/Hp-hr & 1.05lb/hr | 7E | Nitrogen Oxide | PASS | NA | Y
2014 | 461 | 0210002039 | Kilgore Compressor Station-Utica Gas Services, LLC | Pontiff Rd | Kilgore | 43988 |  | Carroll | P003 | 1,775 hp NG-fired 4SLB Stationary ICE equipped w/catalyst Caterpillar G3606: Serial Number: 4ZS01797 | 2014-12-16 | CC001(Catalytic Converter): Compressor Engine #1 - Oxidation Catalyst; CC002(Catalytic Converter): Compressor Engine #2 - Oxidation Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - Oxidation Catalyst; CC004(Catalytic Converter): Compressor Eng | Alliance Source Testing, Inc. | 1775 | 1.0 g/Hp-hr & 1.96lb/hr | 1598 | 0.4 g/Hp-hr & 1.33lb/hr | 7E | Nitrogen Oxide | PASS | NA | Y
2014 | 464 | 0210002039 | Kilgore Compressor Station-Utica Gas Services, LLC | Pontiff Rd | Kilgore | 43988 |  | Carroll | P004 | 1,775 hp NG-fired 4SLB Stationary ICE equipped w/catalyst Caterpillar G3606: Serial Number: 4ZS01800 | 2014-12-16 | CC001(Catalytic Converter): Compressor Engine #1 - Oxidation Catalyst; CC002(Catalytic Converter): Compressor Engine #2 - Oxidation Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - Oxidation Catalyst; CC004(Catalytic Converter): Compressor Eng | Alliance Source Testing, Inc. | 1775 | 1.0 g/Hp-hr & 1.96lb/hr | 1651 | 0.4 g/Hp-hr & 1.26lb/hr | 7E | Nitrogen Oxide | PASS | NA | Y
2014 | 466 | 0210002039 | Kilgore Compressor Station-Utica Gas Services, LLC | Pontiff Rd | Kilgore | 43988 |  | Carroll | P005 | 1,775 hp NG-fired 4SLB Stationary ICE equipped w/catalyst Caterpillar G3606: Serial Number: 4ZS01804 | 2014-12-16 | CC001(Catalytic Converter): Compressor Engine #1 - Oxidation Catalyst; CC002(Catalytic Converter): Compressor Engine #2 - Oxidation Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - Oxidation Catalyst; CC004(Catalytic Converter): Compressor Eng | Alliance Source Testing, Inc. | 1775 | 1.0 g/Hp-hr & 1.96lb/hr | 1604 | 0.5 g/Hp-hr & 1.57lb/hr | 7E | Nitrogen Oxide | PASS | NA | Y
2014 | 471 | 0210002039 | Kilgore Compressor Station-Utica Gas Services, LLC | Pontiff Rd | Kilgore | 43988 |  | Carroll | P006 | 1,775 hp NG-fired 4SLB Stationary ICE equipped w/catalyst Caterpillar G3606: Serial Number: 4ZS01805 | 2014-12-16 | CC001(Catalytic Converter): Compressor Engine #1 - Oxidation Catalyst; CC002(Catalytic Converter): Compressor Engine #2 - Oxidation Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - Oxidation Catalyst; CC004(Catalytic Converter): Compressor Eng | Alliance Source Testing, Inc. | 1775 | 1.0 g/Hp-hr & 1.96lb/hr | 1604 | 0.4 g/Hp-hr & 1.35lb/hr | 7E | Nitrogen Oxide | PASS | NA | Y
2014 | 472 | 0210002039 | Kilgore Compressor Station-Utica Gas Services, LLC | Pontiff Rd | Kilgore | 43988 |  | Carroll | P007 | 1,775 hp NG-fired 4SLB Stationary ICE equipped w/catalyst Caterpillar G3606: Serial Number: 4ZS01807 | 2014-12-16 | CC001(Catalytic Converter): Compressor Engine #1 - Oxidation Catalyst; CC002(Catalytic Converter): Compressor Engine #2 - Oxidation Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - Oxidation Catalyst; CC004(Catalytic Converter): Compressor Eng | Alliance Source Testing, Inc. | 1775 | 1.0 g/Hp-hr & 1.96lb/hr | 1610 | 0.4 g/Hp-hr & 1.41lb/hr | 7E | Nitrogen Oxide | PASS | NA | Y
2014 | 477 | 0210002039 | Kilgore Compressor Station-Utica Gas Services, LLC | Pontiff Rd | Kilgore | 43988 |  | Carroll | P008 | 1,775 hp NG-fired 4SLB Stationary ICE equipped w/catalyst Caterpillar G3606: Serial Number: 4ZS01808 | 2014-12-16 | CC001(Catalytic Converter): Compressor Engine #1 - Oxidation Catalyst; CC002(Catalytic Converter): Compressor Engine #2 - Oxidation Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - Oxidation Catalyst; CC004(Catalytic Converter): Compressor Eng | Alliance Source Testing, Inc. | 1775 | 1.0 g/Hp-hr & 1.96lb/hr | 1687 | 0.4 g/Hp-hr & 1.30lb/hr | 7E | Nitrogen Oxide | PASS | NA | Y
2014 | 480 | 0210002039 | Kilgore Compressor Station-Utica Gas Services, LLC | Pontiff Rd | Kilgore | 43988 |  | Carroll | P009 | 1,775 hp NG-fired 4SLB Stationary ICE equipped w/catalyst Caterpillar G3606: Serial Number: 4ZS01776 | 2014-12-16 | CC001(Catalytic Converter): Compressor Engine #1 - Oxidation Catalyst; CC002(Catalytic Converter): Compressor Engine #2 - Oxidation Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - Oxidation Catalyst; CC004(Catalytic Converter): Compressor Eng | Alliance Source Testing, Inc. | 1775 | 1.0 g/Hp-hr & 1.96lb/hr | 1616 | 0.3 g/Hp-hr & 1.18lb/hr | 7E | Nitrogen Oxide | PASS | NA | Y
2014 | 483 | 0210002039 | Kilgore Compressor Station-Utica Gas Services, LLC | Pontiff Rd | Kilgore | 43988 |  | Carroll | P010 | 1,775 hp NG-fired 4SLB Stationary ICE equipped w/catalyst Caterpillar G3606: Serial Number: 4ZS01814 | 2014-12-16 | CC001(Catalytic Converter): Compressor Engine #1 - Oxidation Catalyst; CC002(Catalytic Converter): Compressor Engine #2 - Oxidation Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - Oxidation Catalyst; CC004(Catalytic Converter): Compressor Eng | Alliance Source Testing, Inc. | 1775 | 1.0 g/Hp-hr & 1.96lb/hr | 1616 | 0.4 g/Hp-hr & 1.38lb/hr | 7E | Nitrogen Oxide | PASS | NA | Y
2014 | 486 | 0210002039 | Kilgore Compressor Station-Utica Gas Services, LLC | Pontiff Rd | Kilgore | 43988 |  | Carroll | P001 | 1,775 hp NG-fired 4SLB Stationary ICE equipped w/catalyst Caterpillar G3606 Serial Number: 4ZS01713 | 2014-12-17 | CC001(Catalytic Converter): Compressor Engine #1 - Oxidation Catalyst; CC002(Catalytic Converter): Compressor Engine #2 - Oxidation Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - Oxidation Catalyst; CC004(Catalytic Converter): Compressor Eng | Alliance Source Testing, Inc. | 1775 | 1.0 g/Hp-hr & 1.96lb/hr | 1651 | 0.4 g/Hp-hr & 1.36lb/hr | 7E | Nitrogen Oxide | PASS | NA | Y
2014 | 488 | 0210002039 | Kilgore Compressor Station-Utica Gas Services, LLC | Pontiff Rd | Kilgore | 43988 |  | Carroll | P002 | 1,775 hp NG-fired 4SLB Stationary ICE equipped w/catalyst Caterpillar G3606: Serial Number: 4ZS01796 | 2014-12-17 | CC001(Catalytic Converter): Compressor Engine #1 - Oxidation Catalyst; CC002(Catalytic Converter): Compressor Engine #2 - Oxidation Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - Oxidation Catalyst; CC004(Catalytic Converter): Compressor Eng | Alliance Source Testing, Inc. | 1775 | 1.0 g/Hp-hr & 1.96lb/hr | 1633 | 0.3 g/Hp-hr & 1.05lb/hr | 7E | Nitrogen Oxide | PASS | NA | Y
2014 | 491 | 0210002039 | Kilgore Compressor Station-Utica Gas Services, LLC | Pontiff Rd | Kilgore | 43988 |  | Carroll | P003 | 1,775 hp NG-fired 4SLB Stationary ICE equipped w/catalyst Caterpillar G3606: Serial Number: 4ZS01797 | 2014-12-17 | CC001(Catalytic Converter): Compressor Engine #1 - Oxidation Catalyst; CC002(Catalytic Converter): Compressor Engine #2 - Oxidation Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - Oxidation Catalyst; CC004(Catalytic Converter): Compressor Eng | Alliance Source Testing, Inc. | 1775 | 1.0 g/Hp-hr & 1.96lb/hr | 1598 | 0.4 g/Hp-hr & 1.33lb/hr | 7E | Nitrogen Oxide | PASS | NA | Y
2014 | 495 | 0210002039 | Kilgore Compressor Station-Utica Gas Services, LLC | Pontiff Rd | Kilgore | 43988 |  | Carroll | P004 | 1,775 hp NG-fired 4SLB Stationary ICE equipped w/catalyst Caterpillar G3606: Serial Number: 4ZS01800 | 2014-12-17 | CC001(Catalytic Converter): Compressor Engine #1 - Oxidation Catalyst; CC002(Catalytic Converter): Compressor Engine #2 - Oxidation Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - Oxidation Catalyst; CC004(Catalytic Converter): Compressor Eng | Alliance Source Testing, Inc. | 1775 | 1.0 g/Hp-hr & 1.96lb/hr | 1651 | 0.4 g/Hp-hr & 1.26lb/hr | 7E | Nitrogen Oxide | PASS | NA | Y
2014 | 498 | 0210002039 | Kilgore Compressor Station-Utica Gas Services, LLC | Pontiff Rd | Kilgore | 43988 |  | Carroll | P005 | 1,775 hp NG-fired 4SLB Stationary ICE equipped w/catalyst Caterpillar G3606: Serial Number: 4ZS01804 | 2014-12-17 | CC001(Catalytic Converter): Compressor Engine #1 - Oxidation Catalyst; CC002(Catalytic Converter): Compressor Engine #2 - Oxidation Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - Oxidation Catalyst; CC004(Catalytic Converter): Compressor Eng | Alliance Source Testing, Inc. | 1775 | 1.0 g/Hp-hr & 1.96lb/hr | 1604 | 0.5 g/Hp-hr & 1.57lb/hr | 7E | Nitrogen Oxide | PASS | NA | Y
2014 | 501 | 0210002039 | Kilgore Compressor Station-Utica Gas Services, LLC | Pontiff Rd | Kilgore | 43988 |  | Carroll | P006 | 1,775 hp NG-fired 4SLB Stationary ICE equipped w/catalyst Caterpillar G3606: Serial Number: 4ZS01805 | 2014-12-17 | CC001(Catalytic Converter): Compressor Engine #1 - Oxidation Catalyst; CC002(Catalytic Converter): Compressor Engine #2 - Oxidation Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - Oxidation Catalyst; CC004(Catalytic Converter): Compressor Eng | Alliance Source Testing, Inc. | 1775 | 1.0 g/Hp-hr & 1.96lb/hr | 1604 | 0.4 g/Hp-hr & 1.35lb/hr | 7E | Nitrogen Oxide | PASS | NA | Y
2014 | 503 | 0210002039 | Kilgore Compressor Station-Utica Gas Services, LLC | Pontiff Rd | Kilgore | 43988 |  | Carroll | P007 | 1,775 hp NG-fired 4SLB Stationary ICE equipped w/catalyst Caterpillar G3606: Serial Number: 4ZS01807 | 2014-12-17 | CC001(Catalytic Converter): Compressor Engine #1 - Oxidation Catalyst; CC002(Catalytic Converter): Compressor Engine #2 - Oxidation Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - Oxidation Catalyst; CC004(Catalytic Converter): Compressor Eng | Alliance Source Testing, Inc. | 1775 | 1.0 g/Hp-hr & 1.96lb/hr | 1610 | 0.4 g/Hp-hr & 1.41lb/hr | 7E | Nitrogen Oxide | PASS | NA | Y
2014 | 507 | 0210002039 | Kilgore Compressor Station-Utica Gas Services, LLC | Pontiff Rd | Kilgore | 43988 |  | Carroll | P008 | 1,775 hp NG-fired 4SLB Stationary ICE equipped w/catalyst Caterpillar G3606: Serial Number: 4ZS01808 | 2014-12-17 | CC001(Catalytic Converter): Compressor Engine #1 - Oxidation Catalyst; CC002(Catalytic Converter): Compressor Engine #2 - Oxidation Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - Oxidation Catalyst; CC004(Catalytic Converter): Compressor Eng | Alliance Source Testing, Inc. | 1775 | 1.0 g/Hp-hr & 1.96lb/hr | 1687 | 0.4 g/Hp-hr & 1.30lb/hr | 7E | Nitrogen Oxide | PASS | NA | Y
2014 | 508 | 0210002039 | Kilgore Compressor Station-Utica Gas Services, LLC | Pontiff Rd | Kilgore | 43988 |  | Carroll | P009 | 1,775 hp NG-fired 4SLB Stationary ICE equipped w/catalyst Caterpillar G3606: Serial Number: 4ZS01776 | 2014-12-17 | CC001(Catalytic Converter): Compressor Engine #1 - Oxidation Catalyst; CC002(Catalytic Converter): Compressor Engine #2 - Oxidation Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - Oxidation Catalyst; CC004(Catalytic Converter): Compressor Eng | Alliance Source Testing, Inc. | 1775 | 1.0 g/Hp-hr & 1.96lb/hr | 1616 | 0.3 g/Hp-hr & 1.18lb/hr | 7E | Nitrogen Oxide | PASS | NA | Y
2014 | 512 | 0210002039 | Kilgore Compressor Station-Utica Gas Services, LLC | Pontiff Rd | Kilgore | 43988 |  | Carroll | P010 | 1,775 hp NG-fired 4SLB Stationary ICE equipped w/catalyst Caterpillar G3606: Serial Number: 4ZS01814 | 2014-12-17 | CC001(Catalytic Converter): Compressor Engine #1 - Oxidation Catalyst; CC002(Catalytic Converter): Compressor Engine #2 - Oxidation Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - Oxidation Catalyst; CC004(Catalytic Converter): Compressor Eng | Alliance Source Testing, Inc. | 1775 | 1.0 g/Hp-hr & 1.96lb/hr | 1616 | 0.4 g/Hp-hr & 1.38lb/hr | 7E | Nitrogen Oxide | PASS | NA | Y
2014 | 515 | 0210002047 | Chesapeake Exploration LLC - Hutchison 33-15-5 Pad | Moccasin Road NE | Augusta Twp. | 44615 |  | Carroll | P002 | Natural Gas Engines | 2014-07-01 | Catalyst | Alliance Source Testing, Inc. | 211 Hp | 82ppmvd@15%O2 | 150 Hp or 71% of Max | 3.0ppmvd@15%O2 | 7E | Nitrogen Oxide | PASS | NA | Y | Unit not tested at 90% of Max
2014 | 518 | 0210002056 | Chesapeake Exploration LLC - Bryan Shaw 21-13-5 Pad | Perron Rd SE | Harlem Springs | 43903 |  | Carroll | P002 | One or multiple stationary natural gas-fired spark ignition (SI) internal combustion engines (ICE) with a combined total horsepower (HP) of no more than 1,800 HP for the site. Includes 2007 and later model year engines manufactured after the applicable effective date identified in 40 CFR 60.4230(a)(3) and engines manufactured before the NSPS effective date where compliance with the Part 60 Subpart JJJJ emissions standards for the same size engine can be demonstrated through stack testing. | 2014-10-09 | Catalyst | Alliance Source Testing, Inc. | 185 Bhp | NOx-82 ppmvd @ 15% O2 | 167 Bhp | 3.1 ppmvd | 7E | Nitrogen Oxide | PASS | NA | Y | G6X08444 Serial # 185 Bhp Site Rate engine Tested
2014 | 520 | 0210002057 | Chesapeake Exploration LLC - Javersak 28-12-5 Pad | Saber Road | Kilgore | 43903 |  | Carroll | P002 | One or multiple stationary natural gas-fired spark ignition (SI) internal combustion engines (ICE) with a combined total horsepower (HP) of no more than 1,800 HP for the site.* Includes 2007 and later model year engines manufactured after the applicable effective date identified in 40 CFR 60.4230(a)(3); and engines manufactured before the effective date of the NSPS, where compliance with the Part 60 Subpart JJJJ emissions standards for the same size engine can be met by retrofitting the engine with a control device and demonstrated through stack testing. | 2014-11-13 | Catalyst | Alliance Source Testing | 174 Site Ratew 211 Max | 82 ppmvd @ 15% O2 | 167 or 96% of Site Rate | 0.2 ppmvd @ 15% O2 | 7E | Nitrogen Oxide | PASS | NA | Y
2014 | 525 | 0210012002 | Utica Gas Services, LLC-Carrollton Compressor Facility | 2098 Panda Road SE | Carrollton | 44615 |  | Carroll | P004 | 1,775 HP natural gas-fired Caterpillar G3606 engine #1 equipped with an oxidation catalyst. | 2014-02-10 | Oxid. Cat.(Catalytic Converter): Oxidative Catalyst | Air Hygiene Services | 1775 HP | 160ppmvd@15%O2, 1.96lbs/hr, 2.0g/hp-hr | 1684 HP | 30.37ppmvd@15%O2, 1.23lbs/hr, 0.33g/hp-hr | 7E | Nitrogen Oxide | PASS | NA | Y
2014 | 528 | 0210012002 | Utica Gas Services, LLC-Carrollton Compressor Facility | 2098 Panda Road SE | Carrollton | 44615 |  | Carroll | P005 | 1,775 HP natural gas-fired Caterpillar G3606 engine #2 equipped with an oxidation catalyst | 2014-02-10 | Oxid. Cat.(Catalytic Converter): Oxidative Catalyst | Air Hygiene Services | 1775 HP | 160ppmvd@15%O2, 1.96lbs/hr, 2.0g/hp-hr | 1666 HP | 32.64ppmvd@15%O2, 1.27lbs/hr, 0.35g/hp-hr | 7E | Nitrogen Oxide | PASS | NA | Y
2014 | 529 | 0210012002 | Utica Gas Services, LLC-Carrollton Compressor Facility | 2098 Panda Road SE | Carrollton | 44615 |  | Carroll | P006 | 1,775 HP natural gas-fired Caterpillar G3606 engine #3 equipped with an oxidation catalyst | 2014-02-10 | Oxid. Cat.(Catalytic Converter): Oxidative Catalyst | Air Hygiene Services | 1775 HP | 82ppmvd@15%O2, 1.96lbs/hr, 1.0g/hp-hr | 1617 HP | 28.57ppmvd@15%O2, 1.04lbs/hr, 0.29g/hp-hr | 7E | Nitrogen Oxide | PASS | NA | Y
2014 | 532 | 0210012002 | Utica Gas Services, LLC-Carrollton Compressor Facility | 2098 Panda Road SE | Carrollton | 44615 |  | Carroll | P007 | 1,775 HP natural gas-fired Caterpillar G3606 engine #4 equipped with an oxidation catalyst | 2014-02-10 | Oxid. Cat.(Catalytic Converter): Oxidative Catalyst | Air Hygiene Services | 1775 HP | 82ppmvd@15%O2, 1.96lbs/hr, 1.0g/hp-hr | 1613 HP | 26.08ppmvd@15%O2, 0.96lbs/hr, 0.27g/hp-hr | 7E | Nitrogen Oxide | PASS | NA | Y
2014 | 535 | 0210012002 | Utica Gas Services, LLC-Carrollton Compressor Facility | 2098 Panda Road SE | Carrollton | 44615 |  | Carroll | P008 | 1,775 HP natural gas-fired Caterpillar G3606 engine #5 equipped with an oxidation catalyst | 2014-02-10 | Oxid. Cat.(Catalytic Converter): Oxidative Catalyst | Air Hygiene Services | 1775 HP | 82ppmvd@15%O2, 1.96lbs/hr, 1.0g/hp-hr | 1622 HP | 31.59ppmvd@15%O2, 1.16lbs/hr, 0.32g/hp-hr | 7E | Nitrogen Oxide | PASS | NA | Y
2014 | 540 | 0210012002 | Utica Gas Services, LLC-Carrollton Compressor Facility | 2098 Panda Road SE | Carrollton | 44615 |  | Carroll | P009 | 1,775 HP natural gas-fired Caterpillar G3606 engine #6 equipped with an oxidation catalyst | 2014-02-10 | Oxid. Cat.(Catalytic Converter): Oxidative Catalyst | Air Hygiene Services | 1775 HP | 82ppmvd@15%O2, 1.96lbs/hr, 1.0g/hp-hr | 1623 HP | 26.92ppmvd@15%O2, 0.94lbs/hr, 0.26g/hp-hr | 7E | Nitrogen Oxide | PASS | NA | Y
2014 | 541 | 0210012002 | Utica Gas Services, LLC-Carrollton Compressor Facility | 2098 Panda Road SE | Carrollton | 44615 |  | Carroll | P010 | 1,775 HP natural gas-fired Caterpillar G3606 engine #7 equipped with an oxidation catalyst | 2014-02-10 | Oxid. Cat.(Catalytic Converter): Oxidative Catalyst | Air Hygiene Services | 1775 HP | 82ppmvd@15%O2, 1.96lbs/hr, 1.0g/hp-hr | 1615 HP | 27.51ppmvd@15%O2, 0.99lbs/hr, 0.28g/hp-hr | 7E | Nitrogen Oxide | PASS | NA | Y
2014 | 546 | 0210012002 | Utica Gas Services, LLC-Carrollton Compressor Facility | 2098 Panda Road SE | Carrollton | 44615 |  | Carroll | P011 | 1,775 HP natural gas-fired Caterpillar G3606 engine #8 equipped with an oxidation catalyst | 2014-02-10 | Oxid. Cat.(Catalytic Converter): Oxidative Catalyst | Air Hygiene Services | 1775 HP | 82ppmvd@15%O2, 1.96lbs/hr, 1.0g/hp-hr | 1620 HP | 23.59ppmvd@15%O2, 0.86lbs/hr, 0.24g/hp-hr | 7E | Nitrogen Oxide | PASS | NA | Y
2014 | 547 | 0210012002 | Utica Gas Services, LLC-Carrollton Compressor Facility | 2098 Panda Road SE | Carrollton | 44615 |  | Carroll | P012 | 1,775 HP natural gas-fired Caterpillar G3606 engine #9 equipped with an oxidation catalyst | 2014-02-10 | Oxid. Cat.(Catalytic Converter): Oxidative Catalyst | Air Hygiene Services | 1775 HP | 82ppmvd@15%O2, 1.96lbs/hr, 1.0g/hp-hr | 1643 HP | 30.40ppmvd@15%O2, 1.19lbs/hr, 0.33g/hp-hr | 7E | Nitrogen Oxide | PASS | NA | Y
2014 | 550 | 0210012002 | Utica Gas Services, LLC-Carrollton Compressor Facility | 2098 Panda Road SE | Carrollton | 44615 |  | Carroll | P013 | 1,775 HP natural gas-fired Caterpillar G3606 engine #10equipped with an oxidation catalyst | 2014-02-10 | Oxid. Cat.(Catalytic Converter): Oxidative Catalyst | Air Hygiene Services | 1775 HP | 82ppmvd@15%O2, 1.96lbs/hr, 1.0g/hp-hr | 1593 HP | 34.64ppmvd@15%O2, 1.14lbs/hr, 0.32g/hp-hr | 7E | Nitrogen Oxide | PASS | NA | Y
2014 | 553 | 0210012002 | Utica Gas Services, LLC-Carrollton Compressor Facility | 2098 Panda Road SE | Carrollton | 44615 |  | Carroll | P004 | 1,775 HP natural gas-fired Caterpillar G3606 engine #1 equipped with an oxidation catalyst. | 2014-02-11 | Oxid. Cat.(Catalytic Converter): Oxidative Catalyst | Air Hygiene Services | 1775 HP | 160ppmvd@15%O2, 1.96lbs/hr, 2.0g/hp-hr | 1684 HP | 30.37ppmvd@15%O2, 1.23lbs/hr, 0.33g/hp-hr | 7E | Nitrogen Oxide | PASS | NA | Y
2014 | 556 | 0210012002 | Utica Gas Services, LLC-Carrollton Compressor Facility | 2098 Panda Road SE | Carrollton | 44615 |  | Carroll | P005 | 1,775 HP natural gas-fired Caterpillar G3606 engine #2 equipped with an oxidation catalyst | 2014-02-11 | Oxid. Cat.(Catalytic Converter): Oxidative Catalyst | Air Hygiene Services | 1775 HP | 160ppmvd@15%O2, 1.96lbs/hr, 2.0g/hp-hr | 1666 HP | 32.64ppmvd@15%O2, 1.27lbs/hr, 0.35g/hp-hr | 7E | Nitrogen Oxide | PASS | NA | Y
2014 | 561 | 0210012002 | Utica Gas Services, LLC-Carrollton Compressor Facility | 2098 Panda Road SE | Carrollton | 44615 |  | Carroll | P006 | 1,775 HP natural gas-fired Caterpillar G3606 engine #3 equipped with an oxidation catalyst | 2014-02-11 | Oxid. Cat.(Catalytic Converter): Oxidative Catalyst | Air Hygiene Services | 1775 HP | 82ppmvd@15%O2, 1.96lbs/hr, 1.0g/hp-hr | 1617 HP | 28.57ppmvd@15%O2, 1.04lbs/hr, 0.29g/hp-hr | 7E | Nitrogen Oxide | PASS | NA | Y
2014 | 562 | 0210012002 | Utica Gas Services, LLC-Carrollton Compressor Facility | 2098 Panda Road SE | Carrollton | 44615 |  | Carroll | P007 | 1,775 HP natural gas-fired Caterpillar G3606 engine #4 equipped with an oxidation catalyst | 2014-02-11 | Oxid. Cat.(Catalytic Converter): Oxidative Catalyst | Air Hygiene Services | 1775 HP | 82ppmvd@15%O2, 1.96lbs/hr, 1.0g/hp-hr | 1613 HP | 26.08ppmvd@15%O2, 0.96lbs/hr, 0.27g/hp-hr | 7E | Nitrogen Oxide | PASS | NA | Y
2014 | 566 | 0210012002 | Utica Gas Services, LLC-Carrollton Compressor Facility | 2098 Panda Road SE | Carrollton | 44615 |  | Carroll | P008 | 1,775 HP natural gas-fired Caterpillar G3606 engine #5 equipped with an oxidation catalyst | 2014-02-11 | Oxid. Cat.(Catalytic Converter): Oxidative Catalyst | Air Hygiene Services | 1775 HP | 82ppmvd@15%O2, 1.96lbs/hr, 1.0g/hp-hr | 1622 HP | 31.59ppmvd@15%O2, 1.16lbs/hr, 0.32g/hp-hr | 7E | Nitrogen Oxide | PASS | NA | Y
2014 | 568 | 0210012002 | Utica Gas Services, LLC-Carrollton Compressor Facility | 2098 Panda Road SE | Carrollton | 44615 |  | Carroll | P009 | 1,775 HP natural gas-fired Caterpillar G3606 engine #6 equipped with an oxidation catalyst | 2014-02-11 | Oxid. Cat.(Catalytic Converter): Oxidative Catalyst | Air Hygiene Services | 1775 HP | 82ppmvd@15%O2, 1.96lbs/hr, 1.0g/hp-hr | 1623 HP | 26.92ppmvd@15%O2, 0.94lbs/hr, 0.26g/hp-hr | 7E | Nitrogen Oxide | PASS | NA | Y
2014 | 571 | 0210012002 | Utica Gas Services, LLC-Carrollton Compressor Facility | 2098 Panda Road SE | Carrollton | 44615 |  | Carroll | P010 | 1,775 HP natural gas-fired Caterpillar G3606 engine #7 equipped with an oxidation catalyst | 2014-02-11 | Oxid. Cat.(Catalytic Converter): Oxidative Catalyst | Air Hygiene Services | 1775 HP | 82ppmvd@15%O2, 1.96lbs/hr, 1.0g/hp-hr | 1615 HP | 27.51ppmvd@15%O2, 0.99lbs/hr, 0.28g/hp-hr | 7E | Nitrogen Oxide | PASS | NA | Y
2014 | 574 | 0210012002 | Utica Gas Services, LLC-Carrollton Compressor Facility | 2098 Panda Road SE | Carrollton | 44615 |  | Carroll | P011 | 1,775 HP natural gas-fired Caterpillar G3606 engine #8 equipped with an oxidation catalyst | 2014-02-11 | Oxid. Cat.(Catalytic Converter): Oxidative Catalyst | Air Hygiene Services | 1775 HP | 82ppmvd@15%O2, 1.96lbs/hr, 1.0g/hp-hr | 1620 HP | 23.59ppmvd@15%O2, 0.86lbs/hr, 0.24g/hp-hr | 7E | Nitrogen Oxide | PASS | NA | Y
2014 | 577 | 0210012002 | Utica Gas Services, LLC-Carrollton Compressor Facility | 2098 Panda Road SE | Carrollton | 44615 |  | Carroll | P012 | 1,775 HP natural gas-fired Caterpillar G3606 engine #9 equipped with an oxidation catalyst | 2014-02-11 | Oxid. Cat.(Catalytic Converter): Oxidative Catalyst | Air Hygiene Services | 1775 HP | 82ppmvd@15%O2, 1.96lbs/hr, 1.0g/hp-hr | 1643 HP | 30.40ppmvd@15%O2, 1.19lbs/hr, 0.33g/hp-hr | 7E | Nitrogen Oxide | PASS | NA | Y
2014 | 582 | 0210012002 | Utica Gas Services, LLC-Carrollton Compressor Facility | 2098 Panda Road SE | Carrollton | 44615 |  | Carroll | P013 | 1,775 HP natural gas-fired Caterpillar G3606 engine #10equipped with an oxidation catalyst | 2014-02-11 | Oxid. Cat.(Catalytic Converter): Oxidative Catalyst | Air Hygiene Services | 1775 HP | 82ppmvd@15%O2, 1.96lbs/hr, 1.0g/hp-hr | 1593 HP | 34.64ppmvd@15%O2, 1.14lbs/hr, 0.32g/hp-hr | 7E | Nitrogen Oxide | PASS | NA | Y
2014 | 583 | 0210012002 | Utica Gas Services, LLC-Carrollton Compressor Facility | 2098 Panda Road SE | Carrollton | 44615 |  | Carroll | P004 | 1,775 HP natural gas-fired Caterpillar G3606 engine #1 equipped with an oxidation catalyst. | 2014-02-12 | Oxid. Cat.(Catalytic Converter): Oxidative Catalyst | Air Hygiene Services | 1775 HP | 160ppmvd@15%O2, 1.96lbs/hr, 2.0g/hp-hr | 1684 HP | 30.37ppmvd@15%O2, 1.23lbs/hr, 0.33g/hp-hr | 7E | Nitrogen Oxide | PASS | NA | Y
2014 | 588 | 0210012002 | Utica Gas Services, LLC-Carrollton Compressor Facility | 2098 Panda Road SE | Carrollton | 44615 |  | Carroll | P005 | 1,775 HP natural gas-fired Caterpillar G3606 engine #2 equipped with an oxidation catalyst | 2014-02-12 | Oxid. Cat.(Catalytic Converter): Oxidative Catalyst | Air Hygiene Services | 1775 HP | 160ppmvd@15%O2, 1.96lbs/hr, 2.0g/hp-hr | 1666 HP | 32.64ppmvd@15%O2, 1.27lbs/hr, 0.35g/hp-hr | 7E | Nitrogen Oxide | PASS | NA | Y
2014 | 589 | 0210012002 | Utica Gas Services, LLC-Carrollton Compressor Facility | 2098 Panda Road SE | Carrollton | 44615 |  | Carroll | P006 | 1,775 HP natural gas-fired Caterpillar G3606 engine #3 equipped with an oxidation catalyst | 2014-02-12 | Oxid. Cat.(Catalytic Converter): Oxidative Catalyst | Air Hygiene Services | 1775 HP | 82ppmvd@15%O2, 1.96lbs/hr, 1.0g/hp-hr | 1617 HP | 28.57ppmvd@15%O2, 1.04lbs/hr, 0.29g/hp-hr | 7E | Nitrogen Oxide | PASS | NA | Y
2014 | 593 | 0210012002 | Utica Gas Services, LLC-Carrollton Compressor Facility | 2098 Panda Road SE | Carrollton | 44615 |  | Carroll | P007 | 1,775 HP natural gas-fired Caterpillar G3606 engine #4 equipped with an oxidation catalyst | 2014-02-12 | Oxid. Cat.(Catalytic Converter): Oxidative Catalyst | Air Hygiene Services | 1775 HP | 82ppmvd@15%O2, 1.96lbs/hr, 1.0g/hp-hr | 1613 HP | 26.08ppmvd@15%O2, 0.96lbs/hr, 0.27g/hp-hr | 7E | Nitrogen Oxide | PASS | NA | Y
2014 | 595 | 0210012002 | Utica Gas Services, LLC-Carrollton Compressor Facility | 2098 Panda Road SE | Carrollton | 44615 |  | Carroll | P008 | 1,775 HP natural gas-fired Caterpillar G3606 engine #5 equipped with an oxidation catalyst | 2014-02-12 | Oxid. Cat.(Catalytic Converter): Oxidative Catalyst | Air Hygiene Services | 1775 HP | 82ppmvd@15%O2, 1.96lbs/hr, 1.0g/hp-hr | 1622 HP | 31.59ppmvd@15%O2, 1.16lbs/hr, 0.32g/hp-hr | 7E | Nitrogen Oxide | PASS | NA | Y
2014 | 598 | 0210012002 | Utica Gas Services, LLC-Carrollton Compressor Facility | 2098 Panda Road SE | Carrollton | 44615 |  | Carroll | P009 | 1,775 HP natural gas-fired Caterpillar G3606 engine #6 equipped with an oxidation catalyst | 2014-02-12 | Oxid. Cat.(Catalytic Converter): Oxidative Catalyst | Air Hygiene Services | 1775 HP | 82ppmvd@15%O2, 1.96lbs/hr, 1.0g/hp-hr | 1623 HP | 26.92ppmvd@15%O2, 0.94lbs/hr, 0.26g/hp-hr | 7E | Nitrogen Oxide | PASS | NA | Y
2014 | 603 | 0210012002 | Utica Gas Services, LLC-Carrollton Compressor Facility | 2098 Panda Road SE | Carrollton | 44615 |  | Carroll | P010 | 1,775 HP natural gas-fired Caterpillar G3606 engine #7 equipped with an oxidation catalyst | 2014-02-12 | Oxid. Cat.(Catalytic Converter): Oxidative Catalyst | Air Hygiene Services | 1775 HP | 82ppmvd@15%O2, 1.96lbs/hr, 1.0g/hp-hr | 1615 HP | 27.51ppmvd@15%O2, 0.99lbs/hr, 0.28g/hp-hr | 7E | Nitrogen Oxide | PASS | NA | Y
2014 | 606 | 0210012002 | Utica Gas Services, LLC-Carrollton Compressor Facility | 2098 Panda Road SE | Carrollton | 44615 |  | Carroll | P011 | 1,775 HP natural gas-fired Caterpillar G3606 engine #8 equipped with an oxidation catalyst | 2014-02-12 | Oxid. Cat.(Catalytic Converter): Oxidative Catalyst | Air Hygiene Services | 1775 HP | 82ppmvd@15%O2, 1.96lbs/hr, 1.0g/hp-hr | 1620 HP | 23.59ppmvd@15%O2, 0.86lbs/hr, 0.24g/hp-hr | 7E | Nitrogen Oxide | PASS | NA | Y
2014 | 608 | 0210012002 | Utica Gas Services, LLC-Carrollton Compressor Facility | 2098 Panda Road SE | Carrollton | 44615 |  | Carroll | P012 | 1,775 HP natural gas-fired Caterpillar G3606 engine #9 equipped with an oxidation catalyst | 2014-02-12 | Oxid. Cat.(Catalytic Converter): Oxidative Catalyst | Air Hygiene Services | 1775 HP | 82ppmvd@15%O2, 1.96lbs/hr, 1.0g/hp-hr | 1643 HP | 30.40ppmvd@15%O2, 1.19lbs/hr, 0.33g/hp-hr | 7E | Nitrogen Oxide | PASS | NA | Y
2014 | 610 | 0210012002 | Utica Gas Services, LLC-Carrollton Compressor Facility | 2098 Panda Road SE | Carrollton | 44615 |  | Carroll | P013 | 1,775 HP natural gas-fired Caterpillar G3606 engine #10equipped with an oxidation catalyst | 2014-02-12 | Oxid. Cat.(Catalytic Converter): Oxidative Catalyst | Air Hygiene Services | 1775 HP | 82ppmvd@15%O2, 1.96lbs/hr, 1.0g/hp-hr | 1593 HP | 34.64ppmvd@15%O2, 1.14lbs/hr, 0.32g/hp-hr | 7E | Nitrogen Oxide | PASS | NA | Y
2014 | 618 | 0210012004 | Augusta Compressor Facility- Utica Gas Services, L.L.C. | 8034 Bane Rd NE | East Twp. | 44427 |  | Carroll | P006 | 1,775-hp Caterpillar G3606 Compressor Engine w/ Oxidation Catalyst | 2014-09-16 | Oxid. Cat. 3(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 4(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 5(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 6(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 7(Catalytic Converter): | Great Plains Analytics | 1775 Hp | 1.96 lbs/hr, 1.0 g/hp/hr, 82 ppmvd@15%O2 | 1831 | 1.18 lbs/hr, 0.29 g/hp/hr, 27.9 ppmvd@15%O2 | 7E | Nitrogen Oxide | PASS | NA | Y
2014 | 621 | 0210012004 | Augusta Compressor Facility- Utica Gas Services, L.L.C. | 8034 Bane Rd NE | East Twp. | 44427 |  | Carroll | P007 | 1,775-hp Caterpillar G3606 Compressor Engine w/ Oxidation Catalyst | 2014-09-16 | Oxid. Cat. 3(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 4(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 5(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 6(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 7(Catalytic Converter): | Great Plains Analytics | 1775 Hp | 1.96 lbs/hr, 1.0 g/hp/hr, 82 ppmvd@15%O2 | 1839 | 1.52 lbs/hr, 0.37 g/hp/hr, 34.41 ppmvd@15%O2 | 7E | Nitrogen Oxide | PASS | NA | Y
2014 | 624 | 0210012004 | Augusta Compressor Facility- Utica Gas Services, L.L.C. | 8034 Bane Rd NE | East Twp. | 44427 |  | Carroll | P008 | 1,775-hp Caterpillar G3606 Compressor Engine w/ Oxidation Catalyst | 2014-09-16 | Oxid. Cat. 3(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 4(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 5(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 6(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 7(Catalytic Converter): | Great Plains Analytics | 1775 Hp | 1.96 lbs/hr, 1.0 g/hp/hr, 82 ppmvd@15%O2 | 1809 | 1.5 lbs/hr, 0.38 g/hp/hr, 36.46 ppmvd@15%O2 | 7E | Nitrogen Oxide | PASS | NA | Y
2014 | 625 | 0210012004 | Augusta Compressor Facility- Utica Gas Services, L.L.C. | 8034 Bane Rd NE | East Twp. | 44427 |  | Carroll | P009 | 1,775-hp Caterpillar G3606 Compressor Engine w/ Oxidation Catalyst | 2014-09-16 | Oxid. Cat. 3(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 4(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 5(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 6(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 7(Catalytic Converter): | Great Plains Analytics | 1775 Hp | 1.96 lbs/hr, 1.0 g/hp/hr, 82 ppmvd@15%O2 | 1788 | 1.66 lbs/hr, 0.42 g/hp/hr, 39.26 ppmvd@15%O2 | 7E | Nitrogen Oxide | PASS | NA | Y
2014 | 628 | 0210012004 | Augusta Compressor Facility- Utica Gas Services, L.L.C. | 8034 Bane Rd NE | East Twp. | 44427 |  | Carroll | P010 | 1,775-hp Caterpillar G3606 Compressor Engine w/ Oxidation Catalyst | 2014-09-16 | Oxid. Cat. 3(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 4(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 5(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 6(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 7(Catalytic Converter): | Great Plains Analytics | 1775 Hp | 1.96 lbs/hr, 1.0 g/hp/hr, 82 ppmvd@15%O2 | 1819 | 1.48 lbs/hr, 0.37 g/hp/hr, 34.26 ppmvd@15%O2 | 7E | Nitrogen Oxide | PASS | NA | Y
2014 | 631 | 0210012004 | Augusta Compressor Facility- Utica Gas Services, L.L.C. | 8034 Bane Rd NE | East Twp. | 44427 |  | Carroll | P011 | 1,775-hp Caterpillar G3606 Compressor Engine w/ Oxidation Catalyst | 2014-09-16 | Oxid. Cat. 3(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 4(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 5(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 6(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 7(Catalytic Converter): | Great Plains Analytics | 1775 Hp | 1.96 lbs/hr, 1.0 g/hp/hr, 82 ppmvd@15%O2 | 1821 | 1.38 lbs/hr, 0.34 g/hp/hr, 35.58 ppmvd@15%O2 | 7E | Nitrogen Oxide | PASS | NA | Y
2014 | 636 | 0210012004 | Augusta Compressor Facility- Utica Gas Services, L.L.C. | 8034 Bane Rd NE | East Twp. | 44427 |  | Carroll | P012 | 1,775-hp Caterpillar G3606 Compressor Engine w/ Oxidation Catalyst | 2014-09-16 | Oxid. Cat. 3(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 4(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 5(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 6(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 7(Catalytic Converter): | Great Plains Analytics | 1775 Hp | 1.96 lbs/hr, 1.0 g/hp/hr, 82 ppmvd@15%O2 | 1817 | 1.75 lbs/hr, 0.43 g/hp/hr, 40.52 ppmvd@15%O2 | 7E | Nitrogen Oxide | PASS | NA | Y
2014 | 639 | 0210012004 | Augusta Compressor Facility- Utica Gas Services, L.L.C. | 8034 Bane Rd NE | East Twp. | 44427 |  | Carroll | P013 | 1,775-hp Caterpillar G3606 Compressor Engine w/ Oxidation Catalyst | 2014-09-16 | Oxid. Cat. 3(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 4(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 5(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 6(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 7(Catalytic Converter): | Great Plains Analytics | 1775 Hp | 1.96 lbs/hr, 1.0 g/hp/hr, 82 ppmvd@15%O2 | 1780 | 1.84 lbs/hr, 0..46 g/hp/hr, 42.81 ppmvd@15%O2 | 7E | Nitrogen Oxide | PASS | NA | Y
2014 | 641 | 0210012004 | Augusta Compressor Facility- Utica Gas Services, L.L.C. | 8034 Bane Rd NE | East Twp. | 44427 |  | Carroll | P006 | 1,775-hp Caterpillar G3606 Compressor Engine w/ Oxidation Catalyst | 2014-09-17 | Oxid. Cat. 3(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 4(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 5(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 6(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 7(Catalytic Converter): | Great Plains Analytics | 1775 Hp | 1.96 lbs/hr, 1.0 g/hp/hr, 82 ppmvd@15%O2 | 1831 | 1.18 lbs/hr, 0.29 g/hp/hr, 27.9 ppmvd@15%O2 | 7E | Nitrogen Oxide | PASS | NA | Y
2014 | 644 | 0210012004 | Augusta Compressor Facility- Utica Gas Services, L.L.C. | 8034 Bane Rd NE | East Twp. | 44427 |  | Carroll | P007 | 1,775-hp Caterpillar G3606 Compressor Engine w/ Oxidation Catalyst | 2014-09-17 | Oxid. Cat. 3(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 4(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 5(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 6(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 7(Catalytic Converter): | Great Plains Analytics | 1775 Hp | 1.96 lbs/hr, 1.0 g/hp/hr, 82 ppmvd@15%O2 | 1839 | 1.52 lbs/hr, 0.37 g/hp/hr, 34.41 ppmvd@15%O2 | 7E | Nitrogen Oxide | PASS | NA | Y
2014 | 647 | 0210012004 | Augusta Compressor Facility- Utica Gas Services, L.L.C. | 8034 Bane Rd NE | East Twp. | 44427 |  | Carroll | P008 | 1,775-hp Caterpillar G3606 Compressor Engine w/ Oxidation Catalyst | 2014-09-17 | Oxid. Cat. 3(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 4(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 5(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 6(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 7(Catalytic Converter): | Great Plains Analytics | 1775 Hp | 1.96 lbs/hr, 1.0 g/hp/hr, 82 ppmvd@15%O2 | 1809 | 1.5 lbs/hr, 0.38 g/hp/hr, 36.46 ppmvd@15%O2 | 7E | Nitrogen Oxide | PASS | NA | Y
2014 | 651 | 0210012004 | Augusta Compressor Facility- Utica Gas Services, L.L.C. | 8034 Bane Rd NE | East Twp. | 44427 |  | Carroll | P009 | 1,775-hp Caterpillar G3606 Compressor Engine w/ Oxidation Catalyst | 2014-09-17 | Oxid. Cat. 3(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 4(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 5(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 6(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 7(Catalytic Converter): | Great Plains Analytics | 1775 Hp | 1.96 lbs/hr, 1.0 g/hp/hr, 82 ppmvd@15%O2 | 1788 | 1.66 lbs/hr, 0.42 g/hp/hr, 39.26 ppmvd@15%O2 | 7E | Nitrogen Oxide | PASS | NA | Y
2014 | 654 | 0210012004 | Augusta Compressor Facility- Utica Gas Services, L.L.C. | 8034 Bane Rd NE | East Twp. | 44427 |  | Carroll | P010 | 1,775-hp Caterpillar G3606 Compressor Engine w/ Oxidation Catalyst | 2014-09-17 | Oxid. Cat. 3(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 4(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 5(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 6(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 7(Catalytic Converter): | Great Plains Analytics | 1775 Hp | 1.96 lbs/hr, 1.0 g/hp/hr, 82 ppmvd@15%O2 | 1819 | 1.48 lbs/hr, 0.37 g/hp/hr, 34.26 ppmvd@15%O2 | 7E | Nitrogen Oxide | PASS | NA | Y
2014 | 656 | 0210012004 | Augusta Compressor Facility- Utica Gas Services, L.L.C. | 8034 Bane Rd NE | East Twp. | 44427 |  | Carroll | P011 | 1,775-hp Caterpillar G3606 Compressor Engine w/ Oxidation Catalyst | 2014-09-17 | Oxid. Cat. 3(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 4(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 5(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 6(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 7(Catalytic Converter): | Great Plains Analytics | 1775 Hp | 1.96 lbs/hr, 1.0 g/hp/hr, 82 ppmvd@15%O2 | 1821 | 1.38 lbs/hr, 0.34 g/hp/hr, 35.58 ppmvd@15%O2 | 7E | Nitrogen Oxide | PASS | NA | Y
2014 | 658 | 0210012004 | Augusta Compressor Facility- Utica Gas Services, L.L.C. | 8034 Bane Rd NE | East Twp. | 44427 |  | Carroll | P012 | 1,775-hp Caterpillar G3606 Compressor Engine w/ Oxidation Catalyst | 2014-09-17 | Oxid. Cat. 3(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 4(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 5(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 6(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 7(Catalytic Converter): | Great Plains Analytics | 1775 Hp | 1.96 lbs/hr, 1.0 g/hp/hr, 82 ppmvd@15%O2 | 1817 | 1.75 lbs/hr, 0.43 g/hp/hr, 40.52 ppmvd@15%O2 | 7E | Nitrogen Oxide | PASS | NA | Y
2014 | 663 | 0210012004 | Augusta Compressor Facility- Utica Gas Services, L.L.C. | 8034 Bane Rd NE | East Twp. | 44427 |  | Carroll | P009 | 1,775-hp Caterpillar G3606 Compressor Engine w/ Oxidation Catalyst | 2014-09-18 | Oxid. Cat. 3(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 4(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 5(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 6(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 7(Catalytic Converter): | Great Plains Analytics | 1775 Hp | 1.96 lbs/hr, 1.0 g/hp/hr, 82 ppmvd@15%O2 | 1788 | 1.66 lbs/hr, 0.42 g/hp/hr, 39.26 ppmvd@15%O2 | 7E | Nitrogen Oxide | PASS | NA | Y
2014 | 664 | 0210012004 | Augusta Compressor Facility- Utica Gas Services, L.L.C. | 8034 Bane Rd NE | East Twp. | 44427 |  | Carroll | P010 | 1,775-hp Caterpillar G3606 Compressor Engine w/ Oxidation Catalyst | 2014-09-18 | Oxid. Cat. 3(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 4(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 5(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 6(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 7(Catalytic Converter): | Great Plains Analytics | 1775 Hp | 1.96 lbs/hr, 1.0 g/hp/hr, 82 ppmvd@15%O2 | 1819 | 1.48 lbs/hr, 0.37 g/hp/hr, 34.26 ppmvd@15%O2 | 7E | Nitrogen Oxide | PASS | NA | Y
2014 | 669 | 0210012004 | Augusta Compressor Facility- Utica Gas Services, L.L.C. | 8034 Bane Rd NE | East Twp. | 44427 |  | Carroll | P011 | 1,775-hp Caterpillar G3606 Compressor Engine w/ Oxidation Catalyst | 2014-09-18 | Oxid. Cat. 3(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 4(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 5(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 6(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 7(Catalytic Converter): | Great Plains Analytics | 1775 Hp | 1.96 lbs/hr, 1.0 g/hp/hr, 82 ppmvd@15%O2 | 1821 | 1.38 lbs/hr, 0.34 g/hp/hr, 35.58 ppmvd@15%O2 | 7E | Nitrogen Oxide | PASS | NA | Y
2014 | 672 | 0210012004 | Augusta Compressor Facility- Utica Gas Services, L.L.C. | 8034 Bane Rd NE | East Twp. | 44427 |  | Carroll | P012 | 1,775-hp Caterpillar G3606 Compressor Engine w/ Oxidation Catalyst | 2014-09-18 | Oxid. Cat. 3(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 4(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 5(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 6(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 7(Catalytic Converter): | Great Plains Analytics | 1775 Hp | 1.96 lbs/hr, 1.0 g/hp/hr, 82 ppmvd@15%O2 | 1817 | 1.75 lbs/hr, 0.43 g/hp/hr, 40.52 ppmvd@15%O2 | 7E | Nitrogen Oxide | PASS | NA | Y
2014 | 675 | 0210012004 | Augusta Compressor Facility- Utica Gas Services, L.L.C. | 8034 Bane Rd NE | East Twp. | 44427 |  | Carroll | P013 | 1,775-hp Caterpillar G3606 Compressor Engine w/ Oxidation Catalyst | 2014-09-18 | Oxid. Cat. 3(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 4(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 5(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 6(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 7(Catalytic Converter): | Great Plains Analytics | 1775 Hp | 1.96 lbs/hr, 1.0 g/hp/hr, 82 ppmvd@15%O2 | 1780 | 1.84 lbs/hr, 0..46 g/hp/hr, 42.81 ppmvd@15%O2 | 7E | Nitrogen Oxide | PASS | NA | Y
2014 | 687 | 0210012022 | Chesapeake Exploration LLC - Krichbaum 2-14-5 Pad | County Highway 21 | Carrollton | 44615 |  | Carroll | P002 | Natural Gas Engines | 2014-03-04 | Catalyst | Alliance Source Testing, Inc. | 211 HP | 82 ppmvd @ 15% O2 | 168 hp | 64 ppmvd @ 15% O2 | 7E | Nitrogen Oxide | PASS | NA | Y
2014 | 691 | 0210012030 | Blue Racer Midstream LLC - Carroll Co Field Station #1 | Cobbler Rd NE | Carrollton | 44615 |  | Carroll | P001 | 1,340 HP Caterpillar G3516LE 4SLB Compressor Engine #1 with Oxidation Catalyst. Engine model year: 2013. | 2014-09-24 | CC-1(Catalytic Converter): Oxidation Catalyst 1; CC-2(Catalytic Converter): Oxidation Catalyst 2 | Air/ Compliance Consultants | 1380 Hp | 82 ppmvd@15%O2 & 1.0 g/bhp-hr | 1159 Hp or 83.9% | 26.72 ppmvd@15%O2 & 0.39 g/bhp-hr | 7E | Nitrogen Oxide | PASS | NA | Y | Testing at a lower rate than 90% of Maximum was allowed because they were barely able to achieve each of these loads independently of the other engine, without taking the other engine down. 90% of the time the engines operate at 50% or lower and they have records to show that. Utilized M320 with SF6 Tracer as a surrogate for M7E as allowed by JJJJ
2014 | 695 | 0210012030 | Blue Racer Midstream LLC - Carroll Co Field Station #1 | Cobbler Rd NE | Carrollton | 44615 |  | Carroll | P002 | 1,340 HP Caterpillar G3516LE 4SLB Compressor Engine #2 with Oxidation Catalyst. Engine model year: 2013. | 2014-09-24 | CC-1(Catalytic Converter): Oxidation Catalyst 1; CC-2(Catalytic Converter): Oxidation Catalyst 2 | Air/ Compliance Consultants | 1380 Hp | 82 ppmvd@15%O2 & 1.0 g/bhp-hr | 1006 Hp or 73.8% | 26.48 ppmvd@15%O2 & 0.39 g/bhp-hr | 7E | Nitrogen Oxide | PASS | NA | Y | Testing at a lower rate than 90% of Maximum was allowed because they were barely able to achieve each of these loads independently of the other engine, without taking the other engine down. 90% of the time the engines operate at 50% or lower and they have records to show that. Utilized M320 with SF6 Tracer as a surrogate for M7E as allowed by JJJJ
2014 | 700 | 0210012038 | Chesapeake Exploration LLC - GF Farms 25-14-5 Pad | Steubenville Rd SE | Carrollton | 44615 |  | Carroll | P002 | Natural Gas Engines | 2014-11-12 | Catalyst | Alliance Source Testing | 174 Site Rate 211 MAX | 82 ppmvd @ 15% O2 | 167 97% of Site Rate | 0.7 ppmvd @ 15% O2 | 7E | Nitrogen Dioxide | PASS | NA | Y
2014 | 701 | 0210012045 | Chesapeake Exploration LLC - Stanton 29-13-5 Pad | Canyon Road SE | Carrollton | 44615 |  | Carroll | P002 | One or multiple stationary natural gas-fired spark ignition (SI) internal combustion engines (ICE) with a combined total horsepower (HP) of no more than 1,800 HP for the site.* Includes 2007 and later model year engines manufactured after the applicable effective date identified in 40 CFR 60.4230(a)(3); and engines manufactured before the effective date of the NSPS, where compliance with the Part 60 Subpart JJJJ emissions standards for the same size engine can be met by retrofitting the engine with a control device and demonstrated through stack testing. | 2014-12-22 | Catalyst | Alliance Source Testing | 211 HP MAX 195 Site rate HP | NOx-82 ppmvd @ 15% O2 | 175 Hp | 3.2 ppmvd @ 15% O2 | 7E | Nitrogen Dioxide | PASS | NA | Y
2014 | 705 | 0210032001 | Chesapeake Exploration LLC - Edie 17-13-6 Pad | Amsterdam Road SW | Leesville | 44639 |  | Carroll | P002 | Natural Gas Engines | 2014-04-07 | Catalyst | Alliance Source Testing | 211 HP | 82 ppmvd@15%O2 | 155 HP or 73.5% of Max | 4.5 ppmvd@15% O2 | 7E | Nitrogen Oxide | PASS | NA | Y | Engine will require a retest if engine exceeds 10% of the tested rate.
2014 | 723 | 0215112002 | Chesapeake Exploration LLC - Pitts 22-14-4 Pad | Nature Rd SE (Carroll Rd) | Summitville | 43962 |  | Columbiana | P002 | Natural Gas Engines | 2014-12-22 | Catalyst | Alliance Source Testing | 211 HP MAX 195 Site rate HP | NOx-82 ppmvd @ 15% O2 | 193 Hp | 8.0 ppmvd @ 15% O2 | 7E | Nitrogen Dioxide | PASS | NA | Y
2014 | 1010 | 0250002027 | Poland-CLL Production Facility | East of Cowden Rd and Moore Rd | Poland Twp. | 44436 |  | Mahoning | P002 | 1,340-hp Caterpillar G3516LE natural gas-fired compressor engine with oxidation catalyst, manufactured on 5/31/2007 | 2014-07-01 | Catalytic Co(Catalytic Converter): Catalytic Converter | Alliance Source Testing, Inc. | 1340 Hp | 82 ppmvd@15%O2 and 1.0g/bhp-hr | 590 hp or 44% load | 59 ppmvd@15%O2 and 0.93g/bhp-hr | 7E | Nitrogen Oxide | PASS | NA | Y | NSPS JJJJ Required test The facility was aware of the fact that they were well below the 90% threshold and are aware that they will have to test again if they run at a rate of 10% greater than the tested.
2014 | 1117 | 0278002033 | Halcon Operating Co Inc - Avalon Farms Production Facility | 3393 Warren Sharon Rd | Vienna Twp.. | 44473 |  | Trumbull | P002 | Natural Gas Engines | 2014-04-08 | CTRL-3(Other): NSCR | Air Compliance/Consultants | 400 HP | 82 ppmvd@15%O2 and 2.0 g/bhp-hr | 260 hp | 12.97 ppmvd and 0.21 g/bhp-hr | 7E | Nitrogen Oxide | PASS | Y | Y
2014 | 1158 | 0285000366 | East Ohio Gas - Chippewa Station | 17045 Galehouse Road | Doylestown | 44230 |  | Wayne | B010 | 2,370 hp 4SLB SI ICE; CAT G3608 | 2014-06-02 | Engine 5 Converter(Catalytic Converter): Engine #5; Cat B010(Catalytic Converter): Catalytic Converter for B010, engine #6; Catalytic(Catalytic Converter): Engine 7 Catalytic converter | Air/Compliance Consultants, Inc. | 2370 Hp | 82 ppm@15%O2 or 1.0 g/bhp-hr | 2315 Hp | 20.13 ppm@15%O2 and 0.25 g/bhp-hr | 7E | Nitrogen Oxide | PASS | NA | Y | B009-2.8 Catalyst Pressure and 853 degF Catalyst temp, B010-2.16 Catalyst Pressure and 908 degF Catalyst temp, B014-1.0 Catalyst Pressure and 851 degF Catalyst Temperature
2014 | 1160 | 0285000366 | East Ohio Gas - Chippewa Station | 17045 Galehouse Road | Doylestown | 44230 |  | Wayne | B014 | 2,370 hp 4SLB SI ICE: CAT 3608 w/catalyst | 2014-06-02 | Engine 5 Converter(Catalytic Converter): Engine #5; Cat B010(Catalytic Converter): Catalytic Converter for B010, engine #6; Catalytic(Catalytic Converter): Engine 7 Catalytic converter | Air/Compliance Consultants, Inc. | 2370 Hp | 160ppm@15%O2 or 2.0g/bhp-hr | 2362 Hp | 82.92 ppm@15%O2 and 1.03g/bhp-hr | 7E | Nitrogen Oxide | PASS | NA | Y | B009-2.8 Catalyst Pressure and 853 degF Catalyst temp, B010-2.16 Catalyst Pressure and 908 degF Catalyst temp, B014-1.0 Catalyst Pressure and 851 degF Catalyst Temperature
2014 | 1165 | 0285000366 | East Ohio Gas - Chippewa Station | 17045 Galehouse Road | Doylestown | 44230 |  | Wayne | B010 | 2,370 hp 4SLB SI ICE; CAT G3608 | 2014-06-03 | Engine 5 Converter(Catalytic Converter): Engine #5; Cat B010(Catalytic Converter): Catalytic Converter for B010, engine #6; Catalytic(Catalytic Converter): Engine 7 Catalytic converter | Air/Compliance Consultants, Inc. | 2370 Hp | 82 ppm@15%O2 or 1.0 g/bhp-hr | 2315 Hp | 20.13 ppm@15%O2 and 0.25 g/bhp-hr | 7E | Nitrogen Oxide | PASS | NA | Y | B009-2.8 Catalyst Pressure and 853 degF Catalyst temp, B010-2.16 Catalyst Pressure and 908 degF Catalyst temp, B014-1.0 Catalyst Pressure and 851 degF Catalyst Temperature
2014 | 1167 | 0285000366 | East Ohio Gas - Chippewa Station | 17045 Galehouse Road | Doylestown | 44230 |  | Wayne | B014 | 2,370 hp 4SLB SI ICE: CAT 3608 w/catalyst | 2014-06-03 | Engine 5 Converter(Catalytic Converter): Engine #5; Cat B010(Catalytic Converter): Catalytic Converter for B010, engine #6; Catalytic(Catalytic Converter): Engine 7 Catalytic converter | Air/Compliance Consultants, Inc. | 2370 Hp | 160ppm@15%O2 or 2.0g/bhp-hr | 2362 Hp | 82.92 ppm@15%O2 and 1.03g/bhp-hr | 7E | Nitrogen Oxide | PASS | NA | Y | B009-2.8 Catalyst Pressure and 853 degF Catalyst temp, B010-2.16 Catalyst Pressure and 908 degF Catalyst temp, B014-1.0 Catalyst Pressure and 851 degF Catalyst Temperature
2014 | 1170 | 0285000388 | East Ohio Gas Company - Paint | STATE RTE 250 | Wooster | 44624 |  | Wayne | B002 | Natural gas fired Internal Combustion Engine with max input capacity of 11.9 MMBtu/hr - Caterpillar G3516TALE with 1340 HP, 4-stroke, selective catalytic reduction (SCR) | 2014-07-26 | Three way Catalyst; CatOx(Catalytic Converter): Catalytic oxidizer for Engine 2 | Air/Compliance Consultants | 1340 Hp | 160 ppm @ 15% O2 and 2.0 g/hp-hr | 1207 Hp or 90.1% | 91.7ppm @ 15% O2 and 1.3 g/hp-hr | 7E | Nitrogen Oxide | PASS | NA | Y
2014 | 1239 | 0335012004 | Napoleon Biogas, LLC | 12329 County Road P-3 | Napoleon | 43545 |  | Henry | P002 | Jenbacher Engine (1996 hp) | 2014-12-16 | None | KBD Technic | 1966 hp | 1.1 g/bhp-hr | 1912 hp | 0.54 g/bhp-hr | 7E | Nitrogen Dioxide | PASS | Y | Y
2014 | 1243 | 0335012004 | Napoleon Biogas, LLC | 12329 County Road P-3 | Napoleon | 43545 |  | Henry | P001 | Jenbacher Engine (1996 hp) | 2014-12-17 | None | KBD Technic | 1966 hp | 1.1 g/bhp-hr | 1912 hp | 0.52 g/bhp-hr | 7E | Nitrogen Dioxide | PASS | Y | Y
2014 | 1427 | 0630005012 | Gulfport Energy- Groh Well Pad | 19667 Cadiz Rd | Quaker City | 42773 |  | Guernsey | P002 | One 50-hp Zenith ZPP416 and one 203-hp Caterpillar G3306B NA natural gas-fired engines for compressors. One or multiple stationary natural gas-fired spark ignition (SI) internal combustion engines (ICE) wiht a combined total horsepower (HP) or no more than 1,800 HP for the site. | 2014-08-07 | none | BCMJ Controls Inc. | 145 Hp | 2.0 g/Hp-hr | 128 Hp | 0.59 g/Hp-hr | 7E | Nitrogen Dioxide | PASS | NA | Y
2014 | 1428 | 0630005024 | Gulfport Energy Corporation - Karen 23-9-7 Pad | Oxford Rd | Quaker City | 43773 |  | Guernsey | P002 | One or multiple stationary natural gas-fired spark ignition (SI) internal combustion engines (ICE) with a combined total horsepower (HP) of no more than 1,800 HP for the site. Includes 2007 and later model year engines manufactured after the applicable effective date identified in 40 CFR 60.4230(a)(3) and engines manufactured before the NSPS effective date where compliance with the Part 60 Subpart JJJJ emissions standards for the same size engine can be demonstrated through stack testing. | 2014-08-08 | catalyst | BCMJ Controls, Inc | 118 Hp | 2.0 g/Hp-hr | 52 Hp | 0.03 g/Hp-hr | 7E | Nitrogen Dioxide | PASS | NA | Y
2014 | 1433 | 0630005024 | Gulfport Energy Corporation - Karen 23-9-7 Pad | Oxford Rd | Quaker City | 43773 |  | Guernsey | P002 | One or multiple stationary natural gas-fired spark ignition (SI) internal combustion engines (ICE) with a combined total horsepower (HP) of no more than 1,800 HP for the site. Includes 2007 and later model year engines manufactured after the applicable effective date identified in 40 CFR 60.4230(a)(3) and engines manufactured before the NSPS effective date where compliance with the Part 60 Subpart JJJJ emissions standards for the same size engine can be demonstrated through stack testing. | 2014-12-04 | none | Great Plains Analytical Services | 118 Hp | 2.0 g/Hp-hr | 63 Hp | 0.317 g/Hp-hr | 7E | Nitrogen Dioxide | PASS | NA | Y | method 7E not used. methods 1-3a and ASTM 6348-03 FTIR
2014 | 1436 | 0656005010 | Dominion East Ohio - Switzerland Compressor Station | German Ridge Road | Switzerland Twp. | 43942 |  | Monroe | P001 | 3550 Hp Natural gas-fired (4SLB) Caterpillar model 3612 LE DM5309-06 compressor engines equipped with catalytic reduction (three-way). | 2014-11-11 | catalytic reduction | Air Compliance Consultants | 3550 Hp | 0.5 g/Hp-hr | 3408 Hp | 0.39 g/Hp-hr | 7E | Nitrogen Dioxide | PASS | NA | Y
2014 | 1612 | 0605000020 | Tennessee Gas Pipeline Station 204 | 2335 US Route 50 West | Albany | 45710 | 0000 | Athens | B012 | Recip. Engine 11A - Clark Gas Engine TLA-10 3,400 hp | 2014-08-26 | none | Kinder Morgan Corp. | 3,400 Hp | 4.33 g/Hp-hr | 3,268 Hp | 4.33 g/Hp-hr | 7 | NOx - Nitrogen Oxides | PASS | NA | Y | method ASTM 6522-00
2014 | 1613 | 0605000020 | Tennessee Gas Pipeline Station 204 | 2335 US Route 50 West | Albany | 45710 | 0000 | Athens | B013 | Recip. Engine 12A - Clark Gas Engine TLA-10 3,400 hp | 2014-09-24 | none | Kindermorgan Corp. | 3400 Hp | 8 gr/Hp-hr | 3346 Hp | 4.62 g/Hp-hr | 7E | Nitrogen Dioxide | PASS | NA | N | Method 7E not used. ASTM 6522-00 used.
2014 | 1628 | 0607005015 | Morristown Compressor Station | Between Hwys 100 and 203 | Union Twp. | 43713 |  | Belmont | P001 | compressor engine | 2014-11-20 | CC001(Catalytic Converter): Compressor Engine #1 Catalytic Converter; CC002(Catalytic Converter): Compressor Engine #2 Catalytic Converter; CC003(Catalytic Converter): Compressor Engine #3 Catalytic Converter; CC004(Catalytic Converter): Compressor Engine | Air Hygiene, Inc. | 2,370 hp | 1.0 g/hp-hr | 2,236 hp | 0.45 g/hp-hr | 7E | Nitrogen Dioxide | PASS | NA | Y
2014 | 1630 | 0607005015 | Morristown Compressor Station | Between Hwys 100 and 203 | Union Twp. | 43713 |  | Belmont | P002 | compressor engine | 2014-11-20 | CC001(Catalytic Converter): Compressor Engine #1 Catalytic Converter; CC002(Catalytic Converter): Compressor Engine #2 Catalytic Converter; CC003(Catalytic Converter): Compressor Engine #3 Catalytic Converter; CC004(Catalytic Converter): Compressor Engine | Air Hygiene, Inc. | 2,370 hp | 1.0 g/hp-hr | 2,299 hp | 0.42 g/hp-hr | 7E | Nitrogen Dioxide | PASS | NA | Y
2014 | 1633 | 0607005015 | Morristown Compressor Station | Between Hwys 100 and 203 | Union Twp. | 43713 |  | Belmont | P003 | compressor engine | 2014-11-20 | CC001(Catalytic Converter): Compressor Engine #1 Catalytic Converter; CC002(Catalytic Converter): Compressor Engine #2 Catalytic Converter; CC003(Catalytic Converter): Compressor Engine #3 Catalytic Converter; CC004(Catalytic Converter): Compressor Engine | Air Hygiene, Inc. | 2,370 hp | 1.0 g/hp-hr | 2,236 hp | 0.48 g/hp-hr | 7E | Nitrogen Dioxide | PASS | NA | Y
2014 | 1637 | 0607005015 | Morristown Compressor Station | Between Hwys 100 and 203 | Union Twp. | 43713 |  | Belmont | P004 | compressor engine | 2014-11-20 | CC001(Catalytic Converter): Compressor Engine #1 Catalytic Converter; CC002(Catalytic Converter): Compressor Engine #2 Catalytic Converter; CC003(Catalytic Converter): Compressor Engine #3 Catalytic Converter; CC004(Catalytic Converter): Compressor Engine | Air Hygiene, Inc. | 2,370 hp | 1.0 g/hp-hr | 2,283 hp | 0.35 g/hp-hr | 7E | Nitrogen Dioxide | PASS | NA | Y
2014 | 1640 | 0607005015 | Morristown Compressor Station | Between Hwys 100 and 203 | Union Twp. | 43713 |  | Belmont | P005 | compressor engine | 2014-11-20 | CC001(Catalytic Converter): Compressor Engine #1 Catalytic Converter; CC002(Catalytic Converter): Compressor Engine #2 Catalytic Converter; CC003(Catalytic Converter): Compressor Engine #3 Catalytic Converter; CC004(Catalytic Converter): Compressor Engine | Air Hygiene, Inc. | 2,370 hp | 1.0 g/hp-hr | 2,212 hp | 0.33 g/hp-hr | 7E | Nitrogen Dioxide | PASS | NA | Y
2014 | 1643 | 0607005015 | Morristown Compressor Station | Between Hwys 100 and 203 | Union Twp. | 43713 |  | Belmont | P006 | compressor engine | 2014-11-20 | CC001(Catalytic Converter): Compressor Engine #1 Catalytic Converter; CC002(Catalytic Converter): Compressor Engine #2 Catalytic Converter; CC003(Catalytic Converter): Compressor Engine #3 Catalytic Converter; CC004(Catalytic Converter): Compressor Engine | Air Hygiene, Inc. | 2,370 hp | 1.0 g/hp-hr | 2,140 hp | 0.40 g/hp-hr | 7E | Nitrogen Dioxide | PASS | NA | Y
2014 | 1645 | 0607005015 | Morristown Compressor Station | Between Hwys 100 and 203 | Union Twp. | 43713 |  | Belmont | P001 | compressor engine | 2014-11-21 | CC001(Catalytic Converter): Compressor Engine #1 Catalytic Converter; CC002(Catalytic Converter): Compressor Engine #2 Catalytic Converter; CC003(Catalytic Converter): Compressor Engine #3 Catalytic Converter; CC004(Catalytic Converter): Compressor Engine | Air Hygiene, Inc. | 2,370 hp | 1.0 g/hp-hr | 2,236 hp | 0.45 g/hp-hr | 7E | Nitrogen Dioxide | PASS | NA | Y
2014 | 1649 | 0607005015 | Morristown Compressor Station | Between Hwys 100 and 203 | Union Twp. | 43713 |  | Belmont | P002 | compressor engine | 2014-11-21 | CC001(Catalytic Converter): Compressor Engine #1 Catalytic Converter; CC002(Catalytic Converter): Compressor Engine #2 Catalytic Converter; CC003(Catalytic Converter): Compressor Engine #3 Catalytic Converter; CC004(Catalytic Converter): Compressor Engine | Air Hygiene, Inc. | 2,370 hp | 1.0 g/hp-hr | 2,299 hp | 0.42 g/hp-hr | 7E | Nitrogen Dioxide | PASS | NA | Y
2014 | 1652 | 0607005015 | Morristown Compressor Station | Between Hwys 100 and 203 | Union Twp. | 43713 |  | Belmont | P003 | compressor engine | 2014-11-21 | CC001(Catalytic Converter): Compressor Engine #1 Catalytic Converter; CC002(Catalytic Converter): Compressor Engine #2 Catalytic Converter; CC003(Catalytic Converter): Compressor Engine #3 Catalytic Converter; CC004(Catalytic Converter): Compressor Engine | Air Hygiene, Inc. | 2,370 hp | 1.0 g/hp-hr | 2,236 hp | 0.48 g/hp-hr | 7E | Nitrogen Dioxide | PASS | NA | Y
2014 | 1655 | 0607005015 | Morristown Compressor Station | Between Hwys 100 and 203 | Union Twp. | 43713 |  | Belmont | P004 | compressor engine | 2014-11-21 | CC001(Catalytic Converter): Compressor Engine #1 Catalytic Converter; CC002(Catalytic Converter): Compressor Engine #2 Catalytic Converter; CC003(Catalytic Converter): Compressor Engine #3 Catalytic Converter; CC004(Catalytic Converter): Compressor Engine | Air Hygiene, Inc. | 2,370 hp | 1.0 g/hp-hr | 2,283 hp | 0.35 g/hp-hr | 7E | Nitrogen Dioxide | PASS | NA | Y
2014 | 1659 | 0607005015 | Morristown Compressor Station | Between Hwys 100 and 203 | Union Twp. | 43713 |  | Belmont | P005 | compressor engine | 2014-11-21 | CC001(Catalytic Converter): Compressor Engine #1 Catalytic Converter; CC002(Catalytic Converter): Compressor Engine #2 Catalytic Converter; CC003(Catalytic Converter): Compressor Engine #3 Catalytic Converter; CC004(Catalytic Converter): Compressor Engine | Air Hygiene, Inc. | 2,370 hp | 1.0 g/hp-hr | 2,212 hp | 0.33 g/hp-hr | 7E | Nitrogen Dioxide | PASS | NA | Y
2014 | 1660 | 0607005015 | Morristown Compressor Station | Between Hwys 100 and 203 | Union Twp. | 43713 |  | Belmont | P006 | compressor engine | 2014-11-21 | CC001(Catalytic Converter): Compressor Engine #1 Catalytic Converter; CC002(Catalytic Converter): Compressor Engine #2 Catalytic Converter; CC003(Catalytic Converter): Compressor Engine #3 Catalytic Converter; CC004(Catalytic Converter): Compressor Engine | Air Hygiene, Inc. | 2,370 hp | 1.0 g/hp-hr | 2,140 hp | 0.40 g/hp-hr | 7E | Nitrogen Dioxide | PASS | NA | Y
2014 | 1664 | 0607015001 | Tri-County Compressor Station (MarkWest / Ohio Oil Gath | North of intersection of Hwy 379 and Town | Barnesville | 43713 |  | Belmont | P003 | Compressor Engine #3 - 1980 HP (15.43 MMBtu/hr) Waukesha P9390 - natural gas-fired four-stroke rich burn internal combustion engine equipped with a three-way oxidation catalyst controlling CH2O, CO, NOx, & VOCs by 80, 97, 98.5 & 66 percent respectively | 2014-11-11 | CC002(Catalytic Converter): Compressor Engine #2 - 3-way Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - 3-way Catalyst; CC004(Catalytic Converter): Compressor Engine #4 - 3-way Catalyst; CC005(Catalytic Converter): Compressor Engine #5 - 3-w | Air Hygiene, Inc | 1980 hp | 1.0 g/hp-hr | 1,526 hp | 0.08 g/hp-hr | 7E | Nitrogen Dioxide | PASS | NA | Y
2014 | 1668 | 0607015001 | Tri-County Compressor Station (MarkWest / Ohio Oil Gath | North of intersection of Hwy 379 and Town | Barnesville | 43713 |  | Belmont | P004 | Compressor Engine #4 - 1980 HP (15.43 MMBtu/hr) Waukesha P9390 - natural gas-fired four-stroke rich burn internal combustion engine equipped with a three-way oxidation catalyst controlling CH2O, CO, NOx, & VOCs by 80, 97, 98.5 & 66 percent respectively | 2014-11-11 | CC002(Catalytic Converter): Compressor Engine #2 - 3-way Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - 3-way Catalyst; CC004(Catalytic Converter): Compressor Engine #4 - 3-way Catalyst; CC005(Catalytic Converter): Compressor Engine #5 - 3-w | Air Hygiene, Inc | 1980 hp | 1.0 g/hp-hr | 1,525 hp | 0.15 g/hp-hr | 7E | Nitrogen Dioxide | PASS | NA | Y
2014 | 1670 | 0607015001 | Tri-County Compressor Station (MarkWest / Ohio Oil Gath | North of intersection of Hwy 379 and Town | Barnesville | 43713 |  | Belmont | P005 | Compressor Engine #5 - 1980 HP (15.43 MMBtu/hr) Waukesha P9390 - natural gas-fired four-stroke rich burn internal combustion engine equipped with a three-way oxidation catalyst controlling CH2O, CO, NOx, & VOCs by 80, 97, 98.5 & 66 percent respectively | 2014-11-11 | CC002(Catalytic Converter): Compressor Engine #2 - 3-way Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - 3-way Catalyst; CC004(Catalytic Converter): Compressor Engine #4 - 3-way Catalyst; CC005(Catalytic Converter): Compressor Engine #5 - 3-w | Air Hygiene, Inc | 1980 hp | 1.0 g/hp-hr | 1,482 hp | 0.17 g/hp-hr | 7E | Nitrogen Dioxide | PASS | NA | Y
2014 | 1673 | 0607015001 | Tri-County Compressor Station (MarkWest / Ohio Oil Gath | North of intersection of Hwy 379 and Town | Barnesville | 43713 |  | Belmont | P006 | Compressor Engine #6 - 1980 HP (15.43 MMBtu/hr) Waukesha P9390 - natural gas-fired four-stroke rich burn internal combustion engine equipped with a three-way oxidation catalyst controlling CH2O, CO, NOx, & VOCs by 80, 97, 98.5 & 66 percent respectively | 2014-11-11 | CC002(Catalytic Converter): Compressor Engine #2 - 3-way Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - 3-way Catalyst; CC004(Catalytic Converter): Compressor Engine #4 - 3-way Catalyst; CC005(Catalytic Converter): Compressor Engine #5 - 3-w | Air Hygiene, Inc | 1980 hp | 1.0 g/hp-hr | 1,794 hp | 0.10 g/hp-hr | 7E | Nitrogen Dioxide | PASS | NA | Y
2014 | 1677 | 0607015001 | Tri-County Compressor Station (MarkWest / Ohio Oil Gath | North of intersection of Hwy 379 and Town | Barnesville | 43713 |  | Belmont | P003 | Compressor Engine #3 - 1980 HP (15.43 MMBtu/hr) Waukesha P9390 - natural gas-fired four-stroke rich burn internal combustion engine equipped with a three-way oxidation catalyst controlling CH2O, CO, NOx, & VOCs by 80, 97, 98.5 & 66 percent respectively | 2014-11-12 | CC002(Catalytic Converter): Compressor Engine #2 - 3-way Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - 3-way Catalyst; CC004(Catalytic Converter): Compressor Engine #4 - 3-way Catalyst; CC005(Catalytic Converter): Compressor Engine #5 - 3-w | Air Hygiene, Inc | 1980 hp | 1.0 g/hp-hr | 1,526 hp | 0.08 g/hp-hr | 7E | Nitrogen Dioxide | PASS | NA | Y
2014 | 1680 | 0607015001 | Tri-County Compressor Station (MarkWest / Ohio Oil Gath | North of intersection of Hwy 379 and Town | Barnesville | 43713 |  | Belmont | P004 | Compressor Engine #4 - 1980 HP (15.43 MMBtu/hr) Waukesha P9390 - natural gas-fired four-stroke rich burn internal combustion engine equipped with a three-way oxidation catalyst controlling CH2O, CO, NOx, & VOCs by 80, 97, 98.5 & 66 percent respectively | 2014-11-12 | CC002(Catalytic Converter): Compressor Engine #2 - 3-way Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - 3-way Catalyst; CC004(Catalytic Converter): Compressor Engine #4 - 3-way Catalyst; CC005(Catalytic Converter): Compressor Engine #5 - 3-w | Air Hygiene, Inc | 1980 hp | 1.0 g/hp-hr | 1,525 hp | 0.15 g/hp-hr | 7E | Nitrogen Dioxide | PASS | NA | Y
2014 | 1681 | 0607015001 | Tri-County Compressor Station (MarkWest / Ohio Oil Gath | North of intersection of Hwy 379 and Town | Barnesville | 43713 |  | Belmont | P005 | Compressor Engine #5 - 1980 HP (15.43 MMBtu/hr) Waukesha P9390 - natural gas-fired four-stroke rich burn internal combustion engine equipped with a three-way oxidation catalyst controlling CH2O, CO, NOx, & VOCs by 80, 97, 98.5 & 66 percent respectively | 2014-11-12 | CC002(Catalytic Converter): Compressor Engine #2 - 3-way Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - 3-way Catalyst; CC004(Catalytic Converter): Compressor Engine #4 - 3-way Catalyst; CC005(Catalytic Converter): Compressor Engine #5 - 3-w | Air Hygiene, Inc | 1980 hp | 1.0 g/hp-hr | 1,482 hp | 0.17 g/hp-hr | 7E | Nitrogen Dioxide | PASS | NA | Y
2014 | 1684 | 0607015001 | Tri-County Compressor Station (MarkWest / Ohio Oil Gath | North of intersection of Hwy 379 and Town | Barnesville | 43713 |  | Belmont | P006 | Compressor Engine #6 - 1980 HP (15.43 MMBtu/hr) Waukesha P9390 - natural gas-fired four-stroke rich burn internal combustion engine equipped with a three-way oxidation catalyst controlling CH2O, CO, NOx, & VOCs by 80, 97, 98.5 & 66 percent respectively | 2014-11-12 | CC002(Catalytic Converter): Compressor Engine #2 - 3-way Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - 3-way Catalyst; CC004(Catalytic Converter): Compressor Engine #4 - 3-way Catalyst; CC005(Catalytic Converter): Compressor Engine #5 - 3-w | Air Hygiene, Inc | 1980 hp | 1.0 g/hp-hr | 1,794 hp | 0.10 g/hp-hr | 7E | Nitrogen Dioxide | PASS | NA | Y
2014 | 1687 | 0607015001 | Tri-County Compressor Station (MarkWest / Ohio Oil Gath | North of intersection of Hwy 379 and Town | Barnesville | 43713 |  | Belmont | P003 | Compressor Engine #3 - 1980 HP (15.43 MMBtu/hr) Waukesha P9390 - natural gas-fired four-stroke rich burn internal combustion engine equipped with a three-way oxidation catalyst controlling CH2O, CO, NOx, & VOCs by 80, 97, 98.5 & 66 percent respectively | 2014-11-29 | CC002(Catalytic Converter): Compressor Engine #2 - 3-way Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - 3-way Catalyst; CC004(Catalytic Converter): Compressor Engine #4 - 3-way Catalyst; CC005(Catalytic Converter): Compressor Engine #5 - 3-w | Air Hygiene, Inc | 1980 hp | 1.0 g/hp-hr | 1,526 hp | 0.08 g/hp-hr | 7E | Nitrogen Dioxide | PASS | NA | Y
2014 | 1692 | 0607015001 | Tri-County Compressor Station (MarkWest / Ohio Oil Gath | North of intersection of Hwy 379 and Town | Barnesville | 43713 |  | Belmont | P004 | Compressor Engine #4 - 1980 HP (15.43 MMBtu/hr) Waukesha P9390 - natural gas-fired four-stroke rich burn internal combustion engine equipped with a three-way oxidation catalyst controlling CH2O, CO, NOx, & VOCs by 80, 97, 98.5 & 66 percent respectively | 2014-11-29 | CC002(Catalytic Converter): Compressor Engine #2 - 3-way Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - 3-way Catalyst; CC004(Catalytic Converter): Compressor Engine #4 - 3-way Catalyst; CC005(Catalytic Converter): Compressor Engine #5 - 3-w | Air Hygiene, Inc | 1980 hp | 1.0 g/hp-hr | 1,525 hp | 0.15 g/hp-hr | 7E | Nitrogen Dioxide | PASS | NA | Y
2014 | 1695 | 0607015001 | Tri-County Compressor Station (MarkWest / Ohio Oil Gath | North of intersection of Hwy 379 and Town | Barnesville | 43713 |  | Belmont | P005 | Compressor Engine #5 - 1980 HP (15.43 MMBtu/hr) Waukesha P9390 - natural gas-fired four-stroke rich burn internal combustion engine equipped with a three-way oxidation catalyst controlling CH2O, CO, NOx, & VOCs by 80, 97, 98.5 & 66 percent respectively | 2014-11-29 | CC002(Catalytic Converter): Compressor Engine #2 - 3-way Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - 3-way Catalyst; CC004(Catalytic Converter): Compressor Engine #4 - 3-way Catalyst; CC005(Catalytic Converter): Compressor Engine #5 - 3-w | Air Hygiene, Inc | 1980 hp | 1.0 g/hp-hr | 1,482 hp | 0.17 g/hp-hr | 7E | Nitrogen Dioxide | PASS | NA | Y
2014 | 1696 | 0607015001 | Tri-County Compressor Station (MarkWest / Ohio Oil Gath | North of intersection of Hwy 379 and Town | Barnesville | 43713 |  | Belmont | P006 | Compressor Engine #6 - 1980 HP (15.43 MMBtu/hr) Waukesha P9390 - natural gas-fired four-stroke rich burn internal combustion engine equipped with a three-way oxidation catalyst controlling CH2O, CO, NOx, & VOCs by 80, 97, 98.5 & 66 percent respectively | 2014-11-29 | CC002(Catalytic Converter): Compressor Engine #2 - 3-way Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - 3-way Catalyst; CC004(Catalytic Converter): Compressor Engine #4 - 3-way Catalyst; CC005(Catalytic Converter): Compressor Engine #5 - 3-w | Air Hygiene, Inc | 1980 hp | 1.0 g/hp-hr | 1,794 hp | 0.10 g/hp-hr | 7E | Nitrogen Dioxide | PASS | NA | Y
2014 | 1733 | 0634005027 | Arrowhead Compressor Station | E of Clements Rd and S of Jockey Hollow | Athens Twp. | 43977 |  | Harrison | P006 | Compressor Engine #3 - Caterpillar G3608 - natural gas fired four-stroke, lean burn internal combustion engine rated at an operating capacity of 2,370 horsepower equipped with a catalytic convertor. | 2014-05-01 | CC003(Catalytic Converter): Compressor Engine #3 Catalytic Convertor | Air Hygiene | 2,370 hp | 0.5 g/hp-hr | 2,212 hp | 0.18 g/hp-hr | 7E | Nitrogen Dioxide | PASS | NA | Y
2014 | 1737 | 0634005027 | Arrowhead Compressor Station | E of Clements Rd and S of Jockey Hollow | Athens Twp. | 43977 |  | Harrison | P007 | Compressor Engine #4 - Caterpillar G3608 - natural gas fired four-stroke, lean burn internal combustion engine rated at an operating capacity of 2,370 horsepower equipped with a catalytic convertor | 2014-06-18 | CC004(Catalytic Converter): Compressor Engine #4 Catalytic Convertor | Air Hygiene | 2,370 hp | 0.5 g/hp-hr | 2,165 | 0.37 g/hp-hr | 7E | Nitrogen Dioxide | PASS | NA | Y
2014 | 1739 | 0634005027 | Arrowhead Compressor Station | E of Clements Rd and S of Jockey Hollow | Athens Twp. | 43977 |  | Harrison | P006 | Compressor Engine #3 - Caterpillar G3608 - natural gas fired four-stroke, lean burn internal combustion engine rated at an operating capacity of 2,370 horsepower equipped with a catalytic convertor. | 2014-09-12 | CC003(Catalytic Converter): Compressor Engine #3 Catalytic Convertor; CC004(Catalytic Converter): Compressor Engine #4 Catalytic Convertor | Air Hygeine International | 2370 Hp | 0.50 g/Hp-hr | 2243 Hp | 0.29 g/Hp-hr | 7E | Nitrogen Dioxide | PASS | NA | Y
2014 | 1742 | 0634005027 | Arrowhead Compressor Station | E of Clements Rd and S of Jockey Hollow | Athens Twp. | 43977 |  | Harrison | P007 | Compressor Engine #4 - Caterpillar G3608 - natural gas fired four-stroke, lean burn internal combustion engine rated at an operating capacity of 2,370 horsepower equipped with a catalytic convertor | 2014-09-12 | CC003(Catalytic Converter): Compressor Engine #3 Catalytic Convertor; CC004(Catalytic Converter): Compressor Engine #4 Catalytic Convertor | Air Hygeine International | 2370 Hp | 0.50 g/Hp-hr | 2185 Hp | 0.35 g/Hp-hr | 7E | Nitrogen Dioxide | PASS | NA | Y
2014 | 1746 | 0634005027 | Arrowhead Compressor Station | E of Clements Rd and S of Jockey Hollow | Athens Twp. | 43977 |  | Harrison | P008 | Compressor Engine #5 - Caterpillar G3608 - natural gas fired four-stroke, lean burn internal combustion engine rated at an operating capacity of 2,370 horsepower equipped with a catalytic convertor | 2014-11-20 | CC005(Catalytic Converter): Compressor Engine #5 Catalytic Convertor | Air Hygiene, Inc. | 2370 Hp | 1.0 g/Hp-hr | 2209 Hp | 0.32 g/Hp-hr | 7E | Nitrogen Dioxide | PASS | NA | Y
2014 | 1748 | 0634005027 | Arrowhead Compressor Station | E of Clements Rd and S of Jockey Hollow | Athens Twp. | 43977 |  | Harrison | P009 | Compressor Engine #6 - Caterpillar G3608 - natural gas fired four-stroke, lean burn internal combustion engine rated at an operating capacity of 2,370 horsepower equipped with a catalytic convertor | 2014-11-20 | CC006(Catalytic Converter): Compressor Engine #6 Catalytic Convertor; CC07(Catalytic Converter): Compressor Engine #7 Catalytic Convertor; CC008(Catalytic Converter): Compressor Engine #8 Catalytic Convertor | Air Hygiene Inc. | 2370 Hp | 1.0 g/Hp-hr | 2207 Hp | 0.43 g/Hp-hr | 7E | Nitrogen Dioxide | PASS | NA | Y
2014 | 1751 | 0634005027 | Arrowhead Compressor Station | E of Clements Rd and S of Jockey Hollow | Athens Twp. | 43977 |  | Harrison | P010 | Compressor Engine #7 - Caterpillar G3608 - natural gas fired four-stroke, lean burn internal combustion engine rated at an operating capacity of 2,370 horsepower equipped with a catalytic convertor | 2014-11-20 | CC006(Catalytic Converter): Compressor Engine #6 Catalytic Convertor; CC07(Catalytic Converter): Compressor Engine #7 Catalytic Convertor; CC008(Catalytic Converter): Compressor Engine #8 Catalytic Convertor | Air Hygiene Inc. | 2370 Hp | 1.0 g/Hp-hr | 2252 Hp | 0.35 g/Hp-hr | 7E | Nitrogen Dioxide | PASS | NA | Y
2014 | 1756 | 0634005027 | Arrowhead Compressor Station | E of Clements Rd and S of Jockey Hollow | Athens Twp. | 43977 |  | Harrison | P011 | Compressor Engine #8 - Caterpillar G3608 - natural gas fired four-stroke, lean burn internal combustion engine rated at an operating capacity of 2,370 horsepower equipped with a catalytic convertor | 2014-11-20 | CC006(Catalytic Converter): Compressor Engine #6 Catalytic Convertor; CC07(Catalytic Converter): Compressor Engine #7 Catalytic Convertor; CC008(Catalytic Converter): Compressor Engine #8 Catalytic Convertor | Air Hygiene Inc. | 2370 Hp | 1.0 g/Hp-hr | 2197 Hp | 0.35 Hp-hr | 7E | Nitrogen Dioxide | PASS | NA | Y
2014 | 1758 | 0634005029 | Cadiz Gas Plant | 43071 Industrial Park Rd | Cadiz | 43907 |  | Harrison | P007 | Compressor Engine #7 - 4735 HP Caterpillar G3616 engine (CM-1206-7) - natural gas-fired four-stroke lean burn internal combustion engine equipped with an oxidation catalyst controlling CO, VOC and formaldehyde 95, 75, and 90 percent respectively. | 2014-12-19 | CC007(Catalytic Converter): oxidation catalyst; CC008(Catalytic Converter): oxidation catalyst | Air Hygiene | 4,735 Hp | 0.5 g/hp-hr | 4,376 hp | 0.27 g/hp-hr | 7E | Nitrogen Dioxide | PASS | NA | Y
2014 | 1763 | 0634005029 | Cadiz Gas Plant | 43071 Industrial Park Rd | Cadiz | 43907 |  | Harrison | P008 | Compressor Engine #8 - 4735 HP Caterpillar G3616 engine (CM-1206-8) - natural gas-fired four-stroke lean burn internal combustion engine equipped with an oxidation catalyst controlling CO, VOC and formaldehyde 95, 75, and 90 percent respectively. | 2014-12-19 | CC007(Catalytic Converter): oxidation catalyst; CC008(Catalytic Converter): oxidation catalyst | Air Hygiene | 4,735 Hp | 0.5 g/hp-hr | 4,378 Hp | 0.38 g/hp-hr | 7E | Nitrogen Dioxide | PASS | NA | Y
2014 | 1764 | 0634005033 | Harrison West Compressor Station | Possum Hollow Road | Freeport | 43973 |  | Harrison | P004 | Compressor Engine #4 - 1980 HP (15.43 MMBtu/hr) Waukesha P9390 - natural gas-fired four-stroke rich burn internal combustion engine equipped with a three-way oxidation catalyst controlling CH2O, CO, NOx, & VOCs by 80, 97, 98.5 & 66 percent respectively | 2014-04-08 | CC004(Catalytic Converter): Compressor Engine #4 - 3-way Catalyst | Air Hygiene International | 1,980 hp | 1.0 g/hp-hr | 1,782 hp | 0.032 g/hp-hr | 7E | Nitrogen Dioxide | PASS | NA | Y
2014 | 1768 | 0634005033 | Harrison West Compressor Station | Possum Hollow Road | Freeport | 43973 |  | Harrison | P005 | Compressor Engine #5 - 1980 HP (15.43 MMBtu/hr) Waukesha P9390 - natural gas-fired four-stroke rich burn internal combustion engine equipped with a three-way oxidation catalyst controlling CH2O, CO, NOx, & VOCs by 80, 97, 98.5 & 66 percent respectively | 2014-04-08 | CC005(Catalytic Converter): Compressor Engine #5 - 3-way Catalyst | Air Hygiene International | 1,980 hp | 1.0 g/hp-hr | 1,868 hp | 0.193 g/hr-hr | 7E | Nitrogen Dioxide | PASS | NA | Y
2014 | 1771 | 0634005033 | Harrison West Compressor Station | Possum Hollow Road | Freeport | 43973 |  | Harrison | P006 | Compressor Engine #6 - 1980 HP (15.43 MMBtu/hr) Waukesha P9390 - natural gas-fired four-stroke rich burn internal combustion engine equipped with a three-way oxidation catalyst controlling CH2O, CO, NOx, & VOCs by 80, 97, 98.5 & 66 percent respectively | 2014-04-08 | CC006(Catalytic Converter): Compressor Engine #6 - 3-way Catalyst | Air Hygiene International | 1,980 hp | 1.0 g/hp-hr | 1,840 hp | 0.085 g/hp-hr | 7E | Nitrogen Dioxide | PASS | NA | Y
2014 | 1774 | 0634005033 | Harrison West Compressor Station | Possum Hollow Road | Freeport | 43973 |  | Harrison | P001 | Compressor Engine #1 - 1480 HP (11.39 MMBtu/hr) Waukesha L7042 - natural gas-fired four-stroke rich burn internal combustion engine equipped with a three-way oxidation catalyst controlling CH2O, CO, NOx, & VOCs by 80, 97, 98.5 & 66 percent respectively | 2014-04-09 | CC001(Catalytic Converter): Compressor Engine #1 - 3-way Catalyst | Air Hygiene International | 1,480 hp | 1.0 g/hp-hr | 1,406 hp | 0.854 g/hp-hr | 7E | Nitrogen Dioxide | PASS | NA | Y
2014 | 1776 | 0634005033 | Harrison West Compressor Station | Possum Hollow Road | Freeport | 43973 |  | Harrison | P002 | Compressor Engine #2 - 1480 HP (11.39 MMBtu/hr) Waukesha L7042 - natural gas-fired four-stroke rich burn internal combustion engine equipped with a three-way oxidation catalyst controlling CH2O, CO, NOx, & VOCs by 80, 97, 98.5 & 66 percent respectively | 2014-04-09 | CC002(Catalytic Converter): Compressor Engine #2 - 3-way Catalyst | Air Hygiene International | 1,480 hp | 1.0 g/hp-hr | 1,881 hp | 0.459 g/hp-hr | 7E | Nitrogen Dioxide | PASS | NA | Y
2014 | 1779 | 0634005033 | Harrison West Compressor Station | Possum Hollow Road | Freeport | 43973 |  | Harrison | P007 | Compressor Engine #7 - 1980 HP (15.43 MMBtu/hr) Waukesha P9390 - natural gas-fired four-stroke rich burn internal combustion engine equipped with a three-way oxidation catalyst controlling CH2O, CO, NOx, & VOCs by 80, 97, 98.5 & 66 percent respectively | 2014-04-09 | CC007(Catalytic Converter): Compressor Engine #7 - 3-way Catalyst | Air Hygiene International | 1,980 hp | 1.0 g/hp-hr | 1,822 hp | 0.172 g/hp-hr | 7E | Nitrogen Dioxide | PASS | NA | Y
2014 | 1782 | 0634005033 | Harrison West Compressor Station | Possum Hollow Road | Freeport | 43973 |  | Harrison | P001 | Compressor Engine #1 - 1480 HP (11.39 MMBtu/hr) Waukesha L7042 - natural gas-fired four-stroke rich burn internal combustion engine equipped with a three-way oxidation catalyst controlling CH2O, CO, NOx, & VOCs by 80, 97, 98.5 & 66 percent respectively | 2014-12-11 | CC001(Catalytic Converter): Compressor Engine #1 - 3-way Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - 3-way Catalyst; CC004(Catalytic Converter): Compressor Engine #4 - 3-way Catalyst; CC007(Catalytic Converter): Compressor Engine #7 - 3-w | Air Hygiene, Inc. | 1,480 hp | 0.20 g/hp-hr | 1,324 hp | 0.175 g/hp-hr | 7E | Nitrogen Dioxide | PASS | NA | Y
2014 | 1785 | 0634005033 | Harrison West Compressor Station | Possum Hollow Road | Freeport | 43973 |  | Harrison | P003 | Compressor Engine #3 - 1980 HP (15.43 MMBtu/hr) Waukesha P9390 - natural gas-fired four-stroke rich burn internal combustion engine equipped with a three-way oxidation catalyst controlling CH2O, CO, NOx, & VOCs by 80, 97, 98.5 & 66 percent respectively | 2014-12-11 | CC001(Catalytic Converter): Compressor Engine #1 - 3-way Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - 3-way Catalyst; CC004(Catalytic Converter): Compressor Engine #4 - 3-way Catalyst; CC007(Catalytic Converter): Compressor Engine #7 - 3-w | Air Hygiene, Inc. | 1,980 hp | 0.20 g/hp-hr | 1,820 hp | 0.02 g/hp-hr | 7E | Nitrogen Dioxide | PASS | NA | Y
2014 | 1788 | 0634005033 | Harrison West Compressor Station | Possum Hollow Road | Freeport | 43973 |  | Harrison | P004 | Compressor Engine #4 - 1980 HP (15.43 MMBtu/hr) Waukesha P9390 - natural gas-fired four-stroke rich burn internal combustion engine equipped with a three-way oxidation catalyst controlling CH2O, CO, NOx, & VOCs by 80, 97, 98.5 & 66 percent respectively | 2014-12-11 | CC001(Catalytic Converter): Compressor Engine #1 - 3-way Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - 3-way Catalyst; CC004(Catalytic Converter): Compressor Engine #4 - 3-way Catalyst; CC007(Catalytic Converter): Compressor Engine #7 - 3-w | Air Hygiene, Inc. | 1,980 hp | 0.20 g/hp-hr | 1,824 hp | 0.031 g/hp-hr | 7E | Nitrogen Dioxide | PASS | NA | Y
2014 | 1792 | 0634005033 | Harrison West Compressor Station | Possum Hollow Road | Freeport | 43973 |  | Harrison | P007 | Compressor Engine #7 - 1980 HP (15.43 MMBtu/hr) Waukesha P9390 - natural gas-fired four-stroke rich burn internal combustion engine equipped with a three-way oxidation catalyst controlling CH2O, CO, NOx, & VOCs by 80, 97, 98.5 & 66 percent respectively | 2014-12-11 | CC001(Catalytic Converter): Compressor Engine #1 - 3-way Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - 3-way Catalyst; CC004(Catalytic Converter): Compressor Engine #4 - 3-way Catalyst; CC007(Catalytic Converter): Compressor Engine #7 - 3-w | Air Hygiene, Inc. | 1,980 hp | 0.20 g/hp-hr | 1,799 hp | 0.112 g/hp-hr | 7E | Nitrogen Dioxide | PASS | NA | Y
2014 | 1796 | 0634005033 | Harrison West Compressor Station | Possum Hollow Road | Freeport | 43973 |  | Harrison | P001 | Compressor Engine #1 - 1480 HP (11.39 MMBtu/hr) Waukesha L7042 - natural gas-fired four-stroke rich burn internal combustion engine equipped with a three-way oxidation catalyst controlling CH2O, CO, NOx, & VOCs by 80, 97, 98.5 & 66 percent respectively | 2014-12-12 | CC001(Catalytic Converter): Compressor Engine #1 - 3-way Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - 3-way Catalyst; CC004(Catalytic Converter): Compressor Engine #4 - 3-way Catalyst; CC007(Catalytic Converter): Compressor Engine #7 - 3-w | Air Hygiene, Inc. | 1,480 hp | 0.20 g/hp-hr | 1,324 hp | 0.175 g/hp-hr | 7E | Nitrogen Dioxide | PASS | NA | Y
2014 | 1797 | 0634005033 | Harrison West Compressor Station | Possum Hollow Road | Freeport | 43973 |  | Harrison | P003 | Compressor Engine #3 - 1980 HP (15.43 MMBtu/hr) Waukesha P9390 - natural gas-fired four-stroke rich burn internal combustion engine equipped with a three-way oxidation catalyst controlling CH2O, CO, NOx, & VOCs by 80, 97, 98.5 & 66 percent respectively | 2014-12-12 | CC001(Catalytic Converter): Compressor Engine #1 - 3-way Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - 3-way Catalyst; CC004(Catalytic Converter): Compressor Engine #4 - 3-way Catalyst; CC007(Catalytic Converter): Compressor Engine #7 - 3-w | Air Hygiene, Inc. | 1,980 hp | 0.20 g/hp-hr | 1,820 hp | 0.02 g/hp-hr | 7E | Nitrogen Dioxide | PASS | NA | Y
2014 | 1802 | 0634005033 | Harrison West Compressor Station | Possum Hollow Road | Freeport | 43973 |  | Harrison | P004 | Compressor Engine #4 - 1980 HP (15.43 MMBtu/hr) Waukesha P9390 - natural gas-fired four-stroke rich burn internal combustion engine equipped with a three-way oxidation catalyst controlling CH2O, CO, NOx, & VOCs by 80, 97, 98.5 & 66 percent respectively | 2014-12-12 | CC001(Catalytic Converter): Compressor Engine #1 - 3-way Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - 3-way Catalyst; CC004(Catalytic Converter): Compressor Engine #4 - 3-way Catalyst; CC007(Catalytic Converter): Compressor Engine #7 - 3-w | Air Hygiene, Inc. | 1,980 hp | 0.20 g/hp-hr | 1,824 hp | 0.031 g/hp-hr | 7E | Nitrogen Dioxide | PASS | NA | Y
2014 | 1805 | 0634005033 | Harrison West Compressor Station | Possum Hollow Road | Freeport | 43973 |  | Harrison | P007 | Compressor Engine #7 - 1980 HP (15.43 MMBtu/hr) Waukesha P9390 - natural gas-fired four-stroke rich burn internal combustion engine equipped with a three-way oxidation catalyst controlling CH2O, CO, NOx, & VOCs by 80, 97, 98.5 & 66 percent respectively | 2014-12-12 | CC001(Catalytic Converter): Compressor Engine #1 - 3-way Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - 3-way Catalyst; CC004(Catalytic Converter): Compressor Engine #4 - 3-way Catalyst; CC007(Catalytic Converter): Compressor Engine #7 - 3-w | Air Hygiene, Inc. | 1,980 hp | 0.20 g/hp-hr | 1,799 hp | 0.112 g/hp-hr | 7E | Nitrogen Dioxide | PASS | NA | Y
2014 | 1806 | 0634005034 | Lake Compressor Station | County Highway 21 | Freeport | 43973 |  | Harrison | P003 | Compressor Engine #3 - 1980 HP (15.43 MMBtu/hr) Waukesha P9390 - natural gas-fired four-stroke rich burn internal combustion engine equipped with a three-way oxidation catalyst controlling CH2O, CO, NOx, & VOCs by 80, 97, 98.5 & 66 percent respectively | 2014-04-10 | CC003(Catalytic Converter): Compressor Engine #3 - 3-way Catalyst | Air Hygiene Internatjional | 1980 hp | 1.0 g/hp-hr | 1,782 hp | 0.225 g/hp-hr | 7E | Nitrogen Dioxide | PASS | NA | Y
2014 | 1810 | 0634005034 | Lake Compressor Station | County Highway 21 | Freeport | 43973 |  | Harrison | P004 | Compressor Engine #4 - 1980 HP (15.43 MMBtu/hr) Waukesha P9390 - natural gas-fired four-stroke rich burn internal combustion engine equipped with a three-way oxidation catalyst controlling CH2O, CO, NOx, & VOCs by 80, 97, 98.5 & 66 percent respectively | 2014-04-10 | CC004(Catalytic Converter): Compressor Engine #4 - 3-way Catalyst | Air Hygiene International | 1,980 hp | 1.0 g/hp-hr | 1,782 | 0.269 g/hp-hr | 7E | Nitrogen Dioxide | PASS | NA | Y
2014 | 1814 | 0634005034 | Lake Compressor Station | County Highway 21 | Freeport | 43973 |  | Harrison | P005 | Compressor Engine #5 - 1980 HP (15.43 MMBtu/hr) Waukesha P9390 - natural gas-fired four-stroke rich burn internal combustion engine equipped with a three-way oxidation catalyst controlling CH2O, CO, NOx, & VOCs by 80, 97, 98.5 & 66 percent respectively | 2014-04-10 | CC005(Catalytic Converter): Compressor Engine #5 - 3-way Catalyst | Air Hygiene International | 1,980 | 1.0 g/hp-hr | 1,441 hp | 0.703 g/hp-hr | 7E | Nitrogen Dioxide | PASS | NA | Y
2014 | 1817 | 0634005034 | Lake Compressor Station | County Highway 21 | Freeport | 43973 |  | Harrison | P001 | Compressor Engine #1 - 1480 HP (11.39 MMBtu/hr) Waukesha L7042 - natural gas-fired four-stroke rich burn internal combustion engine equipped with a three-way oxidation catalyst controlling CH2O, CO, NOx, & VOCs by 80, 97, 98.5 & 66 percent respectively | 2014-04-11 | CC001(Catalytic Converter): Compressor Engine #1 - 3-way Catalyst | Air Hygiene International | 1,480 hp | 1.0 g/hp-hr | 1,480 hp | 0.075 g/hp-hr | 7E | Nitrogen Dioxide | PASS | NA | Y
2014 | 1818 | 0634005034 | Lake Compressor Station | County Highway 21 | Freeport | 43973 |  | Harrison | P002 | Compressor Engine #2 - 1480 HP (11.39 MMBtu/hr) Waukesha L7042 - natural gas-fired four-stroke rich burn internal combustion engine equipped with a three-way oxidation catalyst controlling CH2O, CO, NOx, & VOCs by 80, 97, 98.5 & 66 percent respectively | 2014-04-11 | CC002(Catalytic Converter): Compressor Engine #2 - 3-way Catalyst | Air Hygiene International | 1,480 hp | 1.0 g/hp-hr | 1,280 hp | 0.326 g/hp-hr | 7E | Nitrogen Dioxide | PASS | NA | Y
2014 | 1823 | 0634005034 | Lake Compressor Station | County Highway 21 | Freeport | 43973 |  | Harrison | P002 | Compressor Engine #2 - 1480 HP (11.39 MMBtu/hr) Waukesha L7042 - natural gas-fired four-stroke rich burn internal combustion engine equipped with a three-way oxidation catalyst controlling CH2O, CO, NOx, & VOCs by 80, 97, 98.5 & 66 percent respectively | 2014-12-15 | CC002(Catalytic Converter): Compressor Engine #2 - 3-way Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - 3-way Catalyst; CC004(Catalytic Converter): Compressor Engine #4 - 3-way Catalyst; CC005(Catalytic Converter):; CC011(Catalytic Converter | Air Hygiene, Inc | 1,480 hp | 0.20 g/hp-hr | 1,151 hp | 0.11 g/hp-hr | 7E | Nitrogen Dioxide | PASS | NA | Y
2014 | 1824 | 0634005034 | Lake Compressor Station | County Highway 21 | Freeport | 43973 |  | Harrison | P003 | Compressor Engine #3 - 1980 HP (15.43 MMBtu/hr) Waukesha P9390 - natural gas-fired four-stroke rich burn internal combustion engine equipped with a three-way oxidation catalyst controlling CH2O, CO, NOx, & VOCs by 80, 97, 98.5 & 66 percent respectively | 2014-12-15 | CC002(Catalytic Converter): Compressor Engine #2 - 3-way Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - 3-way Catalyst; CC004(Catalytic Converter): Compressor Engine #4 - 3-way Catalyst; CC005(Catalytic Converter):; CC011(Catalytic Converter | Air Hygiene, Inc | 1,980 hp | 0.20 g/hp-hr | 1,571 hp | 0.001 g/hp-hr | 7E | Nitrogen Dioxide | PASS | NA | Y
2014 | 1829 | 0634005034 | Lake Compressor Station | County Highway 21 | Freeport | 43973 |  | Harrison | P004 | Compressor Engine #4 - 1980 HP (15.43 MMBtu/hr) Waukesha P9390 - natural gas-fired four-stroke rich burn internal combustion engine equipped with a three-way oxidation catalyst controlling CH2O, CO, NOx, & VOCs by 80, 97, 98.5 & 66 percent respectively | 2014-12-15 | CC002(Catalytic Converter): Compressor Engine #2 - 3-way Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - 3-way Catalyst; CC004(Catalytic Converter): Compressor Engine #4 - 3-way Catalyst; CC005(Catalytic Converter):; CC011(Catalytic Converter | Air Hygiene, Inc | 1,980 hp | 0.20 g/hp-hr | 1,677 hp | 0.019 g/hp-hr | 7E | Nitrogen Dioxide | PASS | NA | Y
2014 | 1831 | 0634005034 | Lake Compressor Station | County Highway 21 | Freeport | 43973 |  | Harrison | P011 | Compressor Engine #9 - Waukesha L7042 - natural gas fired four-stroke, rich burn internal combustion engine rated at an operating capacity of 1,480 horsepower equipped with a three-way oxidation catalyst. | 2014-12-15 | CC002(Catalytic Converter): Compressor Engine #2 - 3-way Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - 3-way Catalyst; CC004(Catalytic Converter): Compressor Engine #4 - 3-way Catalyst; CC005(Catalytic Converter):; CC011(Catalytic Converter | Air Hygiene, Inc | 1,480 hp | 0.20 g/hp-hr | 1,014 hp | 0.151 g/hp-hr | 7E | Nitrogen Dioxide | PASS | NA | Y
2014 | 1834 | 0634005034 | Lake Compressor Station | County Highway 21 | Freeport | 43973 |  | Harrison | P002 | Compressor Engine #2 - 1480 HP (11.39 MMBtu/hr) Waukesha L7042 - natural gas-fired four-stroke rich burn internal combustion engine equipped with a three-way oxidation catalyst controlling CH2O, CO, NOx, & VOCs by 80, 97, 98.5 & 66 percent respectively | 2014-12-16 | CC002(Catalytic Converter): Compressor Engine #2 - 3-way Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - 3-way Catalyst; CC004(Catalytic Converter): Compressor Engine #4 - 3-way Catalyst; CC005(Catalytic Converter):; CC011(Catalytic Converter | Air Hygiene, Inc | 1,480 hp | 0.20 g/hp-hr | 1,151 hp | 0.11 g/hp-hr | 7E | Nitrogen Dioxide | PASS | NA | Y
2014 | 1837 | 0634005034 | Lake Compressor Station | County Highway 21 | Freeport | 43973 |  | Harrison | P003 | Compressor Engine #3 - 1980 HP (15.43 MMBtu/hr) Waukesha P9390 - natural gas-fired four-stroke rich burn internal combustion engine equipped with a three-way oxidation catalyst controlling CH2O, CO, NOx, & VOCs by 80, 97, 98.5 & 66 percent respectively | 2014-12-16 | CC002(Catalytic Converter): Compressor Engine #2 - 3-way Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - 3-way Catalyst; CC004(Catalytic Converter): Compressor Engine #4 - 3-way Catalyst; CC005(Catalytic Converter):; CC011(Catalytic Converter | Air Hygiene, Inc | 1,980 hp | 0.20 g/hp-hr | 1,571 hp | 0.001 g/hp-hr | 7E | Nitrogen Dioxide | PASS | NA | Y
2014 | 1841 | 0634005034 | Lake Compressor Station | County Highway 21 | Freeport | 43973 |  | Harrison | P004 | Compressor Engine #4 - 1980 HP (15.43 MMBtu/hr) Waukesha P9390 - natural gas-fired four-stroke rich burn internal combustion engine equipped with a three-way oxidation catalyst controlling CH2O, CO, NOx, & VOCs by 80, 97, 98.5 & 66 percent respectively | 2014-12-16 | CC002(Catalytic Converter): Compressor Engine #2 - 3-way Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - 3-way Catalyst; CC004(Catalytic Converter): Compressor Engine #4 - 3-way Catalyst; CC005(Catalytic Converter):; CC011(Catalytic Converter | Air Hygiene, Inc | 1,980 hp | 0.20 g/hp-hr | 1,677 hp | 0.019 g/hp-hr | 7E | Nitrogen Dioxide | PASS | NA | Y
2014 | 1844 | 0634005034 | Lake Compressor Station | County Highway 21 | Freeport | 43973 |  | Harrison | P011 | Compressor Engine #9 - Waukesha L7042 - natural gas fired four-stroke, rich burn internal combustion engine rated at an operating capacity of 1,480 horsepower equipped with a three-way oxidation catalyst. | 2014-12-16 | CC002(Catalytic Converter): Compressor Engine #2 - 3-way Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - 3-way Catalyst; CC004(Catalytic Converter): Compressor Engine #4 - 3-way Catalyst; CC005(Catalytic Converter):; CC011(Catalytic Converter | Air Hygiene, Inc | 1,480 hp | 0.20 g/hp-hr | 1,014 hp | 0.151 g/hp-hr | 7E | Nitrogen Dioxide | PASS | NA | Y
2014 | 1845 | 0634005037 | Chesapeake Exploration LLC - Gotshall 14-12-5 Pad | Burrier Rd | Scio | 43986 |  | Harrison | P002 | Flash gas compressor equipped with catalyst, 211 hp, CAT G3306TA (Spark Ignition Internal Combustion Engine, P002) | 2014-04-09 | none | Alliance Source Testing | 211 hp | 160 ppm | 175 hp | 21.6 ppm | 7E | Nitrogen Dioxide | PASS | NA | Y
2014 | 1848 | 0634005040 | Archer Compressor Facility | County Highway 45 | Cadiz | 43907 |  | Harrison | P001 | Compressor Engine #1 - 1775 HP Caterpillar G3606 (4S-LB) - natural gas-fired four-cycle lean burn internal combustion engine rated equipped with an oxidation catalyst controlling CO and VOC emissions. | 2014-11-10 | OxidCat-101(Catalytic Converter): Oxidative Catalyst | EcoTest Energy Inc. | 1775 Hp | 1.0 g/Hp-hr | 1608 Hp | 0.29 g/Hp-hr | 7E | Nitrogen Dioxide | PASS | NA | Y | Method 7E not used. Method 205, 320 and ASTM 6348-3 used. FTIR
2014 | 1853 | 0634005040 | Archer Compressor Facility | County Highway 45 | Cadiz | 43907 |  | Harrison | P002 | Compressor Engine #2 - 1775 HP Caterpillar G3606 (4S-LB) - natural gas-fired four-cycle lean burn internal combustion engine rated equipped with an oxidation catalyst controlling CO and VOC emissions. | 2014-11-10 | OxidCat-102(Catalytic Converter): Oxidative Catalyst | EcoTest Energy Services | 1775 Hp | 1.0 g/Hp-hr | 1600 Hp | 0.43 g/Hp-hr | 7E | Nitrogen Dioxide | PASS | NA | Y | Method 7E not used. Method 205, 320 and ASTM 6348-3 FTIR
2014 | 1856 | 0634005040 | Archer Compressor Facility | County Highway 45 | Cadiz | 43907 |  | Harrison | P003 | Compressor Engine #3 - 1775 HP Caterpillar G3606 (4S-LB) - natural gas-fired four-cycle lean burn internal combustion engine rated equipped with an oxidation catalyst controlling CO and VOC emissions. | 2014-11-10 | OxidCat-103(Catalytic Converter): Oxidative Catalyst | EcoTest Energy Services | 1775 Hp | 1.0 0 g/Hp-hr | 1627 Hp | 0.35 g/Hp-hr | 7E | Nitrogen Dioxide | PASS | NA | Y | Method 7E not used. Method 205, 320 and ASTM 6348-3 used. FTIR
2014 | 1858 | 0634005040 | Archer Compressor Facility | County Highway 45 | Cadiz | 43907 |  | Harrison | P004 | Compressor Engine #4 - 1775 HP Caterpillar G3606 (4S-LB) - natural gas-fired four-cycle lean burn internal combustion engine rated equipped with an oxidation catalyst controlling CO and VOC emissions. | 2014-11-10 | OxidCat-104(Catalytic Converter): Oxidative Catalyst | EcoTest Energy Services | 1775 Hp | 1.00 g/Hp-hr | 1642 Hp | 0.4 g/Hp-hr | 7E | Nitrogen Dioxide | PASS | NA | Y | Method 7E not used. Methods 205, 320 and ASTM 6348-3 FTIR
2014 | 1860 | 0634005040 | Archer Compressor Facility | County Highway 45 | Cadiz | 43907 |  | Harrison | P005 | Compressor Engine #5 - 1775 HP Caterpillar G3606 (4S-LB) - natural gas-fired four-cycle lean burn internal combustion engine rated equipped with an oxidation catalyst controlling CO and VOC emissions. | 2014-11-11 | OxidCat-105(Catalytic Converter): Oxidative Catalyst | EcoTest Energy Services | 1775 Hp | 1.00 g/Hp-hr | 1638 Hp | 0.4 g/Hp-hr | 7E | Nitrogen Dioxide | PASS | NA | Y | Method 7E not used. Methods 205, 320 and ASTM 6348-3 FTIR
2014 | 1864 | 0634005040 | Archer Compressor Facility | County Highway 45 | Cadiz | 43907 |  | Harrison | P006 | Compressor Engine #6 - 1775 HP Caterpillar G3606 (4S-LB) - natural gas-fired four-cycle lean burn internal combustion engine rated equipped with an oxidation catalyst controlling CO and VOC emissions. | 2014-11-11 | OxidCat-106(Catalytic Converter): Oxidative Catalyst | EcoTest Services | 1775 Hp | 1.00 g/Hp-hr | 1683 Hp | 0.2 g/Hp-hr | 7E | Nitrogen Dioxide | PASS | NA | Y | Method 7E not used. Method 205, 320 and ASTM 6348-3 FTIR
2014 | 1866 | 0634005040 | Archer Compressor Facility | County Highway 45 | Cadiz | 43907 |  | Harrison | P007 | Compressor Engine #7 - 1775 HP Caterpillar G3606 (4S-LB) - natural gas-fired four-cycle lean burn internal combustion engine rated equipped with an oxidation catalyst controlling CO and VOC emissions. | 2014-11-12 | OxidCat-107(Catalytic Converter): Oxidative Catalyst | EcoTest Services | 1775 Hp | 1.00 g/Hp-hr | 1703 Hp | 0.3 g/Hp-hr | 7E | Nitrogen Dioxide | PASS | NA | Y | Method 7E not used. Method 205, 320 and ASSTM 6348-3 FTIR
2014 | 1871 | 0634005040 | Archer Compressor Facility | County Highway 45 | Cadiz | 43907 |  | Harrison | P008 | Compressor Engine #8 - 1775 HP Caterpillar G3606 (4S-LB) - natural gas-fired four-cycle lean burn internal combustion engine rated equipped with an oxidation catalyst controlling CO and VOC emissions. | 2014-11-12 | OxidCat-108(Catalytic Converter): Oxidative Catalyst | EcoTest Energy Services | 1775 Hp | 1.00 g/Hp-hr | 1608 Hp | 0.341 g/Hp-hr | 7E | Nitrogen Dioxide | PASS | NA | Y | Method 7E not used. Methods 205, 320 and ASTM 6348-3 FTIR
2014 | 1874 | 0634005043 | Gulfport Energy- BK Stephens | 75501 Tyson Road | Cadiz | 43907 |  | Harrison | P002 | One or multiple stationary natural gas-fired spark ignition (SI) internal combustion engines (ICE) wiht a combined total horsepower (HP) of no more than 1,800 HP for the site. | 2014-07-02 | none | BCMJ Control Inc | 400 Hp | 2.0 g/Hp-hr | 280 Hp | 0.56 g/Hp-hr | 7E | Nitrogen Dioxide | PASS | NA | Y | 400 Hp Waukesha engine-Serial #-C-17249/1-results above 203 Hp Caterpillar engine-Serial #4FD18737- tested rate: 0.16 g/Hp-hr NOX 0.1 g/Hp-hr CO 0.13 g/Hp-hr VOC allowable rate: 2.0 g/Hp-hr NOX 4.0 g/Hp-hr CO 1.0 g/Hp-hr VOC
2014 | 1876 | 0634005045 | Gulfport Energy- Clay Well Pad | 31501 Morrison Road | Freeport | 43973 |  | Harrison | P002 | One or multiple stationary natural gas-fired spark ignition (SI) internal combustion engines (ICE) with a combined total horsepower (HP) of no more than 1,800 HP for the site. Includes 2007 and later model year engines manufactured after the applicable effective date identified in 40 CFR 60.4230(a)(3) and engines manufactured before the NSPS effective date where compliance with the Part 60 Subpart JJJJ emissions standards for the same size engine can be demonstrated through stack testing. | 2014-07-08 | none-carbureted air fuel mix to control emissions | BCMJ Control, Inc. | 145 Hp | 2.0 g/Hp-hr | 53 Hp | 0.1 g/Hp-hr | 7E | Nitrogen Dioxide | PASS | NA | Y | Serial # 9TG00298 2.0 g/Hp-hr 630 Hp 1.15 g/Hp-hr 350 Method 320-infra red
2014 | 1880 | 0634005048 | Gulfport Energy- Boy Scout Well Pad | 79900 Adams Rd | Tippecanoe | 44699 |  | Harrison | P002 | One 60 hp Waukesha 310 and one 64 hp HEC 3491-OPV natural gas engines for compressors | 2014-07-02 | none | BCMJ Controls, Inc | 400 Hp | 2.0 g/Hp-hr 400 Hp Waukesha | 217 Hp | 1.62 g/Hp-hr | 7E | Nitrogen Dioxide | PASS | NA | Y | 118 hp Cummins engine(same allowable rates as above) 0.11 g/Hp-hr NOX 145 Hp Caterpillar engine (one hour run only-same allowable rates as above) 4.91 g/Hp-hr NOX- Fail
2014 | 1881 | 0634005049 | Gulfport Energy- Ryser #1-25H Well Pad | 77100 Scott Hill Road | Flushing | 43977 |  | Harrison | P002 | One or multiple stationary natural gas-fired spark ignition (SI) internal combustion engines (ICE) with a combined total horsepower (HP) of no more than 1,800 HP for the site. | 2014-07-07 | catalytic reduction | BCMJ Control, Inc | 325 Hp caterpillar engine S#4FD00578 | 2.0 g/Hp-hr | 134 Hp | 0.34 g/Hp-hr | 7E | Nitrogen Dioxide | PASS | NA | Y | 215 Hp Caterpillar engine-NOX 2.0 g/Hp-hr 215 Hp 0.34 g/Hp-hr 36 Hp S# G6X00951
2014 | 1884 | 0634005054 | Gulfport Energy - Lyons Well Pad | 27650 Friendly Ridge Rd | Tippecanoe | 44699 |  | Harrison | P002 | Two 50-hp Blackmer 942 natural gas-fired engines for compressors. | 2014-08-06 | non selective catalytic reduction | BCMJ Controls, Inc | 380 Hp | 2.0 g/Hp-hr | 296 Hp | 0.12 g/Hp-hr | 7E | Nitrogen Dioxide | PASS | NA | Y
2014 | 1887 | 0634005056 | Scio Compressor Station | 37650 Bower Rd | Scio | 43988 |  | Harrison | P005 | Compressor Engine #5 - 1,775 HP Caterpillar G3606 (4S-LB) - natural gas-fired four-cycle lean burn internal combustion engine equipped with an oxidation catalyst controlling CO & VOC emissions | 2014-06-23 | CC005(Catalytic Converter): Compressor Engine #5 - Oxidation Catalyst | Alliance Source Testing | 1,775 Hp | 0.50 g/Hp-hr 82 ppm | 1,627 Hp | 0.50 g/Hp-hr 40.3 ppm | 7E | Nitrogen Dioxide | PASS | NA | Y
2014 | 1892 | 0634005056 | Scio Compressor Station | 37650 Bower Rd | Scio | 43988 |  | Harrison | P006 | Compressor Engine #6 - 1,775 HP Caterpillar G3606 (4S-LB) - natural gas-fired four-cycle lean burn internal combustion engine equipped with an oxidation catalyst controlling CO & VOC emissions | 2014-06-23 | CC006(Catalytic Converter): Compressor Engine #6 - Oxidation Catalyst | Alliance Source Testing | 1,775 Hp | 0.50 g/Hp-hr 82 ppm | 1,630 Hp | 0.2 g/Hp-hr 19.8 ppm | 7E | Nitrogen Dioxide | PASS | NA | Y
2014 | 1894 | 0634005056 | Scio Compressor Station | 37650 Bower Rd | Scio | 43988 |  | Harrison | P001 | Compressor Engine #1 - 1,775 HP Caterpillar G3606 (4S-LB) - natural gas-fired four-cycle lean burn internal combustion engine equipped with an oxidation catalyst controlling CO & VOC emissions. | 2014-06-24 | CC001(Catalytic Converter): Compressor Engine #1 - Oxidation Catalyst | Alliance Source Testing | 1,775 Hp | 0.50g/Hp-hr | 1,650 Hp | 0.2 g/Hp-hr | 7E | Nitrogen Dioxide | PASS | NA | Y
2014 | 1896 | 0634005056 | Scio Compressor Station | 37650 Bower Rd | Scio | 43988 |  | Harrison | P002 | Compressor Engine #2 - 1,775 HP Caterpillar G3606 (4S-LB) - natural gas-fired four-cycle lean burn internal combustion engine equipped with an oxidation catalyst controlling CO & VOC emissions | 2014-06-24 | CC002(Catalytic Converter): Compressor Engine #2 - Oxidation Catalyst | Alliance Source Testing | 2,775 Hp | 0.50 g/Hp-hr | 1,659 Hp | 0.2 g/Hp-hr | 7E | Nitrogen Dioxide | PASS | NA | Y
2014 | 1901 | 0634005056 | Scio Compressor Station | 37650 Bower Rd | Scio | 43988 |  | Harrison | P003 | Compressor Engine #3 - 1,775 HP Caterpillar G3606 (4S-LB) - natural gas-fired four-cycle lean burn internal combustion engine equipped with an oxidation catalyst controlling CO & VOC emissions | 2014-06-24 | CC003(Catalytic Converter): Compressor Engine #3 - Oxidation Catalyst | Alliance Source Testing | 1,775 Hp | 0.5 g/Hp-hr 82 ppm | 1,616 | 0.2 g/Hp-hr 21 ppm | 7E | Nitrogen Dioxide | PASS | NA | Y
2014 | 1902 | 0634005056 | Scio Compressor Station | 37650 Bower Rd | Scio | 43988 |  | Harrison | P004 | Compressor Engine #4 - 1,775 HP Caterpillar G3606 (4S-LB) - natural gas-fired four-cycle lean burn internal combustion engine equipped with an oxidation catalyst controlling CO & VOC emissions | 2014-06-24 | CC004(Catalytic Converter): Compressor Engine #4 - Oxidation Catalyst | Alliance Source Testing | 1,775 Hp | 0.50 g/Hp-hr 82 ppm | 1,651 Hp | 0.2 g/Hp-hr 20.2 ppm | 7E | Nitrogen Dioxide | PASS | NA | Y
2014 | 1906 | 0634005056 | Scio Compressor Station | 37650 Bower Rd | Scio | 43988 |  | Harrison | P007 | Compressor Engine #7 - 1,775 HP Caterpillar G3606 (4S-LB) - natural gas-fired four-cycle lean burn internal combustion engine equipped with an oxidation catalyst controlling CO & VOC emissions | 2014-06-25 | CC007(Catalytic Converter): Compressor Engine #7 - Oxidation Catalyst | Alliance Source Testing | 1,775 Hp | 0.05 g/Hp-hr 82 ppm | 1,605 Hp | 0.3 g/Hp-hr 26.5 ppm | 7E | Nitrogen Dioxide | PASS | NA | Y
2014 | 1908 | 0634005056 | Scio Compressor Station | 37650 Bower Rd | Scio | 43988 |  | Harrison | P008 | Compressor Engine #8 - 1,775 HP Caterpillar G3606 (4S-LB) - natural gas-fired four-cycle lean burn internal combustion engine equipped with an oxidation catalyst controlling CO & VOC emissions | 2014-06-25 | CC008(Catalytic Converter): Compressor Engine #8 - Oxidation Catalyst | Alliance Source Testing | 1,775 Hp | 0.50 g/Hp-hr 82 ppm | 1,615 Hp | 0.2 g/Hp-hr 20.9 ppm | 7E | Nitrogen Dioxide | PASS | NA | Y
2014 | 1912 | 0634005056 | Scio Compressor Station | 37650 Bower Rd | Scio | 43988 |  | Harrison | P009 | Compressor Engine #9 - 1,775 HP Caterpillar G3606 (4S-LB) - natural gas-fired four-cycle lean burn internal combustion engine equipped with an oxidation catalyst controlling CO & VOC emissions | 2014-06-25 | CC009(Catalytic Converter): Compressor Engine #9 - Oxidation Catalyst | Alliance Source Testing | 1,775 Hp | 0.50 g/Hp-hr 82 ppm | 1,613 Hp | 0.3 g/Hp-hr 24.6 ppm | 7E | Nitrogen Dioxide | PASS | Y | Y
2014 | 1914 | 0634005056 | Scio Compressor Station | 37650 Bower Rd | Scio | 43988 |  | Harrison | P010 | Compressor Engine #10 - 1,775 HP Caterpillar G3606 (4S-LB) - natural gas-fired four-cycle lean burn internal combustion engine equipped with an oxidation catalyst controlling CO & VOC emissions | 2014-06-25 | CC010(Catalytic Converter): Compressor Engine #10 - Oxidation Catalyst | Alliance Source Testing | 1,775 Hp | 0.50 g/Hp-hr 82 ppm | 1,602 | 0.3 g/Hp-hr 25.2 ppm | 7E | Nitrogen Dioxide | PASS | NA | Y
2014 | 1928 | 0634005058 | Atlas Noble, LLC - Cramblett Well Pad | Bowers Road | North Twp. | 43988 |  | Harrison | P002 | 415 Hp Caterpillar G379 TA natural gas fired recovery compressor engine equipped with a catalytic converter. (non JJJJ engine). 68 Hp Caterpillar VRG330 natural gas fired vapor recovery unit equipped with a catalytic convertor. | 2014-03-04 | none | Air Compliance Consultants | 415 hp | 160 ppm | 204 hp | 25 ppm | 7E | Nitrogen Dioxide | PASS | NA | Y
2014 | 1934 | 0634005059 | Chesapeake Exploration LLC - Kidd 21-12-6 Pad | Township Highway 219 - Beagle Club Rd | Scio | 43988 |  | Harrison | P002 | One or multiple stationary natural gas-fired spark ignition (SI) internal combustion engines (ICE) with a combined total horsepower (HP) of no more than 1,800 HP for the site.* Includes 2007 and later model year engines manufactured after the applicable effective date identified in 40 CFR 60.4230(a)(3) and engines manufactured before the NSPS effective date where compliance with the Part 60 Subpart JJJJ emissions standards for the same size engine can be demonstrated through stack testing. | 2014-06-30 | none | Alliance Source Testing | 211 Hp | 2.0 g/Hp-hr | 143 Hp | 0.04 g/Hp-hr | 7E | Nitrogen Dioxide | PASS | NA | Y
2014 | 1936 | 0634005072 | Gulfport Energy - Milliken | 31255 Cadiz-Piedmont Rd | Freeport | 43973 |  | Harrison | P002 | One or multiple stationary natural gas-fired spark ignition (SI) internal combustion engines (ICE) wiht a combined total horsepower (HP) of no more than 1,800 HP for the site. | 2014-08-12 | catalytic | BCMJ Controls Inc | 145 Hp Caterpillar S# O7Y05427 | 2.0 g/Hp-hr | 122 Hp | 1.15 g/Hp-hr | 7E | Nitrogen Dioxide | PASS | NA | Y | 60 Hp HEC engine 2.8 g/Hp-hr 60 Hp 0.11 g/Hp-hr 30 Hp
2014 | 1938 | 0634005077 | Gulfport Energy - Michael Well Pad | 75096 Tyson Rd | Flushing | 43977 |  | Harrison | P002 | One or multiple stationary natural gas-fired spark ignition (SI) internal combustion engines (ICE) wiht a combined total horsepower (HP) of no more than 1,800 HP for the site. | 2014-12-03 | none | Great Plains Analytical Services | 118 Hp | 2.0 g/Hp-hr | 53 Hp | 0.855 g/Hp-hr | 7E | Nitrogen Dioxide | PASS | NA | Y | method 7E not used. Method 1-3A and ASTM 6348-03 used
2014 | 1950 | 0656005010 | Dominion East Ohio - Switzerland Compressor Station | German Ridge Road | Switzerland Twp. | 43942 |  | Monroe | P003 | 3550 Hp Natural gas-fired (4SLB) Caterpillar model 3612 LE DM5309-06 compressor engines equipped with catalytic reduction (three-way). | 2014-11-11 | catalytic reduction | Air Compliance Consultants | 3550 Hp | 0.5 g/Hp-hr | 3242 | 0.36 g/Hp-hr | 7E | Nitrogen Dioxide | PASS | NA | Y
2014 | 1955 | 0656005010 | Dominion East Ohio - Switzerland Compressor Station | German Ridge Road | Switzerland Twp. | 43942 |  | Monroe | P001 | 3550 Hp Natural gas-fired (4SLB) Caterpillar model 3612 LE DM5309-06 compressor engines equipped with catalytic reduction (three-way). | 2014-11-12 | catalytic reduction | Air Compliance Consultants | 3550 Hp | 0.5 g/Hp-hr | 3408 Hp | 0.39 g/Hp-hr | 7E | Nitrogen Dioxide | PASS | NA | Y
2014 | 2002 | 0656005010 | Dominion East Ohio - Switzerland Compressor Station | German Ridge Road | Switzerland Twp. | 43942 |  | Monroe | P003 | 3550 Hp Natural gas-fired (4SLB) Caterpillar model 3612 LE DM5309-06 compressor engines equipped with catalytic reduction (three-way). | 2014-11-12 | catalytic reduction | Air Compliance Consultants | 3550 Hp | 0.5 g/Hp-hr | 3242 | 0.36 g/Hp-hr | 7E | Nitrogen Dioxide | PASS | NA | Y
2014 | 2008 | 0656005011 | Ormet Production Facility | 43879 St Rte 7 | Hannibal | 43931 |  | Monroe | P001 | CAT 3516BLE SI combustion engine 1380 bhp | 2014-10-30 | none in facility profile | EcoTest Energy Services | 1,380 Hp | 0.5 g/Hp-hr | 1,250 Hp | 0.5 g/Hp-hr | 6348 03 | NOx - Nitrogen Oxides | PASS | NA | Y | Method 320 used-not ASTM 6348-03
2014 | 2009 | 0656005011 | Ormet Production Facility | 43879 St Rte 7 | Hannibal | 43931 |  | Monroe | P001 | CAT 3516BLE SI combustion engine 1380 bhp | 2014-10-30 | none | EcoTest Energy Services | 1,380 Hp | 0.5 g/Hp-hr | 1,250 Hp | 0.5 g/Hp-hr | 7E | Nitrogen Dioxide | PASS | NA | Y | method 7E not used. method 320
2014 | 2012 | 0656105005 | E2 Appalachian Compression LLC - Reusser | Twp Hwy 68 and Twp Hwy 66 | Woodsfield | 43793 |  | Monroe | P003 | 1680 Hp. natural gas rich burn compressor engine - Waukesha L7044GSI | 2014-12-08 | C-3(Catalytic Converter): Engine #3 Catalyst; C-4(Catalytic Converter): Engine #4 Catalyst; C-5(Catalytic Converter): Engine #5 Catalyst; C-6(Catalytic Converter): Engine #6Catalyst; C-8(Catalytic Converter): Engine #8 Catalyst | E2 Energy Services | 1,680 hp | 0.99 lb/hr | 1,551 hp | 0.22 lb/hr | 6348 03 | NOx - Nitrogen Oxides | PASS | NA | Y
2014 | 2016 | 0656105005 | E2 Appalachian Compression LLC - Reusser | Twp Hwy 68 and Twp Hwy 66 | Woodsfield | 43793 |  | Monroe | P004 | 1680 Hp. natural gas rich burn compressor engine - Waukesha L7044GSI | 2014-12-08 | C-3(Catalytic Converter): Engine #3 Catalyst; C-4(Catalytic Converter): Engine #4 Catalyst; C-5(Catalytic Converter): Engine #5 Catalyst; C-6(Catalytic Converter): Engine #6Catalyst; C-8(Catalytic Converter): Engine #8 Catalyst | E2 Energy Services | 1,680 hp | 0.99 lb/hr | 1,590 hp | 0.06 lb/hr | 6348 03 | NOx - Nitrogen Oxides | PASS | NA | Y
2014 | 2020 | 0656105005 | E2 Appalachian Compression LLC - Reusser | Twp Hwy 68 and Twp Hwy 66 | Woodsfield | 43793 |  | Monroe | P005 | 1680 Hp. natural gas rich burn compressor engine - Waukesha L7044GSI | 2014-12-08 | C-3(Catalytic Converter): Engine #3 Catalyst; C-4(Catalytic Converter): Engine #4 Catalyst; C-5(Catalytic Converter): Engine #5 Catalyst; C-6(Catalytic Converter): Engine #6Catalyst; C-8(Catalytic Converter): Engine #8 Catalyst | E2 Energy Services | 1,680 hp | 0.99 lb/hr | 1,557 hp | 0.10 lb/hr | 6348 03 | NOx - Nitrogen Oxides | PASS | NA | Y
2014 | 2023 | 0656105005 | E2 Appalachian Compression LLC - Reusser | Twp Hwy 68 and Twp Hwy 66 | Woodsfield | 43793 |  | Monroe | P006 | 1680 Hp. natural gas rich burn compressor engine - Waukesha L7044GSI | 2014-12-08 | C-3(Catalytic Converter): Engine #3 Catalyst; C-4(Catalytic Converter): Engine #4 Catalyst; C-5(Catalytic Converter): Engine #5 Catalyst; C-6(Catalytic Converter): Engine #6Catalyst; C-8(Catalytic Converter): Engine #8 Catalyst | E2 Energy Services | 1,680 hp | 0.99 lb/hr | 1,551 hp | 0.06 lb/hr | 6348 03 | NOx - Nitrogen Oxides | PASS | NA | Y
2014 | 2025 | 0656105005 | E2 Appalachian Compression LLC - Reusser | Twp Hwy 68 and Twp Hwy 66 | Woodsfield | 43793 |  | Monroe | P008 | 1680 Hp. natural gas rich burn compressor engine - Waukesha L7044GSI | 2014-12-08 | C-3(Catalytic Converter): Engine #3 Catalyst; C-4(Catalytic Converter): Engine #4 Catalyst; C-5(Catalytic Converter): Engine #5 Catalyst; C-6(Catalytic Converter): Engine #6Catalyst; C-8(Catalytic Converter): Engine #8 Catalyst | E2 Energy Services | 1,680 hp | 0.99 lb/hr | 1,551 hp | 0.04 lb/hr | 6348 03 | NOx - Nitrogen Oxides | PASS | NA | Y
2014 | 2027 | 0656105005 | E2 Appalachian Compression LLC - Reusser | Twp Hwy 68 and Twp Hwy 66 | Woodsfield | 43793 |  | Monroe | P003 | 1680 Hp. natural gas rich burn compressor engine - Waukesha L7044GSI | 2014-12-10 | C-3(Catalytic Converter): Engine #3 Catalyst; C-4(Catalytic Converter): Engine #4 Catalyst; C-5(Catalytic Converter): Engine #5 Catalyst; C-6(Catalytic Converter): Engine #6Catalyst; C-8(Catalytic Converter): Engine #8 Catalyst | E2 Energy Services | 1,680 hp | 0.99 lb/hr | 1,551 hp | 0.22 lb/hr | 6348 03 | NOx - Nitrogen Oxides | PASS | NA | Y
2014 | 2032 | 0656105005 | E2 Appalachian Compression LLC - Reusser | Twp Hwy 68 and Twp Hwy 66 | Woodsfield | 43793 |  | Monroe | P004 | 1680 Hp. natural gas rich burn compressor engine - Waukesha L7044GSI | 2014-12-10 | C-3(Catalytic Converter): Engine #3 Catalyst; C-4(Catalytic Converter): Engine #4 Catalyst; C-5(Catalytic Converter): Engine #5 Catalyst; C-6(Catalytic Converter): Engine #6Catalyst; C-8(Catalytic Converter): Engine #8 Catalyst | E2 Energy Services | 1,680 hp | 0.99 lb/hr | 1,590 hp | 0.06 lb/hr | 6348 03 | NOx - Nitrogen Oxides | PASS | NA | Y
2014 | 2035 | 0656105005 | E2 Appalachian Compression LLC - Reusser | Twp Hwy 68 and Twp Hwy 66 | Woodsfield | 43793 |  | Monroe | P005 | 1680 Hp. natural gas rich burn compressor engine - Waukesha L7044GSI | 2014-12-10 | C-3(Catalytic Converter): Engine #3 Catalyst; C-4(Catalytic Converter): Engine #4 Catalyst; C-5(Catalytic Converter): Engine #5 Catalyst; C-6(Catalytic Converter): Engine #6Catalyst; C-8(Catalytic Converter): Engine #8 Catalyst | E2 Energy Services | 1,680 hp | 0.99 lb/hr | 1,557 hp | 0.10 lb/hr | 6348 03 | NOx - Nitrogen Oxides | PASS | NA | Y
2014 | 2038 | 0656105005 | E2 Appalachian Compression LLC - Reusser | Twp Hwy 68 and Twp Hwy 66 | Woodsfield | 43793 |  | Monroe | P006 | 1680 Hp. natural gas rich burn compressor engine - Waukesha L7044GSI | 2014-12-10 | C-3(Catalytic Converter): Engine #3 Catalyst; C-4(Catalytic Converter): Engine #4 Catalyst; C-5(Catalytic Converter): Engine #5 Catalyst; C-6(Catalytic Converter): Engine #6Catalyst; C-8(Catalytic Converter): Engine #8 Catalyst | E2 Energy Services | 1,680 hp | 0.99 lb/hr | 1,551 hp | 0.06 lb/hr | 6348 03 | NOx - Nitrogen Oxides | PASS | NA | Y
2014 | 2041 | 0656105005 | E2 Appalachian Compression LLC - Reusser | Twp Hwy 68 and Twp Hwy 66 | Woodsfield | 43793 |  | Monroe | P008 | 1680 Hp. natural gas rich burn compressor engine - Waukesha L7044GSI | 2014-12-10 | C-3(Catalytic Converter): Engine #3 Catalyst; C-4(Catalytic Converter): Engine #4 Catalyst; C-5(Catalytic Converter): Engine #5 Catalyst; C-6(Catalytic Converter): Engine #6Catalyst; C-8(Catalytic Converter): Engine #8 Catalyst | E2 Energy Services | 1,680 hp | 0.99 lb/hr | 1,551 hp | 0.04 lb/hr | 6348 03 | NOx - Nitrogen Oxides | PASS | NA | Y
2014 | 2042 | 0656105005 | E2 Appalachian Compression LLC - Reusser | Twp Hwy 68 and Twp Hwy 66 | Woodsfield | 43793 |  | Monroe | P003 | 1680 Hp. natural gas rich burn compressor engine - Waukesha L7044GSI | 2014-12-11 | C-3(Catalytic Converter): Engine #3 Catalyst; C-4(Catalytic Converter): Engine #4 Catalyst; C-5(Catalytic Converter): Engine #5 Catalyst; C-6(Catalytic Converter): Engine #6Catalyst; C-8(Catalytic Converter): Engine #8 Catalyst | E2 Energy Services | 1,680 hp | 0.99 lb/hr | 1,551 hp | 0.22 lb/hr | 6348 03 | NOx - Nitrogen Oxides | PASS | NA | Y
2014 | 2047 | 0656105005 | E2 Appalachian Compression LLC - Reusser | Twp Hwy 68 and Twp Hwy 66 | Woodsfield | 43793 |  | Monroe | P004 | 1680 Hp. natural gas rich burn compressor engine - Waukesha L7044GSI | 2014-12-11 | C-3(Catalytic Converter): Engine #3 Catalyst; C-4(Catalytic Converter): Engine #4 Catalyst; C-5(Catalytic Converter): Engine #5 Catalyst; C-6(Catalytic Converter): Engine #6Catalyst; C-8(Catalytic Converter): Engine #8 Catalyst | E2 Energy Services | 1,680 hp | 0.99 lb/hr | 1,590 hp | 0.06 lb/hr | 6348 03 | NOx - Nitrogen Oxides | PASS | NA | Y
2014 | 2049 | 0656105005 | E2 Appalachian Compression LLC - Reusser | Twp Hwy 68 and Twp Hwy 66 | Woodsfield | 43793 |  | Monroe | P005 | 1680 Hp. natural gas rich burn compressor engine - Waukesha L7044GSI | 2014-12-11 | C-3(Catalytic Converter): Engine #3 Catalyst; C-4(Catalytic Converter): Engine #4 Catalyst; C-5(Catalytic Converter): Engine #5 Catalyst; C-6(Catalytic Converter): Engine #6Catalyst; C-8(Catalytic Converter): Engine #8 Catalyst | E2 Energy Services | 1,680 hp | 0.99 lb/hr | 1,557 hp | 0.10 lb/hr | 6348 03 | NOx - Nitrogen Oxides | PASS | NA | Y
2014 | 2052 | 0656105005 | E2 Appalachian Compression LLC - Reusser | Twp Hwy 68 and Twp Hwy 66 | Woodsfield | 43793 |  | Monroe | P006 | 1680 Hp. natural gas rich burn compressor engine - Waukesha L7044GSI | 2014-12-11 | C-3(Catalytic Converter): Engine #3 Catalyst; C-4(Catalytic Converter): Engine #4 Catalyst; C-5(Catalytic Converter): Engine #5 Catalyst; C-6(Catalytic Converter): Engine #6Catalyst; C-8(Catalytic Converter): Engine #8 Catalyst | E2 Energy Services | 1,680 hp | 0.99 lb/hr | 1,551 hp | 0.06 lb/hr | 6348 03 | NOx - Nitrogen Oxides | PASS | NA | Y
2014 | 2055 | 0656105005 | E2 Appalachian Compression LLC - Reusser | Twp Hwy 68 and Twp Hwy 66 | Woodsfield | 43793 |  | Monroe | P008 | 1680 Hp. natural gas rich burn compressor engine - Waukesha L7044GSI | 2014-12-11 | C-3(Catalytic Converter): Engine #3 Catalyst; C-4(Catalytic Converter): Engine #4 Catalyst; C-5(Catalytic Converter): Engine #5 Catalyst; C-6(Catalytic Converter): Engine #6Catalyst; C-8(Catalytic Converter): Engine #8 Catalyst | E2 Energy Services | 1,680 hp | 0.99 lb/hr | 1,551 hp | 0.04 lb/hr | 6348 03 | NOx - Nitrogen Oxides | PASS | NA | Y
2014 | 2059 | 0656105006 | Eclipse Resources 1 LP - Tippens Pad | 40417 Eddy Ridge Road | Woodsfield | 43793 |  | Monroe | P002 | One or multiple stationary natural gas-fired spark ignition (SI) internal combustion engines (ICE) with a combined total horsepower (HP) of no more than 1,800 HP for the site.* Includes 2007 and later model year engines manufactured after the applicable effective date identified in 40 CFR 60.4230(a)(3) and engines manufactured before the NSPS effective date where compliance with the Part 60 Subpart JJJJ emissions standards for the same size engine can be demonstrated through stack testing. | 2014-06-25 | none | Windrock, Inc | 47 Hp Arrow engine E001 | 2.8 g/Hp-hr | 33 Hp | 0.83 g/Hp-hr | 7E | Nitrogen Dioxide | PASS | NA | Y | Arrow engine E001 serial # 4B081005143 was tested (it may have been removed from site or status not updated in Stars) Cummins model GRA855- Allowable NOX Emission Rate-2.0 g/Hp-hr Maximum Operating Rate-225 Hp NOX Emission Rate-0.48 g/Hp-hr Operating Rate-173 Hp
2014 | 2070 | 0661005002 | Summerfield Compressor Station | between CR-45 and HWY 233 | Caldwell | 43724 |  | Noble | P001 | Natural Gas Engine(1) 1,380 hp engine | 2014-05-01 | Catalyst 1(Catalytic Converter): Oxidation Catalyst 1;; Flare(Flare): FL-1 | Environmental Quality Management | 1,380 hp | 1.0 g/hp-hr | 889 hp | 0.597 g/hp-hr | 7E | Nitrogen Dioxide | PASS | NA | Y
2014 | 2074 | 0661005002 | Summerfield Compressor Station | between CR-45 and HWY 233 | Caldwell | 43724 |  | Noble | P002 | Natural Gas Engine (2) 1,380 hp | 2014-05-01 | Catalyst 2(Catalytic Converter): Oxidation Catalyst; Flare(Flare): FL-1 | Environmental Quality Management | 1,380 hp | 1.0 g/hp-hr | 911 hp | 0.689 g/hp-hr | 7E | Nitrogen Dioxide | PASS | NA | Y
2014 | 2078 | 0661005008 | Seneca Gas Plant | Zep Road | Summerfield | 43788 |  | Noble | P001 | Compressor Engine #1 - Natural gas-fired four-stroke lean burn (4SLB) internal combustion engine rated at an operating capacity of 4,735 horsepower (hp) and equipped with an oxidation catalyst. | 2014-04-07 | CC001(Catalytic Converter): Compressor Engine #1 - Catalyic Convertor | Air Hygiene International | 4,735 hp | 1.0 g/hp-hr | 4,356 ph | 0.391 g/hp-hr | 7E | Nitrogen Dioxide | PASS | NA | Y
2014 | 2080 | 0661005008 | Seneca Gas Plant | Zep Road | Summerfield | 43788 |  | Noble | P002 | Compressor Engine #2 - Natural gas-fired four-stroke lean burn (4SLB) internal combustion engine rated at an operating capacity of 4,735 horsepower (hp) and equipped with an oxidation catalyst. | 2014-04-07 | CC002(Catalytic Converter): Compressor Engine #2 - Catalytic Convertor | Air Hygiene International | 4,735 hp | 1.0 g/hp-hr | 4,404 hp | 0.362 g/hp-hr | 7E | Nitrogen Dioxide | PASS | NA | Y
2014 | 2082 | 0661005010 | E2 Appalachian Compression LLC - Upper Hill | Opossum Run Rd and Town Hwy 120 | Sarahsville | 43779 |  | Noble | P009 | 1,680 Hp. Waukesha (L7044GSI) natural gas-fired, rich burn, turbocharged, with oxidation catalyst, compressor engine. | 2014-07-15 | C-9(Catalytic Converter): Engine Catalyst | E2 Energy Services | 1,680 Hp | 0.99 lb/hr | 1,545 Hp | 0.02 lb/hr | 7E | Nitrogen Dioxide | PASS | NA | Y
2014 | 2086 | 0661005010 | E2 Appalachian Compression LLC - Upper Hill | Opossum Run Rd and Town Hwy 120 | Sarahsville | 43779 |  | Noble | P007 | 1,680 Hp. Waukesha (L7044GSI) natural gas-fired, rich burn, turbocharged, with oxidation catalyst, compressor engine. | 2014-11-06 | C-7(Catalytic Converter): Engine Catalyst; C-8(Catalytic Converter): Engine Catalyst; C-9(Catalytic Converter): Engine Catalyst | E2 Energy Services | 1680 Hp | 0.99 lb/hr | 1528 Hp | 0.42 lb/hr | 7E | Nitrogen Dioxide | PASS | NA | Y | Method 7 E not used. Method 3A and ASTM 6348-03 used
2014 | 2089 | 0661005010 | E2 Appalachian Compression LLC - Upper Hill | Opossum Run Rd and Town Hwy 120 | Sarahsville | 43779 |  | Noble | P008 | 1,680 Hp. Waukesha (L7044GSI) natural gas-fired, rich burn, turbocharged, with oxidation catalyst, compressor engine. | 2014-11-06 | C-7(Catalytic Converter): Engine Catalyst; C-8(Catalytic Converter): Engine Catalyst; C-9(Catalytic Converter): Engine Catalyst | E2 Energy Services | 1680 Hp | 0.99 lb/hr | 1221 Hp | 0.23 lb/hr | 7E | Nitrogen Dioxide | PASS | NA | Y | Method 7 E not used. Method 3A and ASTM 6348-03 used
2014 | 2091 | 0661005010 | E2 Appalachian Compression LLC - Upper Hill | Opossum Run Rd and Town Hwy 120 | Sarahsville | 43779 |  | Noble | P009 | 1,680 Hp. Waukesha (L7044GSI) natural gas-fired, rich burn, turbocharged, with oxidation catalyst, compressor engine. | 2014-11-06 | C-7(Catalytic Converter): Engine Catalyst; C-8(Catalytic Converter): Engine Catalyst; C-9(Catalytic Converter): Engine Catalyst | E2 Energy Services | 1680 Hp | 0.99 lb/hr | 1585 Hp | 0.22 lb/hr | 7E | Nitrogen Dioxide | PASS | NA | Y | Method 7 E not used. Method 3A and ASTM 6348-03 used
2014 | 2095 | 0661005010 | E2 Appalachian Compression LLC - Upper Hill | Opossum Run Rd and Town Hwy 120 | Sarahsville | 43779 |  | Noble | P004 | 1,680 Hp. Waukesha (L7044GSI) natural gas-fired, rich burn, turbocharged, with oxidation catalyst, compressor engine. | 2014-11-10 | C-4(Catalytic Converter): Engine Catalyst | E2 Energy Services | 1680 Hp | 0.99 lb/hr | 1547 Hp | 2.68 lb/hr | 7E | Nitrogen Dioxide | FAIL | NA | Y | Method 7E not used. Method 3a and ASTM 6348-03 used
2014 | 2099 | 0661005010 | E2 Appalachian Compression LLC - Upper Hill | Opossum Run Rd and Town Hwy 120 | Sarahsville | 43779 |  | Noble | P002 | 1,680 Hp. Waukesha (L7044GSI) natural gas-fired, rich burn, turbocharged, with oxidation catalyst, compressor engine. | 2014-11-12 | C-2(Catalytic Converter): Engine Catalyst; C-3(Catalytic Converter): Engine Catalyst | E2 Energy Services | 1680 Hp | 0.99 lb/hr | 1575 Hp | 0.46 lb/hr | 7E | Nitrogen Dioxide | PASS | NA | Y | Method 7E not used. Method 3A and ASTM 6348-03 used
2014 | 2101 | 0661005010 | E2 Appalachian Compression LLC - Upper Hill | Opossum Run Rd and Town Hwy 120 | Sarahsville | 43779 |  | Noble | P003 | 1,680 Hp. Waukesha (L7044GSI) natural gas-fired, rich burn, turbocharged, with oxidation catalyst, compressor engine. | 2014-11-12 | C-2(Catalytic Converter): Engine Catalyst; C-3(Catalytic Converter): Engine Catalyst | E2 Energy Services | 1680 Hp | 0.99 lb/hr | 1512 Hp | 0.80 lb/hr | 7E | Nitrogen Dioxide | PASS | NA | Y | Method 7E not used. Method 3A and ASTM 6348-03 used
2014 | 2105 | 0661005010 | E2 Appalachian Compression LLC - Upper Hill | Opossum Run Rd and Town Hwy 120 | Sarahsville | 43779 |  | Noble | P002 | 1,680 Hp. Waukesha (L7044GSI) natural gas-fired, rich burn, turbocharged, with oxidation catalyst, compressor engine. | 2014-11-13 | C-2(Catalytic Converter): Engine Catalyst; C-3(Catalytic Converter): Engine Catalyst | E2 Energy Services | 1680 Hp | 0.99 lb/hr | 1575 Hp | 0.46 lb/hr | 7E | Nitrogen Dioxide | PASS | NA | Y | Method 7E not used. Method 3A and ASTM 6348-03 used
2014 | 2107 | 0661005010 | E2 Appalachian Compression LLC - Upper Hill | Opossum Run Rd and Town Hwy 120 | Sarahsville | 43779 |  | Noble | P003 | 1,680 Hp. Waukesha (L7044GSI) natural gas-fired, rich burn, turbocharged, with oxidation catalyst, compressor engine. | 2014-11-13 | C-2(Catalytic Converter): Engine Catalyst; C-3(Catalytic Converter): Engine Catalyst | E2 Energy Services | 1680 Hp | 0.99 lb/hr | 1512 Hp | 0.80 lb/hr | 7E | Nitrogen Dioxide | PASS | NA | Y | Method 7E not used. Method 3A and ASTM 6348-03 used
2014 | 2424 | 0857103154 | PINNACLE GAS PRODUCERS LLC | 4220 PINNACLE RD | MORAINE | 45439 |  | Montgomery | B001 | 12 MMBtu/hour (1,626 bhp) pipeline quality gas/natural gas-fired compressor engine | 2014-05-20 | N/A | DTE ENERGY | 1200 RPM | 5.37 lb NOx/hr | 856RPM | 2.58 lb/hr | 7E | Nitrogen Oxide | PASS | NA | Y | Fuel BTU Content 978. Average gas process rate for the plant on this date 3.54MMSCF/day.
2014 | 2428 | 0857103154 | PINNACLE GAS PRODUCERS LLC | 4220 PINNACLE RD | MORAINE | 45439 |  | Montgomery | B001 | 12 MMBtu/hour (1,626 bhp) pipeline quality gas/natural gas-fired compressor engine | 2014-05-20 | N/A | DTE ENERGY | 1200 RPM | 5.37 lb NOx/hr | 856 RPM | 2.58 lb/hr | 7E | Nitrogen Dioxide | PASS | NA | Y | Fuel BTU Content 978. Average gas process rate for the plant on this date 3.54MMSCF/day.
2015 | 107 | 0210012002 | Utica Gas Services, LLC-Carrollton Compressor Facility | 2098 Panda Road SE | Carrollton | 44615 |  | Carroll | P007 | 1,775 HP natural gas-fired Caterpillar G3606 engine #4 equipped with an oxidation catalyst | 2015-01-20 | Oxid. Cat.(Catalytic Converter): Oxidative Catalyst | Alliance Source Testing | 1775 HP | 1.96lbs/hr, 1.0g/hp-hr | 1599 HP | 1.05 lbs/hr, 0.3 g/hp-hr | 7E | Nitrogen Oxide | PP | NA | Y | Our facility descriptions have the engines numbered incorrectly, however the Manufacture dates correspond across both the report and permit. P013 is engine 3 onsite (10 in the permit), P006-P012 onsite are C4-C10, but in the permit 3-9. However if you follow only ***(EU P###)*** everything is accurate.
2015 | 109 | 0210012002 | Utica Gas Services, LLC-Carrollton Compressor Facility | 2098 Panda Road SE | Carrollton | 44615 |  | Carroll | P008 | 1,775 HP natural gas-fired Caterpillar G3606 engine #5 equipped with an oxidation catalyst | 2015-01-20 | Oxid. Cat.(Catalytic Converter): Oxidative Catalyst | Alliance Source Testing | 1775 HP | 1.96lbs/hr, 1.0g/hp-hr | 1602 HP | 1.25 lbs/hr, 0.4 g/hp-hr | 7E | Nitrogen Oxide | PP | NA | Y | Our facility descriptions have the engines numbered incorrectly, however the Manufacture dates correspond across both the report and permit. P013 is engine 3 onsite (10 in the permit), P006-P012 onsite are C4-C10, but in the permit 3-9. However if you follow only ***(EU P###)*** everything is accurate.
2015 | 112 | 0210012002 | Utica Gas Services, LLC-Carrollton Compressor Facility | 2098 Panda Road SE | Carrollton | 44615 |  | Carroll | P009 | 1,775 HP natural gas-fired Caterpillar G3606 engine #6 equipped with an oxidation catalyst | 2015-01-20 | Oxid. Cat.(Catalytic Converter): Oxidative Catalyst | Alliance Source Testing | 1775 HP | 1.96lbs/hr, 1.0g/hp-hr | 1656 HP | 1.26 lbs/hr, 0.4 g/hp-hr | 7E | Nitrogen Oxide | PP | NA | Y | Our facility descriptions have the engines numbered incorrectly, however the Manufacture dates correspond across both the report and permit. P013 is engine 3 onsite (10 in the permit), P006-P012 onsite are C4-C10, but in the permit 3-9. However if you follow only ***(EU P###)*** everything is accurate.
2015 | 222 | 0210002071 | Chesapeake Exploration LLC - Kennedy 14-13-5 Pad | OH-9 - Germano Rd | Harlem Springs | 43903 |  | Carroll | P002 | One or multiple stationary natural gas-fired spark ignition (SI) internal combustion engines (ICE) with a combined total horsepower (HP) of no more than 1,800 HP for the site.* Includes 2007 and later model year engines manufactured after the applicable effective date identified in 40 CFR 60.4230(a)(3); and engines manufactured before the effective date of the NSPS, where compliance with the Part 60 Subpart JJJJ emissions standards for the same size engine can be met by retrofitting the engine with a control device and demonstrated through stack testing. | 2015-08-11 | Catalyst | Alliance Source Testing | 630 Hp | 160 ppmvd @ 15% O2 | 422 Hp | 160 ppmvd @ 15% O2 | 7E | Nitrogen Dioxide | PP | NA | Y
2015 | 225 | 0210012002 | Utica Gas Services, LLC-Carrollton Compressor Facility | 2098 Panda Road SE | Carrollton | 44615 |  | Carroll | P004 | 1,775 HP natural gas-fired Caterpillar G3606 engine #1 equipped with an oxidation catalyst. | 2015-01-20 | Oxid. Cat.(Catalytic Converter): Oxidative Catalyst | Alliance Source Testing | 1775 HP | 1.96lbs/hr, 2.0g/hp-hr | 1686 HP | 1.10lbs/hr, 0.3 g/hp-hr | 7E | Nitrogen Oxide | PP | NA | Y | Our facility descriptions have the engines numbered incorrectly, however the Manufacture dates correspond across both the report and permit. P013 is engine 3 onsite (10 in the permit), P006-P012 onsite are C4-C10, but in the permit 3-9. However if you follow only ***(EU P###)*** everything is accurate.
2015 | 228 | 0210012002 | Utica Gas Services, LLC-Carrollton Compressor Facility | 2098 Panda Road SE | Carrollton | 44615 |  | Carroll | P005 | 1,775 HP natural gas-fired Caterpillar G3606 engine #2 equipped with an oxidation catalyst | 2015-01-20 | Oxid. Cat.(Catalytic Converter): Oxidative Catalyst | Alliance Source Testing | 1775 HP | 1.96lbs/hr, 2.0g/hp-hr | 1686 HP | 1.69lbs/hr, 0.5 g/hp-hr | 7E | Nitrogen Oxide | PP | NA | Y | Our facility descriptions have the engines numbered incorrectly, however the Manufacture dates correspond across both the report and permit. P013 is engine 3 onsite (10 in the permit), P006-P012 onsite are C4-C10, but in the permit 3-9. However if you follow only ***(EU P###)*** everything is accurate.
2015 | 230 | 0210012002 | Utica Gas Services, LLC-Carrollton Compressor Facility | 2098 Panda Road SE | Carrollton | 44615 |  | Carroll | P006 | 1,775 HP natural gas-fired Caterpillar G3606 engine #3 equipped with an oxidation catalyst | 2015-01-20 | Oxid. Cat.(Catalytic Converter): Oxidative Catalyst | Alliance Source Testing | 1775 HP | 1.96lbs/hr, 1.0g/hp-hr | 1597 HP | 1.90lbs/hr, 0.5 g/hp-hr | 7E | Nitrogen Oxide | PP | NA | Y | Our facility descriptions have the engines numbered incorrectly, however the Manufacture dates correspond across both the report and permit. P013 is engine 3 onsite (10 in the permit), P006-P012 onsite are C4-C10, but in the permit 3-9. However if you follow only ***(EU P###)*** everything is accurate.
2015 | 238 | 0210012002 | Utica Gas Services, LLC-Carrollton Compressor Facility | 2098 Panda Road SE | Carrollton | 44615 |  | Carroll | P010 | 1,775 HP natural gas-fired Caterpillar G3606 engine #7 equipped with an oxidation catalyst | 2015-01-20 | Oxid. Cat.(Catalytic Converter): Oxidative Catalyst | Alliance Source Testing | 1775 HP | 1.96lbs/hr, 1.0g/hp-hr | 1636 HP | 1.34 lbs/hr, 0.4 g/hp-hr | 7E | Nitrogen Oxide | PP | NA | Y | Our facility descriptions have the engines numbered incorrectly, however the Manufacture dates correspond across both the report and permit. P013 is engine 3 onsite (10 in the permit), P006-P012 onsite are C4-C10, but in the permit 3-9. However if you follow only ***(EU P###)*** everything is accurate.
2015 | 240 | 0210012002 | Utica Gas Services, LLC-Carrollton Compressor Facility | 2098 Panda Road SE | Carrollton | 44615 |  | Carroll | P011 | 1,775 HP natural gas-fired Caterpillar G3606 engine #8 equipped with an oxidation catalyst | 2015-01-20 | Oxid. Cat.(Catalytic Converter): Oxidative Catalyst | Alliance Source Testing | 1775 HP | 1.96lbs/hr, 1.0g/hp-hr | 1639 HP | 1.32 lbs/hr, 0.4 g/hp-hr | 7E | Nitrogen Oxide | PP | NA | Y | Our facility descriptions have the engines numbered incorrectly, however the Manufacture dates correspond across both the report and permit. P013 is engine 3 onsite (10 in the permit), P006-P012 onsite are C4-C10, but in the permit 3-9. However if you follow only ***(EU P###)*** everything is accurate.
2015 | 244 | 0210012002 | Utica Gas Services, LLC-Carrollton Compressor Facility | 2098 Panda Road SE | Carrollton | 44615 |  | Carroll | P012 | 1,775 HP natural gas-fired Caterpillar G3606 engine #9 equipped with an oxidation catalyst | 2015-01-20 | Oxid. Cat.(Catalytic Converter): Oxidative Catalyst | Alliance Source Testing | 1775 HP | 1.96lbs/hr, 1.0g/hp-hr | 1656 HP | 1.12lbs/hr, 0.3 g/hp-hr | 7E | Nitrogen Oxide | PP | NA | Y | Our facility descriptions have the engines numbered incorrectly, however the Manufacture dates correspond across both the report and permit. P013 is engine 3 onsite (10 in the permit), P006-P012 onsite are C4-C10, but in the permit 3-9. However if you follow only ***(EU P###)*** everything is accurate.
2015 | 247 | 0210012002 | Utica Gas Services, LLC-Carrollton Compressor Facility | 2098 Panda Road SE | Carrollton | 44615 |  | Carroll | P013 | 1,775 HP natural gas-fired Caterpillar G3606 engine #10equipped with an oxidation catalyst | 2015-01-20 | Oxid. Cat.(Catalytic Converter): Oxidative Catalyst | Alliance Source Testing | 1775 HP | 1.96lbs/hr, 1.0g/hp-hr | 1660 HP | 1.60 lbs/hr, 0.4 g/hp-hr | 7E | Nitrogen Oxide | PP | NA | Y | Our facility descriptions have the engines numbered incorrectly, however the Manufacture dates correspond across both the report and permit. P013 is engine 3 onsite (10 in the permit), P006-P012 onsite are C4-C10, but in the permit 3-9. However if you follow only ***(EU P###)*** everything is accurate.
2015 | 248 | 0210012002 | Utica Gas Services, LLC-Carrollton Compressor Facility | 2098 Panda Road SE | Carrollton | 44615 |  | Carroll | P004 | 1,775 HP natural gas-fired Caterpillar G3606 engine #1 equipped with an oxidation catalyst. | 2015-01-21 | Oxid. Cat.(Catalytic Converter): Oxidative Catalyst | Alliance Source Testing | 1775 HP | 1.96lbs/hr, 2.0g/hp-hr | 1686 HP | 1.10lbs/hr, 0.3 g/hp-hr | 7E | Nitrogen Oxide | PP | NA | Y | Our facility descriptions have the engines numbered incorrectly, however the Manufacture dates correspond across both the report and permit. P013 is engine 3 onsite (10 in the permit), P006-P012 onsite are C4-C10, but in the permit 3-9. However if you follow only ***(EU P###)*** everything is accurate.
2015 | 253 | 0210012002 | Utica Gas Services, LLC-Carrollton Compressor Facility | 2098 Panda Road SE | Carrollton | 44615 |  | Carroll | P005 | 1,775 HP natural gas-fired Caterpillar G3606 engine #2 equipped with an oxidation catalyst | 2015-01-21 | Oxid. Cat.(Catalytic Converter): Oxidative Catalyst | Alliance Source Testing | 1775 HP | 1.96lbs/hr, 2.0g/hp-hr | 1686 HP | 1.69lbs/hr, 0.5 g/hp-hr | 7E | Nitrogen Oxide | PP | NA | Y | Our facility descriptions have the engines numbered incorrectly, however the Manufacture dates correspond across both the report and permit. P013 is engine 3 onsite (10 in the permit), P006-P012 onsite are C4-C10, but in the permit 3-9. However if you follow only ***(EU P###)*** everything is accurate.
2015 | 254 | 0210012002 | Utica Gas Services, LLC-Carrollton Compressor Facility | 2098 Panda Road SE | Carrollton | 44615 |  | Carroll | P006 | 1,775 HP natural gas-fired Caterpillar G3606 engine #3 equipped with an oxidation catalyst | 2015-01-21 | Oxid. Cat.(Catalytic Converter): Oxidative Catalyst | Alliance Source Testing | 1775 HP | 1.96lbs/hr, 1.0g/hp-hr | 1597 HP | 1.90lbs/hr, 0.5 g/hp-hr | 7E | Nitrogen Oxide | PP | NA | Y | Our facility descriptions have the engines numbered incorrectly, however the Manufacture dates correspond across both the report and permit. P013 is engine 3 onsite (10 in the permit), P006-P012 onsite are C4-C10, but in the permit 3-9. However if you follow only ***(EU P###)*** everything is accurate.
2015 | 257 | 0210012002 | Utica Gas Services, LLC-Carrollton Compressor Facility | 2098 Panda Road SE | Carrollton | 44615 |  | Carroll | P007 | 1,775 HP natural gas-fired Caterpillar G3606 engine #4 equipped with an oxidation catalyst | 2015-01-21 | Oxid. Cat.(Catalytic Converter): Oxidative Catalyst | Alliance Source Testing | 1775 HP | 1.96lbs/hr, 1.0g/hp-hr | 1599 HP | 1.05 lbs/hr, 0.3 g/hp-hr | 7E | Nitrogen Oxide | PP | NA | Y | Our facility descriptions have the engines numbered incorrectly, however the Manufacture dates correspond across both the report and permit. P013 is engine 3 onsite (10 in the permit), P006-P012 onsite are C4-C10, but in the permit 3-9. However if you follow only ***(EU P###)*** everything is accurate.
2015 | 262 | 0210012002 | Utica Gas Services, LLC-Carrollton Compressor Facility | 2098 Panda Road SE | Carrollton | 44615 |  | Carroll | P008 | 1,775 HP natural gas-fired Caterpillar G3606 engine #5 equipped with an oxidation catalyst | 2015-01-21 | Oxid. Cat.(Catalytic Converter): Oxidative Catalyst | Alliance Source Testing | 1775 HP | 1.96lbs/hr, 1.0g/hp-hr | 1602 HP | 1.25 lbs/hr, 0.4 g/hp-hr | 7E | Nitrogen Oxide | PP | NA | Y | Our facility descriptions have the engines numbered incorrectly, however the Manufacture dates correspond across both the report and permit. P013 is engine 3 onsite (10 in the permit), P006-P012 onsite are C4-C10, but in the permit 3-9. However if you follow only ***(EU P###)*** everything is accurate.
2015 | 265 | 0210012002 | Utica Gas Services, LLC-Carrollton Compressor Facility | 2098 Panda Road SE | Carrollton | 44615 |  | Carroll | P009 | 1,775 HP natural gas-fired Caterpillar G3606 engine #6 equipped with an oxidation catalyst | 2015-01-21 | Oxid. Cat.(Catalytic Converter): Oxidative Catalyst | Alliance Source Testing | 1775 HP | 1.96lbs/hr, 1.0g/hp-hr | 1656 HP | 1.26 lbs/hr, 0.4 g/hp-hr | 7E | Nitrogen Oxide | PP | NA | Y | Our facility descriptions have the engines numbered incorrectly, however the Manufacture dates correspond across both the report and permit. P013 is engine 3 onsite (10 in the permit), P006-P012 onsite are C4-C10, but in the permit 3-9. However if you follow only ***(EU P###)*** everything is accurate.
2015 | 267 | 0210012002 | Utica Gas Services, LLC-Carrollton Compressor Facility | 2098 Panda Road SE | Carrollton | 44615 |  | Carroll | P010 | 1,775 HP natural gas-fired Caterpillar G3606 engine #7 equipped with an oxidation catalyst | 2015-01-21 | Oxid. Cat.(Catalytic Converter): Oxidative Catalyst | Alliance Source Testing | 1775 HP | 1.96lbs/hr, 1.0g/hp-hr | 1636 HP | 1.34 lbs/hr, 0.4 g/hp-hr | 7E | Nitrogen Oxide | PP | NA | Y | Our facility descriptions have the engines numbered incorrectly, however the Manufacture dates correspond across both the report and permit. P013 is engine 3 onsite (10 in the permit), P006-P012 onsite are C4-C10, but in the permit 3-9. However if you follow only ***(EU P###)*** everything is accurate.
2015 | 270 | 0210012002 | Utica Gas Services, LLC-Carrollton Compressor Facility | 2098 Panda Road SE | Carrollton | 44615 |  | Carroll | P011 | 1,775 HP natural gas-fired Caterpillar G3606 engine #8 equipped with an oxidation catalyst | 2015-01-21 | Oxid. Cat.(Catalytic Converter): Oxidative Catalyst | Alliance Source Testing | 1775 HP | 1.96lbs/hr, 1.0g/hp-hr | 1639 HP | 1.32 lbs/hr, 0.4 g/hp-hr | 7E | Nitrogen Oxide | PP | NA | Y | Our facility descriptions have the engines numbered incorrectly, however the Manufacture dates correspond across both the report and permit. P013 is engine 3 onsite (10 in the permit), P006-P012 onsite are C4-C10, but in the permit 3-9. However if you follow only ***(EU P###)*** everything is accurate.
2015 | 273 | 0210012002 | Utica Gas Services, LLC-Carrollton Compressor Facility | 2098 Panda Road SE | Carrollton | 44615 |  | Carroll | P012 | 1,775 HP natural gas-fired Caterpillar G3606 engine #9 equipped with an oxidation catalyst | 2015-01-21 | Oxid. Cat.(Catalytic Converter): Oxidative Catalyst | Alliance Source Testing | 1775 HP | 1.96lbs/hr, 1.0g/hp-hr | 1656 HP | 1.12lbs/hr, 0.3 g/hp-hr | 7E | Nitrogen Oxide | PP | NA | Y | Our facility descriptions have the engines numbered incorrectly, however the Manufacture dates correspond across both the report and permit. P013 is engine 3 onsite (10 in the permit), P006-P012 onsite are C4-C10, but in the permit 3-9. However if you follow only ***(EU P###)*** everything is accurate.
2015 | 277 | 0210012002 | Utica Gas Services, LLC-Carrollton Compressor Facility | 2098 Panda Road SE | Carrollton | 44615 |  | Carroll | P013 | 1,775 HP natural gas-fired Caterpillar G3606 engine #10equipped with an oxidation catalyst | 2015-01-21 | Oxid. Cat.(Catalytic Converter): Oxidative Catalyst | Alliance Source Testing | 1775 HP | 1.96lbs/hr, 1.0g/hp-hr | 1660 HP | 1.60 lbs/hr, 0.4 g/hp-hr | 7E | Nitrogen Oxide | PP | NA | Y | Our facility descriptions have the engines numbered incorrectly, however the Manufacture dates correspond across both the report and permit. P013 is engine 3 onsite (10 in the permit), P006-P012 onsite are C4-C10, but in the permit 3-9. However if you follow only ***(EU P###)*** everything is accurate.
2015 | 279 | 0210012002 | Utica Gas Services, LLC-Carrollton Compressor Facility | 2098 Panda Road SE | Carrollton | 44615 |  | Carroll | P004 | 1,775 HP natural gas-fired Caterpillar G3606 engine #1 equipped with an oxidation catalyst. | 2015-01-22 | Oxid. Cat.(Catalytic Converter): Oxidative Catalyst | Alliance Source Testing | 1775 HP | 1.96lbs/hr, 2.0g/hp-hr | 1686 HP | 1.10lbs/hr, 0.3 g/hp-hr | 7E | Nitrogen Oxide | PP | NA | Y | Our facility descriptions have the engines numbered incorrectly, however the Manufacture dates correspond across both the report and permit. P013 is engine 3 onsite (10 in the permit), P006-P012 onsite are C4-C10, but in the permit 3-9. However if you follow only ***(EU P###)*** everything is accurate.
2015 | 281 | 0210012002 | Utica Gas Services, LLC-Carrollton Compressor Facility | 2098 Panda Road SE | Carrollton | 44615 |  | Carroll | P005 | 1,775 HP natural gas-fired Caterpillar G3606 engine #2 equipped with an oxidation catalyst | 2015-01-22 | Oxid. Cat.(Catalytic Converter): Oxidative Catalyst | Alliance Source Testing | 1775 HP | 1.96lbs/hr, 2.0g/hp-hr | 1686 HP | 1.69lbs/hr, 0.5 g/hp-hr | 7E | Nitrogen Oxide | PP | NA | Y | Our facility descriptions have the engines numbered incorrectly, however the Manufacture dates correspond across both the report and permit. P013 is engine 3 onsite (10 in the permit), P006-P012 onsite are C4-C10, but in the permit 3-9. However if you follow only ***(EU P###)*** everything is accurate.
2015 | 285 | 0210012002 | Utica Gas Services, LLC-Carrollton Compressor Facility | 2098 Panda Road SE | Carrollton | 44615 |  | Carroll | P006 | 1,775 HP natural gas-fired Caterpillar G3606 engine #3 equipped with an oxidation catalyst | 2015-01-22 | Oxid. Cat.(Catalytic Converter): Oxidative Catalyst | Alliance Source Testing | 1775 HP | 1.96lbs/hr, 1.0g/hp-hr | 1597 HP | 1.90lbs/hr, 0.5 g/hp-hr | 7E | Nitrogen Oxide | PP | NA | Y | Our facility descriptions have the engines numbered incorrectly, however the Manufacture dates correspond across both the report and permit. P013 is engine 3 onsite (10 in the permit), P006-P012 onsite are C4-C10, but in the permit 3-9. However if you follow only ***(EU P###)*** everything is accurate.
2015 | 289 | 0210012002 | Utica Gas Services, LLC-Carrollton Compressor Facility | 2098 Panda Road SE | Carrollton | 44615 |  | Carroll | P007 | 1,775 HP natural gas-fired Caterpillar G3606 engine #4 equipped with an oxidation catalyst | 2015-01-22 | Oxid. Cat.(Catalytic Converter): Oxidative Catalyst | Alliance Source Testing | 1775 HP | 1.96lbs/hr, 1.0g/hp-hr | 1599 HP | 1.05 lbs/hr, 0.3 g/hp-hr | 7E | Nitrogen Oxide | PP | NA | Y | Our facility descriptions have the engines numbered incorrectly, however the Manufacture dates correspond across both the report and permit. P013 is engine 3 onsite (10 in the permit), P006-P012 onsite are C4-C10, but in the permit 3-9. However if you follow only ***(EU P###)*** everything is accurate.
2015 | 290 | 0210012002 | Utica Gas Services, LLC-Carrollton Compressor Facility | 2098 Panda Road SE | Carrollton | 44615 |  | Carroll | P008 | 1,775 HP natural gas-fired Caterpillar G3606 engine #5 equipped with an oxidation catalyst | 2015-01-22 | Oxid. Cat.(Catalytic Converter): Oxidative Catalyst | Alliance Source Testing | 1775 HP | 1.96lbs/hr, 1.0g/hp-hr | 1602 HP | 1.25 lbs/hr, 0.4 g/hp-hr | 7E | Nitrogen Oxide | PP | NA | Y | Our facility descriptions have the engines numbered incorrectly, however the Manufacture dates correspond across both the report and permit. P013 is engine 3 onsite (10 in the permit), P006-P012 onsite are C4-C10, but in the permit 3-9. However if you follow only ***(EU P###)*** everything is accurate.
2015 | 295 | 0210012002 | Utica Gas Services, LLC-Carrollton Compressor Facility | 2098 Panda Road SE | Carrollton | 44615 |  | Carroll | P009 | 1,775 HP natural gas-fired Caterpillar G3606 engine #6 equipped with an oxidation catalyst | 2015-01-22 | Oxid. Cat.(Catalytic Converter): Oxidative Catalyst | Alliance Source Testing | 1775 HP | 1.96lbs/hr, 1.0g/hp-hr | 1656 HP | 1.26 lbs/hr, 0.4 g/hp-hr | 7E | Nitrogen Oxide | PP | NA | Y | Our facility descriptions have the engines numbered incorrectly, however the Manufacture dates correspond across both the report and permit. P013 is engine 3 onsite (10 in the permit), P006-P012 onsite are C4-C10, but in the permit 3-9. However if you follow only ***(EU P###)*** everything is accurate.
2015 | 298 | 0210012002 | Utica Gas Services, LLC-Carrollton Compressor Facility | 2098 Panda Road SE | Carrollton | 44615 |  | Carroll | P010 | 1,775 HP natural gas-fired Caterpillar G3606 engine #7 equipped with an oxidation catalyst | 2015-01-22 | Oxid. Cat.(Catalytic Converter): Oxidative Catalyst | Alliance Source Testing | 1775 HP | 1.96lbs/hr, 1.0g/hp-hr | 1636 HP | 1.34 lbs/hr, 0.4 g/hp-hr | 7E | Nitrogen Oxide | PP | NA | Y | Our facility descriptions have the engines numbered incorrectly, however the Manufacture dates correspond across both the report and permit. P013 is engine 3 onsite (10 in the permit), P006-P012 onsite are C4-C10, but in the permit 3-9. However if you follow only ***(EU P###)*** everything is accurate.
2015 | 299 | 0210012002 | Utica Gas Services, LLC-Carrollton Compressor Facility | 2098 Panda Road SE | Carrollton | 44615 |  | Carroll | P011 | 1,775 HP natural gas-fired Caterpillar G3606 engine #8 equipped with an oxidation catalyst | 2015-01-22 | Oxid. Cat.(Catalytic Converter): Oxidative Catalyst | Alliance Source Testing | 1775 HP | 1.96lbs/hr, 1.0g/hp-hr | 1639 HP | 1.32 lbs/hr, 0.4 g/hp-hr | 7E | Nitrogen Oxide | PP | NA | Y | Our facility descriptions have the engines numbered incorrectly, however the Manufacture dates correspond across both the report and permit. P013 is engine 3 onsite (10 in the permit), P006-P012 onsite are C4-C10, but in the permit 3-9. However if you follow only ***(EU P###)*** everything is accurate.
2015 | 304 | 0210012002 | Utica Gas Services, LLC-Carrollton Compressor Facility | 2098 Panda Road SE | Carrollton | 44615 |  | Carroll | P012 | 1,775 HP natural gas-fired Caterpillar G3606 engine #9 equipped with an oxidation catalyst | 2015-01-22 | Oxid. Cat.(Catalytic Converter): Oxidative Catalyst | Alliance Source Testing | 1775 HP | 1.96lbs/hr, 1.0g/hp-hr | 1656 HP | 1.12lbs/hr, 0.3 g/hp-hr | 7E | Nitrogen Oxide | PP | NA | Y | Our facility descriptions have the engines numbered incorrectly, however the Manufacture dates correspond across both the report and permit. P013 is engine 3 onsite (10 in the permit), P006-P012 onsite are C4-C10, but in the permit 3-9. However if you follow only ***(EU P###)*** everything is accurate.
2015 | 305 | 0210012002 | Utica Gas Services, LLC-Carrollton Compressor Facility | 2098 Panda Road SE | Carrollton | 44615 |  | Carroll | P013 | 1,775 HP natural gas-fired Caterpillar G3606 engine #10equipped with an oxidation catalyst | 2015-01-22 | Oxid. Cat.(Catalytic Converter): Oxidative Catalyst | Alliance Source Testing | 1775 HP | 1.96lbs/hr, 1.0g/hp-hr | 1660 HP | 1.60 lbs/hr, 0.4 g/hp-hr | 7E | Nitrogen Oxide | PP | NA | Y | Our facility descriptions have the engines numbered incorrectly, however the Manufacture dates correspond across both the report and permit. P013 is engine 3 onsite (10 in the permit), P006-P012 onsite are C4-C10, but in the permit 3-9. However if you follow only ***(EU P###)*** everything is accurate.
2015 | 308 | 0210012046 | Chesapeake Exploration LLC - Bauer 14-14-6 Pad | Autumn Road SW | Carrollton | 44615 |  | Carroll | P002 | Natural Gas Engines | 2015-04-28 | Catalyst | Alliance Source Testing, Inc. | 211 Hp | 82 ppmvd@ 15 % O2 | 194 Hp or 91.9% | 6.3 ppmvd@ 15 % O2 | 7E | Nitrogen Dioxide | PP | NA | Y
2015 | 440 | 0250092002 | City of Struthers WWTP | 530 Lowellville Road | Struthers | 44471 |  | Mahoning | P001 | Stationary internal combustion engine | 2015-03-11 | Catalyst | Custom Stack Analysis | 585 hp as permitted | 3.0 g/hp-hr & 220 ppm @ 15% O2 | 271 hp | 0.79 g & 37.38 ppm | 7E | Nitrogen Dioxide | PP | NA | Y
2015 | 444 | 0250092002 | City of Struthers WWTP | 530 Lowellville Road | Struthers | 44471 |  | Mahoning | P002 | Waukesha H24GLD Engine | 2015-03-11 | Catalyst | Custom Stack Analysis | 585 hp as permitted | 3.0 g/hp-hr & 220 ppm @ 15% O2 | 264 hp | 1.02 g & 50.84 ppm | 7E | Nitrogen Dioxide | PP | NA | Y
2015 | 445 | 0250092002 | City of Struthers WWTP | 530 Lowellville Road | Struthers | 44471 |  | Mahoning | P001 | Stationary internal combustion engine | 2015-03-12 | Catalyst | Custom Stack Analysis | 585 hp as permitted | 3.0 g/hp-hr & 220 ppm @ 15% O2 | 271 hp | 0.79 g & 37.38 ppm | 7E | Nitrogen Dioxide | PP | NA | Y
2015 | 448 | 0634005033 | Harrison West Compressor Station | Possum Hollow Road | Freeport | 43973 |  | Harrison | P005 | Compressor Engine #5 - 1980 HP (15.43 MMBtu/hr) Waukesha P9390 - natural gas-fired four-stroke rich burn internal combustion engine equipped with a three-way oxidation catalyst controlling CH2O, CO, NOx, & VOCs by 80, 97, 98.5 & 66 percent respectively | 2015-05-27 | CC005(Catalytic Converter): Compressor Engine #5 - 3-way Catalyst | Air Hygiene International, Inc. | 1980 hp | 1.0 g/hp-hr | 1650 hp | 0.06 g/hp-hr | 7E | Nitrogen Dioxide | PP | NA | Y
2015 | 449 | 0634005033 | Harrison West Compressor Station | Possum Hollow Road | Freeport | 43973 |  | Harrison | P006 | Compressor Engine #6 - 1980 HP (15.43 MMBtu/hr) Waukesha P9390 - natural gas-fired four-stroke rich burn internal combustion engine equipped with a three-way oxidation catalyst controlling CH2O, CO, NOx, & VOCs by 80, 97, 98.5 & 66 percent respectively | 2015-05-28 | CC006(Catalytic Converter): Compressor Engine #6 - 3-way Catalyst | Air Hygiene International, Inc. | 1980 hp | 1.0 g/hp-hr | 1573 hp | 0.13 g/hp-hr | 7E | Nitrogen Dioxide | PP | NA | Y
2015 | 453 | 0634005033 | Harrison West Compressor Station | Possum Hollow Road | Freeport | 43973 |  | Harrison | P007 | Compressor Engine #7 - 1980 HP (15.43 MMBtu/hr) Waukesha P9390 - natural gas-fired four-stroke rich burn internal combustion engine equipped with a three-way oxidation catalyst controlling CH2O, CO, NOx, & VOCs by 80, 97, 98.5 & 66 percent respectively | 2015-05-28 | CC007(Catalytic Converter): Compressor Engine #7 - 3-way Catalyst | Air Hygiene International, Inc. | 1980 hp | 1.0 g/hp-hr | 1586 hp | 0.11 g/hp-hr | 7E | Nitrogen Dioxide | PP | NA | Y
2015 | 456 | 0661005020 | Rockies Express Pipeline - Seneca Compressor Station | Seneca Lake Rd | Quaker City | 43773 |  | Noble | P005 | compressor engine | 2015-05-18 | Engine 5(Catalytic Converter): Compressor Engine 5 Catalytic Convertor; Engine 4(Catalytic Converter): Compressor Engine 4 Catalytic Convertor; | Compressor Engineering Cort. | 5000 hp | 0.50 g/hp-hr | 4761 hp | 0.3658 g/hp-hr | 7E | Nitrogen Dioxide | PP | NA | Y
2015 | 458 | 0661005020 | Rockies Express Pipeline - Seneca Compressor Station | Seneca Lake Rd | Quaker City | 43773 |  | Noble | P003 | compressor engine 3 | 2015-05-19 | Engine 3(Catalytic Converter): Compressor Engine 1 catalytic converter | Compressor Engineering Cort. | 2250 hp | 1.0 g/hp-hr | 2212 hp | 0.1609 g/hp-hr | 7E | Nitrogen Dioxide | PP | NA | Y
2015 | 477 | 0250092002 | City of Struthers WWTP | 530 Lowellville Road | Struthers | 44471 |  | Mahoning | P002 | Waukesha H24GLD Engine | 2015-03-12 | Catalyst | Custom Stack Analysis | 585 hp as permitted | 3.0 g/hp-hr & 220 ppm @ 15% O2 | 264 hp | 1.02 g & 50.84 ppm | 7E | Nitrogen Dioxide | PP | NA | Y
2015 | 529 | 0285000366 | East Ohio Gas - Chippewa Station | 17045 Galehouse Road | Doylestown | 44230 |  | Wayne | B010 | 2,370 hp 4SLB SI ICE; CAT G3608 | 2015-05-20 | Engine 5 Converter(Catalytic Converter): Engine #5; Cat B010(Catalytic Converter): Catalytic Converter for B010, engine #6; Catalytic(Catalytic Converter): Engine 7 Catalytic converter | Environmental Quality Management | 2370 HP | 2.0 g/hp-hr 160 ppmdv @ 15% O2 | 2225 Hp | 0.71 g/hp-hr 83.4 ppmdv @ 15% O2 | 7E | Nitrogen Dioxide | PP | NA | Y | B009-2.5 Catalyst Pressure and 880 degF Catalyst temp, B010-3.0 Catalyst Pressure and 880 degF Catalyst temp, B014-1.0 Catalyst Pressure and 870 degF Catalyst Temperature
2015 | 530 | 0285000366 | East Ohio Gas - Chippewa Station | 17045 Galehouse Road | Doylestown | 44230 |  | Wayne | B014 | 2,370 hp 4SLB SI ICE: CAT 3608 w/catalyst | 2015-05-20 | Engine 5 Converter(Catalytic Converter): Engine #5; Cat B010(Catalytic Converter): Catalytic Converter for B010, engine #6; Catalytic(Catalytic Converter): Engine 7 Catalytic converter | Environmental Quality Management | 2370 Hp | 1.0 g/hp-hr 82 ppmdv @ 15% O2 | 2241 Hp | 0.40 g/hp-hr 32.7 ppmdv @ 15% O2 | 7E | Nitrogen Dioxide | PP | NA | Y | B009-2.5 Catalyst Pressure and 880 degF Catalyst temp, B010-3.0 Catalyst Pressure and 880 degF Catalyst temp, B014-1.0 Catalyst Pressure and 870 degF Catalyst Temperature
2015 | 537 | 0285000388 | East Ohio Gas Company - Paint | STATE RTE 250 | Wooster | 44624 |  | Wayne | B002 | Natural gas fired Internal Combustion Engine with max input capacity of 11.9 MMBtu/hr - Caterpillar G3516TALE with 1340 HP, 4-stroke, selective catalytic reduction (SCR) | 2015-07-14 | Three way Catalyst; CatOx(Catalytic Converter): Catalytic oxidizer for Engine 2 | Environmental Quality Management | 1340 Hp | 160 ppm @ 15% O2 and 2.0 g/hp-hr | 1236 HP or 92.2 | 98.8 ppm @ 15% O2 and 1.233 g/hp-hr | 7E | Nitrogen Oxide | PP | NA | Y
2015 | 693 | 0607005016 | Barnesville West Compressor Station | Hwy 801 | Warren Twp. | 43713 |  | Belmont | P006 | Compressor Engine #1 - Natural gas-fired four-stroke lean burn (4SLB) internal combustion engine rated at an operating capacity of 2,370 horsepower (hp) and equipped with an oxidation catalyst | 2015-03-25 | CC001(Catalytic Converter): Compressor Engine #1 Catalytic Converter | Air Hygiene Internatinal, Inc | 2370 hp | 0.5 g/hp-hr | 2179 hp | 0.39 g/hp-hr | 7E | Nitrogen Dioxide | PP | NA | Y
2015 | 696 | 0607005016 | Barnesville West Compressor Station | Hwy 801 | Warren Twp. | 43713 |  | Belmont | P007 | Compressor Engine #1 - Natural gas-fired four-stroke lean burn (4SLB) internal combustion engine rated at an operating capacity of 2,370 horsepower (hp) and equipped with an oxidation catalyst | 2015-03-25 | CC002(Catalytic Converter): Compressor Engine #2 Catalytic Converter | Air Hygiene International, Inc | 2,370 hp | 0.5 g/hp-hr | 2,199 hp | 0.29 g/hp-hr | 7E | Nitrogen Dioxide | PP | NA | Y
2015 | 700 | 0607005016 | Barnesville West Compressor Station | Hwy 801 | Warren Twp. | 43713 |  | Belmont | P008 | Compressor Engine #3 - Natural gas-fired four-stroke lean burn (4SLB) internal combustion engine rated at an operating capacity of 2,370 horsepower (hp) and equipped with an oxidation catalyst | 2015-03-26 | CC003(Catalytic Converter): Compressor Engine #3 Catalytic Converter | Air Hygiene International, Inc | 2,370 hp | 0.5 g/hp-hr | 2,174 hp | 0.38 g/hp-hr | 7E | Nitrogen Dioxide | PP | NA | Y
2015 | 703 | 0607005016 | Barnesville West Compressor Station | Hwy 801 | Warren Twp. | 43713 |  | Belmont | P009 | Compressor Engine #4 - Natural gas-fired four-stroke lean burn (4SLB) internal combustion engine rated at an operating capacity of 2,370 horsepower (hp) and equipped with an oxidation catalyst | 2015-03-26 | CC004(Catalytic Converter): Compressor Engine #4 Catalytic Converter | Air Hygiene International, Inc | 2,370 hp | 0.50 g/hp-hr | 2,188 hp | 0.36 g/hp-hr | 7E | Nitrogen Dioxide | PP | NA | Y
2015 | 704 | 0607005016 | Barnesville West Compressor Station | Hwy 801 | Warren Twp. | 43713 |  | Belmont | P010 | Compressor Engine #5 - Natural gas-fired four-stroke lean burn (4SLB) internal combustion engine rated at an operating capacity of 2,370 horsepower (hp) and equipped with an oxidation catalyst | 2015-03-27 | CC005(Catalytic Converter): Compressor Engine #5 Catalytic Converter | Air Hygiene International, Inc | 2,370 hp | 0.5 g/hp-hr | 2,204 hp | 0.27 g/hp-hr | 7E | Nitrogen Dioxide | PP | NA | Y
2015 | 708 | 0607005016 | Barnesville West Compressor Station | Hwy 801 | Warren Twp. | 43713 |  | Belmont | P011 | Compressor Engine #6 - Natural gas-fired four-stroke lean burn (4SLB) internal combustion engine rated at an operating capacity of 2,370 horsepower (hp) and equipped with an oxidation catalyst | 2015-03-27 | CC006(Catalytic Converter): Compressor Engine #6 Catalytic Converter | Air Hygiene International, Inc | 2,370 hp | 0.5 g/hp-hr | 2,309 | 0.26 g/hp-hr | 7E | Nitrogen Dioxide | PP | NA | Y
2015 | 711 | 0607015003 | Gulfport Energy- Shugert 12 Well Pad | 65800 Mt. Olivett Road | Barnesville | 43713 |  | Belmont | P002 | One or multiple stationary natural gas-fired spark ignition (SI) internal combustion engines (ICE) with a combined total horsepower (HP) of no more than 1,800 HP for the site. | 2015-06-25 | none | Great Plains Services | 118 hp | 2.0 g/hp-hr | 91 hp | 0.457 g/hp-hr | 6348 03 | NOx - Nitrogen Oxides | PP | NA | Y
2015 | 713 | 0607015007 | Humphreys Compressor Station | Johnson Ridge Rd | Barnesville | 43713 |  | Belmont | P001 | Compressor Engine #1 - Caterpillar G3612TA - natural gas fired four-stroke, lean burn internal combustion engine rated at an operating capacity of 3,550 horsepower equipped with a double oxidation catalyst. | 2015-04-14 | CC001(Catalytic Converter): Compressor Engine #1 - Oxidation Catalyst | Air Hygiene, Inc. | 3550 hp | 1.0 g/hp-hr | 3290 hp | 0.36 g/hp-hr | 7E | Nitrogen Dioxide | PP | NA | Y
2015 | 716 | 0607015007 | Humphreys Compressor Station | Johnson Ridge Rd | Barnesville | 43713 |  | Belmont | P002 | Compressor Engine #1 - Caterpillar G3612TA - natural gas fired four-stroke, lean burn internal combustion engine rated at an operating capacity of 3,550 horsepower equipped with a double oxidation catalyst. | 2015-04-14 | CC002(Catalytic Converter): Compressor Engine #2 - Oxidation Catalyst | Air Hygiene, Inc. | 3550 hp | 1.0 g/hp-hr | 3307 hp | 0.30 g/hp-hr | 7E | Nitrogen Dioxide | PP | NA | Y
2015 | 721 | 0607015007 | Humphreys Compressor Station | Johnson Ridge Rd | Barnesville | 43713 |  | Belmont | P003 | Compressor Engine #1 - Caterpillar G3612TA - natural gas fired four-stroke, lean burn internal combustion engine rated at an operating capacity of 3,550 horsepower equipped with a double oxidation catalyst. | 2015-04-15 | CC003(Catalytic Converter): Compressor Engine #3 - Oxidation Catalyst | Air Hygiene, Inc. | 3550 hp | 1.0 g/hp-hr | 3294 hp | 0.32 g/hp-hr | 7E | Nitrogen Dioxide | PP | NA | Y
2015 | 741 | 0630005042 | Gulfport Energy - Miller Well Pad | Jasper Rd | Londonderry Twp. | 43973 |  | Guernsey | P002 | One 50-hp Zenith ZPP416 and one 203-hp Caterpillar G3306B NA natural gas-fired engines for compressors. One or multiple stationary natural gas-fired spark ignition (SI) internal combustion engines (ICE) wiht a combined total horsepower (HP) or no more than 1,800 HP for the site. | 2015-06-26 | catalyst | Great Plains Analytical Services | 118 hp | 2.0 g/hp-hr | 87 hp | 0.139 g/hp-hr | 6348 03 | NOx - Nitrogen Oxides | PP | NA | N
2015 | 743 | 0630005042 | Gulfport Energy - Miller Well Pad | Jasper Rd | Londonderry Twp. | 43973 |  | Guernsey | P002 | One 50-hp Zenith ZPP416 and one 203-hp Caterpillar G3306B NA natural gas-fired engines for compressors. One or multiple stationary natural gas-fired spark ignition (SI) internal combustion engines (ICE) wiht a combined total horsepower (HP) or no more than 1,800 HP for the site. | 2015-06-27 | catalyst | Great Plains Analytical Services | 118 hp | 2.0 g/hp-hr | 85 hp | 0.344 g/hp-hr | 6348 03 | NOx - Nitrogen Oxides | PP | NA | N | test date was actually 6-26-2015. To input data for engines that share a P002 number you have to change date or something. If I use 6-26-2015 information will not be accepted because these two engine both are P002 unit numbers-tow engines with hp of less than 1800 hp for site
2015 | 745 | 0630005043 | Gulfport Energy - Ripley Well Pad | Shipley Rd | Londonderry Twp. | 43973 |  | Guernsey | P002 | One 50-hp Zenith ZPP416 and one 203-hp Caterpillar G3306B NA natural gas-fired engines for compressors. One or multiple stationary natural gas-fired spark ignition (SI) internal combustion engines (ICE) wiht a combined total horsepower (HP) or no more than 1,800 HP for the site. | 2015-03-20 | NSCR | Great Plains Analytical Services | 118 hp | 2.0 g/hp-hr | 118 hp | 0.057 g/hp-hr | 6348 03 | NOx - Nitrogen Oxides | PP | NA | Y
2015 | 755 | 0634005027 | Arrowhead Compressor Station | E of Clements Rd and S of Jockey Hollow | Athens Twp. | 43977 |  | Harrison | P006 | Compressor Engine #3 - Caterpillar G3608 - natural gas fired four-stroke, lean burn internal combustion engine rated at an operating capacity of 2,370 horsepower equipped with a catalytic convertor. | 2015-04-13 | CC003(Catalytic Converter): Compressor Engine #3 Catalytic Convertor; CC004(Catalytic Converter): Compressor Engine #4 Catalytic Convertor | Air Hygiene, Inc. | 2370 Hp | 0.5 g/hp-hr | 2223 hp | 0.36 g/hp-hr | 7E | Nitrogen Dioxide | PP | NA | Y
2015 | 758 | 0634005027 | Arrowhead Compressor Station | E of Clements Rd and S of Jockey Hollow | Athens Twp. | 43977 |  | Harrison | P007 | Compressor Engine #4 - Caterpillar G3608 - natural gas fired four-stroke, lean burn internal combustion engine rated at an operating capacity of 2,370 horsepower equipped with a catalytic convertor | 2015-04-13 | CC003(Catalytic Converter): Compressor Engine #3 Catalytic Convertor; CC004(Catalytic Converter): Compressor Engine #4 Catalytic Convertor | Air Hygiene, Inc. | 2370 hp | 0.5 g/hp-hr | 2180 hp | 0.30 g/hp-hr | 7E | Nitrogen Dioxide | PP | NA | Y
2015 | 762 | 0634005033 | Harrison West Compressor Station | Possum Hollow Road | Freeport | 43973 |  | Harrison | P001 | Compressor Engine #1 - 1480 HP (11.39 MMBtu/hr) Waukesha L7042 - natural gas-fired four-stroke rich burn internal combustion engine equipped with a three-way oxidation catalyst controlling CH2O, CO, NOx, & VOCs by 80, 97, 98.5 & 66 percent respectively | 2015-05-26 | CC001(Catalytic Converter): Compressor Engine #1 - 3-way Catalyst | Air Hygiene International, Inc. | 1480 hp | 1.0 g/hp-hr | 1165 hp | 0.16 g/hp-hr | 7E | Nitrogen Dioxide | PP | NA | Y
2015 | 763 | 0634005033 | Harrison West Compressor Station | Possum Hollow Road | Freeport | 43973 |  | Harrison | P003 | Compressor Engine #3 - 1980 HP (15.43 MMBtu/hr) Waukesha P9390 - natural gas-fired four-stroke rich burn internal combustion engine equipped with a three-way oxidation catalyst controlling CH2O, CO, NOx, & VOCs by 80, 97, 98.5 & 66 percent respectively | 2015-05-26 | CC003(Catalytic Converter): Compressor Engine #3 - 3-way Catalyst | Air Hygiene International, Inc. | 1980 hp | 1.0 g/hp-hr | 1661 hp | 0.08 g/hp-hr | 7E | Nitrogen Dioxide | PP | NA | Y
2015 | 768 | 0634005033 | Harrison West Compressor Station | Possum Hollow Road | Freeport | 43973 |  | Harrison | P004 | Compressor Engine #4 - 1980 HP (15.43 MMBtu/hr) Waukesha P9390 - natural gas-fired four-stroke rich burn internal combustion engine equipped with a three-way oxidation catalyst controlling CH2O, CO, NOx, & VOCs by 80, 97, 98.5 & 66 percent respectively | 2015-05-27 | CC004(Catalytic Converter): Compressor Engine #4 - 3-way Catalyst | Air Hygiene International, Inc. | 1980 hp | 1.0 g/hp--hr | 1636 hp | 0.03 g/hp-hr | 7E | Nitrogen Dioxide | PP | NA | Y
2015 | 771 | 0634005034 | Lake Compressor Station | County Highway 21 | Freeport | 43973 |  | Harrison | P001 | Compressor Engine #1 - 1480 HP (11.39 MMBtu/hr) Waukesha L7042 - natural gas-fired four-stroke rich burn internal combustion engine equipped with a three-way oxidation catalyst controlling CH2O, CO, NOx, & VOCs by 80, 97, 98.5 & 66 percent respectively | 2015-04-16 | CC001(Catalytic Converter): Compressor Engine #1 - 3-way Catalyst | Air Hygiene, Inc. | 1480 hp | 1.0 g/hp-hr | 1207 hp | 0.11 g/hp-hr | 7E | Nitrogen Dioxide | PP | NA | Y
2015 | 774 | 0634005034 | Lake Compressor Station | County Highway 21 | Freeport | 43973 |  | Harrison | P005 | Compressor Engine #5 - 1980 HP (15.43 MMBtu/hr) Waukesha P9390 - natural gas-fired four-stroke rich burn internal combustion engine equipped with a three-way oxidation catalyst controlling CH2O, CO, NOx, & VOCs by 80, 97, 98.5 & 66 percent respectively | 2015-04-16 | CC005(Catalytic Converter): Compressor Engine #5 - 3-way Catalyst; CC005(Catalytic Converter): Compressor Engine #5 - 3-way Catalyst | Air Hygiene, Inc. | 1980 hp | 1.0 g/hp-hr | 1617 hp | 0.05 g/hp-hr | 7E | Nitrogen Dioxide | PP | NA | Y
2015 | 779 | 0634005034 | Lake Compressor Station | County Highway 21 | Freeport | 43973 |  | Harrison | P011 | Compressor Engine #9 - Waukesha L7042 - natural gas fired four-stroke, rich burn internal combustion engine rated at an operating capacity of 1,480 horsepower equipped with a three-way oxidation catalyst. | 2015-04-16 | CC011(Catalytic Converter): Compressor Engine #9 - 3-way Catalyst | Air Hygiene, Inc. | 1480 hp | 1.0 g/hp-hr | 1166 hp | 0.12 g/hp-hr | 7E | Nitrogen Dioxide | PP | NA | Y
2015 | 780 | 0634005034 | Lake Compressor Station | County Highway 21 | Freeport | 43973 |  | Harrison | P002 | Compressor Engine #2 - 1480 HP (11.39 MMBtu/hr) Waukesha L7042 - natural gas-fired four-stroke rich burn internal combustion engine equipped with a three-way oxidation catalyst controlling CH2O, CO, NOx, & VOCs by 80, 97, 98.5 & 66 percent respectively | 2015-04-17 | CC002(Catalytic Converter): Compressor Engine #2 - 3-way Catalyst | Air Hygiene, Inc. | 1480 hp | 1.0 g/hp-hr | 1114 hp | 0.13 g/hp-hr | 7E | Nitrogen Dioxide | PP | NA | Y
2015 | 785 | 0634005034 | Lake Compressor Station | County Highway 21 | Freeport | 43973 |  | Harrison | P004 | Compressor Engine #4 - 1980 HP (15.43 MMBtu/hr) Waukesha P9390 - natural gas-fired four-stroke rich burn internal combustion engine equipped with a three-way oxidation catalyst controlling CH2O, CO, NOx, & VOCs by 80, 97, 98.5 & 66 percent respectively | 2015-04-17 | CC004(Catalytic Converter): Compressor Engine #4 - 3-way Catalyst | Air Hygiene, Inc. | 1980 hp | 1.0 g/hp-hr | 1626 hp | 0.06 g/hp-hr | 7E | Nitrogen Dioxide | PP | NA | Y
2015 | 789 | 0634005048 | Gulfport Energy- Boy Scout Well Pad | 79900 Adams Rd | Tippecanoe | 44699 |  | Harrison | P002 | One 60 hp Waukesha 310 and one 64 hp HEC 3491-OPV natural gas engines for compressors | 2015-06-23 | catalyst | Great Plains Analytical Services | 118 hp | 2.0 g/hp-hr | 92 hp | 0.671 g/hp-hr | 6348 03 | NOx - Nitrogen Oxides | PP | NA | Y | 118 hp Cummins engine, serial number 46639148
2015 | 791 | 0634005049 | Gulfport Energy- Ryser #1-25H Well Pad | 77100 Scott Hill Road | Flushing | 43977 |  | Harrison | P002 | One or multiple stationary natural gas-fired spark ignition (SI) internal combustion engines (ICE) with a combined total horsepower (HP) of no more than 1,800 HP for the site. | 2015-06-24 | catalyst | Great Plains Analytical Services | 425 hp | 2.0 g/hp-hr | 353 hp | 1.197 g/hp-hr | 6348 03 | NOx - Nitrogen Oxides | PP | NA | Y
2015 | 794 | 0634005056 | Scio Compressor Station | 37650 Bower Rd | Scio | 43988 |  | Harrison | P003 | Compressor Engine #3 - 1,775 HP Caterpillar G3606 (4S-LB) - natural gas-fired four-cycle lean burn internal combustion engine equipped with an oxidation catalyst controlling CO & VOC emissions | 2015-06-22 | CC003(Catalytic Converter): Compressor Engine #3 - Oxidation Catalyst | Alliance Source Testing | 1775 hp | 0.50 g/hp-hr | 1772 hp | 0.28 g/hp-hr | 7E | Nitrogen Dioxide | PP | NA | Y
2015 | 797 | 0634005056 | Scio Compressor Station | 37650 Bower Rd | Scio | 43988 |  | Harrison | P006 | Compressor Engine #6 - 1,775 HP Caterpillar G3606 (4S-LB) - natural gas-fired four-cycle lean burn internal combustion engine equipped with an oxidation catalyst controlling CO & VOC emissions | 2015-06-22 | CC006(Catalytic Converter): Compressor Engine #6 - Oxidation Catalyst | Alliance Source Testing | 1775 hp | 0.50 g/hp-hr | 1609 hp | 0.42 g/hp-hr | 7E | Nitrogen Dioxide | PP | NA | Y
2015 | 801 | 0634005056 | Scio Compressor Station | 37650 Bower Rd | Scio | 43988 |  | Harrison | P002 | Compressor Engine #2 - 1,775 HP Caterpillar G3606 (4S-LB) - natural gas-fired four-cycle lean burn internal combustion engine equipped with an oxidation catalyst controlling CO & VOC emissions | 2015-06-23 | CC002(Catalytic Converter): Compressor Engine #2 - Oxidation Catalyst | Alliance Source Testing | 1775 hp | 0.50 g/hp-hr | 1598 hp | 0.38 g/hp-hr | 7E | Nitrogen Dioxide | PP | NA | Y
2015 | 803 | 0634005056 | Scio Compressor Station | 37650 Bower Rd | Scio | 43988 |  | Harrison | P008 | Compressor Engine #8 - 1,775 HP Caterpillar G3606 (4S-LB) - natural gas-fired four-cycle lean burn internal combustion engine equipped with an oxidation catalyst controlling CO & VOC emissions | 2015-06-23 | CC008(Catalytic Converter): Compressor Engine #8 - Oxidation Catalyst | Alliance Source Testing | 1775 hp | 0.50 g/hp-hr | 1598 hp | 0.32 g/hp-hr | 7E | Nitrogen Dioxide | PP | NA | Y
2015 | 808 | 0634005056 | Scio Compressor Station | 37650 Bower Rd | Scio | 43988 |  | Harrison | P010 | Compressor Engine #10 - 1,775 HP Caterpillar G3606 (4S-LB) - natural gas-fired four-cycle lean burn internal combustion engine equipped with an oxidation catalyst controlling CO & VOC emissions | 2015-06-23 | CC010(Catalytic Converter): Compressor Engine #10 - Oxidation Catalyst | Alliance Source Testing | 1775 hp | 0.50 g/hp-hr | 1598 hp | 0.33 g/hp-hr | 7E | Nitrogen Dioxide | PP | NA | Y
2015 | 811 | 0634005056 | Scio Compressor Station | 37650 Bower Rd | Scio | 43988 |  | Harrison | P004 | Compressor Engine #4 - 1,775 HP Caterpillar G3606 (4S-LB) - natural gas-fired four-cycle lean burn internal combustion engine equipped with an oxidation catalyst controlling CO & VOC emissions | 2015-07-01 | CC004(Catalytic Converter): Compressor Engine #4 - Oxidation Catalyst | Alliance Source Testing | 1775 hp | 0.50 g/hp-hr | 1615 hp | 0.28 g/hp-hr | 7E | Nitrogen Dioxide | PP | NA | Y
2015 | 814 | 0634005056 | Scio Compressor Station | 37650 Bower Rd | Scio | 43988 |  | Harrison | P005 | Compressor Engine #5 - 1,775 HP Caterpillar G3606 (4S-LB) - natural gas-fired four-cycle lean burn internal combustion engine equipped with an oxidation catalyst controlling CO & VOC emissions | 2015-07-01 | CC005(Catalytic Converter): Compressor Engine #5 - Oxidation Catalyst | Alliance Source Testing | 1775 hp | 0.50 g/hp-hr | 1621 hp | 0.31 g/hp-hr | 7E | Nitrogen Dioxide | PP | NA | Y
2015 | 816 | 0634005056 | Scio Compressor Station | 37650 Bower Rd | Scio | 43988 |  | Harrison | P007 | Compressor Engine #7 - 1,775 HP Caterpillar G3606 (4S-LB) - natural gas-fired four-cycle lean burn internal combustion engine equipped with an oxidation catalyst controlling CO & VOC emissions | 2015-07-01 | CC007(Catalytic Converter): Compressor Engine #7 - Oxidation Catalyst | Alliance Source Testing | 1775 hp | 0.50 g/hp-hr | 1722 hp | 0.29 g/hp-hr | 7E | Nitrogen Dioxide | PP | NA | Y
2015 | 819 | 0634005056 | Scio Compressor Station | 37650 Bower Rd | Scio | 43988 |  | Harrison | P009 | Compressor Engine #9 - 1,775 HP Caterpillar G3606 (4S-LB) - natural gas-fired four-cycle lean burn internal combustion engine equipped with an oxidation catalyst controlling CO & VOC emissions | 2015-07-01 | CC009(Catalytic Converter): Compressor Engine #9 - Oxidation Catalyst | Alliance Source Testing | 1775 hp | 0.50 g/hp-hr | 1728 hp | 0.28 g/hp-hr | 7E | Nitrogen Dioxide | PP | NA | Y
2015 | 821 | 0634005056 | Scio Compressor Station | 37650 Bower Rd | Scio | 43988 |  | Harrison | P001 | Compressor Engine #1 - 1,775 HP Caterpillar G3606 (4S-LB) - natural gas-fired four-cycle lean burn internal combustion engine equipped with an oxidation catalyst controlling CO & VOC emissions. | 2015-07-02 | CC001(Catalytic Converter): Compressor Engine #1 - Oxidation Catalyst | Alliance Source Testing | 1775 hp | 0.50 g/hp-hr | 1745 hp | 0.31 g/hp-hr | 7E | Nitrogen Dioxide | PP | NA | Y
2015 | 828 | 0634005069 | Gulfport Energy - Arrowhead II - Darla | 65800 Mt. Olivett Road | Flushing | 43977 |  | Harrison | P002 | One or multiple stationary natural gas-fired spark ignition (SI) internal combustion engines (ICE) with a combined total horsepower (HP) of no more than 1,800 HP for the site.* Includes 2007 and later model year engines manufactured after the applicable effective date identified in 40 CFR 60.4230(a)(3) and engines manufactured before the NSPS effective date where compliance with the Part 60 Subpart JJJJ emissions standards for the same size engine can be demonstrated through stack testing. | 2015-03-19 | NSCR | Great Plains Analytical | 118 hp | 2.0 g/hp-hr | 99 hp | 0.139 g/hp-hr | 6348 03 | NOx - Nitrogen Oxides | PP | NA | Y
2015 | 830 | 0634005070 | Gulfport Energy - County Line II - Gustina-Bear | 34011 Cadiz-Piedmont Rd | Flushing | 43977 |  | Harrison | P002 | One or multiple stationary natural gas-fired spark ignition (SI) internal combustion engines (ICE) wiht a combined total horsepower (HP) of no more than 1,800 HP for the site. | 2015-03-18 | NSCR | Great Plains Analytical Services | 118 hp | 2.0 g/hp-hr | 57 hp | 0.523 g/hp-hr | 6348 03 | NOx - Nitrogen Oxides | PP | NA | N
2015 | 834 | 0634005071 | Gulfport Energy - County Line - Puskarich | 76015 Moorefield Hill Rd | Flushing | 43977 |  | Harrison | P002 | One or multiple stationary natural gas-fired spark ignition (SI) internal combustion engines (ICE) with a combined total horsepower (HP) of no more than 1,000 HP for the site.* Includes 2007 and later model year engines manufactured after the applicable effective date identified in 40 CFR 60.4230(a)(3); and engines manufactured before the effective date of the NSPS, where compliance with the Part 60 Subpart JJJJ emissions standards for the same size engine can be met by retrofitting the engine with a control device and demonstrated through stack testing. | 2015-03-17 | NSCR | Great Plains Analytical Services | 118 hp | 2.0 g/hp-hr | 103 hp | 0.419 g/hp-hr | 6348 03 | NOx - Nitrogen Oxides | PP | NA | Y
2015 | 837 | 0634005090 | E2 Ohio Compression LLC - Mizer | 84500 Addy Rd | Cadiz | 43907 |  | Harrison | P002 | One or multiple stationary natural gas-fired spark ignition (SI) internal combustion engines (ICE) with a combined total horsepower (HP) of no more than 1,800 HP for the site. Includes 2007 and later model year engines manufactured after the applicable effective date identified in 40 CFR 60.4230(a)(3) and engines manufactured before the NSPS effective date where compliance with the Part 60 Subpart JJJJ emission standards for the same size engine can be demonstrated through stack testing | 2015-02-12 | Cat01(Catalytic Converter): Oxidation Catalyst for 4SLB RICE | E2 Energy Services | 680 hp | 2.0 g/hp-hr | 675 hp | 0.25 g/hp-hr | 6348 03 | NOx - Nitrogen Oxides | PP | NA | Y
2015 | 838 | 0634005101 | Chesapeake Exploration LLC - Trushell 8-13-6 Pad | OH-151E Scio Bowerston Rd | Scio | 43988 |  | Harrison | P002 | One or multiple stationary natural gas-fired spark ignition (SI) internal combustion engines (ICE) with a combined total horsepower (HP) of no more than 1,800 HP for the site.* Includes 2007 and later model year engines manufactured after the applicable effective date identified in 40 CFR 60.4230(a)(3); and engines manufactured before the effective date of the NSPS, where compliance with the Part 60 Subpart JJJJ emissions standards for the same size engine can be met by retrofitting the engine with a control device and demonstrated through stack testing. | 2015-04-29 | NSCR | Alliance Source Testing | 211 hp | 2.0 g/hp-hr | 192 hp | 0.04 g/hp-hr | 7E | Nitrogen Dioxide | PP | NA | Y
2015 | 841 | 0634005103 | Gulfport Energy - Davidson | Possom Hollow Rd | Freeport | 43977 |  | Harrison | P002 | One or multiple stationary natural gas-fired spark ignition (SI) internal combustion engines (ICE) with a combined total horsepower (HP) of no more than 1,000 HP for the site.* Includes 2007 and later model year engines manufactured after the applicable effective date identified in 40 CFR 60.4230(a)(3); and engines manufactured before the effective date of the NSPS, where compliance with the Part 60 Subpart JJJJ emissions standards for the same size engine can be met by retrofitting the engine with a control device and demonstrated through stack testing. | 2015-03-19 | NSCR | Great Plains Analytical Service | 118 hp | 2.0 g/hp-hr | 101 hp | 0.163 g/hp-hr | 6348 03 | NOx - Nitrogen Oxides | PP | NA | Y
2015 | 845 | 0634005103 | Gulfport Energy - Davidson | Possom Hollow Rd | Freeport | 43977 |  | Harrison | P002 | One or multiple stationary natural gas-fired spark ignition (SI) internal combustion engines (ICE) with a combined total horsepower (HP) of no more than 1,000 HP for the site.* Includes 2007 and later model year engines manufactured after the applicable effective date identified in 40 CFR 60.4230(a)(3); and engines manufactured before the effective date of the NSPS, where compliance with the Part 60 Subpart JJJJ emissions standards for the same size engine can be met by retrofitting the engine with a control device and demonstrated through stack testing. | 2015-06-24 | catalyst | Great Plains Analytical Services | 118 hp | 2.0 g/hp-hr | 83 hp | 0.253 g/hp-hr | 6348 03 | NOx - Nitrogen Oxides | PP | NA | Y
2015 | 848 | 0634005108 | Gulfport Energy - Vozar | McElhaney Rd | Freeport | 43973 |  | Harrison | P002 | One or multiple stationary natural gas-fired spark ignition (SI) internal combustion engines (ICE) with a combined total horsepower (HP) of no more than 1,000 HP for the site.* Includes 2007 and later model year engines manufactured after the applicable effective date identified in 40 CFR 60.4230(a)(3); and engines manufactured before the effective date of the NSPS, where compliance with the Part 60 Subpart JJJJ emissions standards for the same size engine can be met by retrofitting the engine with a control device and demonstrated through stack testing. | 2015-06-25 | catalyst | Great Plains Analytical | 118 hp | 2.0 g/hp-hr | 92 hp | 0.222 g/hp-hr | 6348 03 | NOx - Nitrogen Oxides | PP | NA | Y
2015 | 870 | 0656005010 | Dominion East Ohio - Switzerland Compressor Station | German Ridge Road | Switzerland Twp. | 43942 |  | Monroe | P002 | 3550 Hp Natural gas-fired (4SLB) Caterpillar model 3612 LE DM5309-06 compressor engines equipped with catalytic reduction (three-way). | 2015-01-16 | AFR and catalyst controls | Air Compliance Consultants, Inc. | 3,550 hp | 0.5 g/hp-hr | 3,292 hp | 0.46 g/hp-hr | 6348 03 | NOx - Nitrogen Oxides | PP | NA | Y | Method 320 actually used for testing.
2015 | 874 | 0661005008 | Seneca Gas Plant | Zep Road | Summerfield | 43788 |  | Noble | P001 | Compressor Engine #1 - Natural gas-fired four-stroke lean burn (4SLB) internal combustion engine rated at an operating capacity of 4,735 horsepower (hp) and equipped with an oxidation catalyst. | 2015-04-27 | CC001(Catalytic Converter): Compressor Engine #1 - Catalyic Convertor; CC002(Catalytic Converter): Compressor Engine #2 - Catalytic Convertor | Air Hygiene, Inc | 4735 hp | 0.50 g/hp-hr | 4125 hp | 0.29 g/hp-hr | 7E | Nitrogen Dioxide | PP | NA | Y
2015 | 877 | 0661005008 | Seneca Gas Plant | Zep Road | Summerfield | 43788 |  | Noble | P002 | Compressor Engine #2 - Natural gas-fired four-stroke lean burn (4SLB) internal combustion engine rated at an operating capacity of 4,735 horsepower (hp) and equipped with an oxidation catalyst. | 2015-04-27 | CC001(Catalytic Converter): Compressor Engine #1 - Catalyic Convertor; CC002(Catalytic Converter): Compressor Engine #2 - Catalytic Convertor | Air Hygiene, Inc | 4735 hp | 0.50 g/hp-hr | 4072 hp | 0.36 g/hphr | 7E | Nitrogen Dioxide | PP | NA | Y
2015 | 879 | 0661005020 | Rockies Express Pipeline - Seneca Compressor Station | Seneca Lake Rd | Quaker City | 43773 |  | Noble | P001 | Natural gas fired 4 stroke rich burn compressor engine, Waukesha VHP-L7042GSI, controlled by air/fuel ratio and nonselective catalytic reduction (NSCR) | 2015-03-03 | Engine 1(Catalytic Converter): Compressor Engine 1 catalytic converter; Engine 2(Catalytic Converter): Compressor Engine 2 catalytic converter | Compressor Engineering Corp. | 1480 hp | 2.0 g/hp-hr | 1574 hp | 0.3 g/hp-hr | 6348 03 | NOx - Nitrogen Oxides | PP | NA | Y
2015 | 882 | 0661005020 | Rockies Express Pipeline - Seneca Compressor Station | Seneca Lake Rd | Quaker City | 43773 |  | Noble | P002 | Natural gas fired 4 stroke rich burn compressor engine, Waukesha P9394GSI, controlled by air/fuel ratio and nonselective catalytic reduction (NSCR) | 2015-03-03 | Engine 1(Catalytic Converter): Compressor Engine 1 catalytic converter; Engine 2(Catalytic Converter): Compressor Engine 2 catalytic converter | Compressor Engineering Corp. | 2250 hp | 2.0 g/hp-hr | 2237 hp | 0.1 g/hp-hr | 6348 03 | NOx - Nitrogen Oxides | PP | NA | Y
2015 | 885 | 0661005020 | Rockies Express Pipeline - Seneca Compressor Station | Seneca Lake Rd | Quaker City | 43773 |  | Noble | P004 | compressor engine | 2015-05-18 | Engine 5(Catalytic Converter): Compressor Engine 5 Catalytic Convertor; Engine 4(Catalytic Converter): Compressor Engine 4 Catalytic Convertor; | Compressor Engineering Cort. | 5000 hp | 0.50 g/hp-hr | 4728 hp | 0.4217 g/hp-hr | 7E | Nitrogen Dioxide | PP | NA | Y
2015 | 890 | 0661005027 | E2 Appalachian LLC - Batesville | 58380 St John Rd | Quaker City | 43773 |  | Noble | P001 | 1,680 Hp. Waukesha (L7044GSI) natural gas-fired, rich burn, turbocharged, with oxidation catalyst, compressor engine | 2015-01-26 | C2701C(Catalytic Converter): Engine Catalyst | E2 Energy Services | 1680 hp | 1.0 g/hp-hr | 1400 hp | 0.17 g/hp-hr | 6348 03 | NOx - Nitrogen Oxides | PP | NA | Y
2015 | 893 | 0661005027 | E2 Appalachian LLC - Batesville | 58380 St John Rd | Quaker City | 43773 |  | Noble | P002 | 1,680 Hp. Waukesha (L7044GSI) natural gas-fired, rich burn, turbocharged, with oxidation catalyst, compressor engine | 2015-01-26 | C2701C(Catalytic Converter): Engine Catalyst | E2 Energy Services | 1680 hp | 1.0 g/hp-hr | 1361 hp | 0.13 g/hp-hr | 6348 03 | NOx - Nitrogen Oxides | PP | NA | Y
2015 | 897 | 0661005027 | E2 Appalachian LLC - Batesville | 58380 St John Rd | Quaker City | 43773 |  | Noble | P003 | 1,680 Hp. Waukesha (L7044GSI) natural gas-fired, rich burn, turbocharged, with oxidation catalyst, compressor engine | 2015-01-27 | C2701C(Catalytic Converter): Engine Catalyst | E2 Energy Services | 1680 hp | 1.0 g/hp-hr | 1277 hp | 0.16 g/hp-hr | 6348 03 | NOx - Nitrogen Oxides | PP | NA | Y
2015 | 899 | 0661005027 | E2 Appalachian LLC - Batesville | 58380 St John Rd | Quaker City | 43773 |  | Noble | P007 | 1,680 Hp. Waukesha (L7044GSI) natural gas-fired, rich burn, turbocharged, with oxidation catalyst, compressor engine | 2015-02-19 | C2707C(Catalytic Converter): Engine Catalyst | E2 Energy Services | 1,680 hp | 1.0 g/hp-hr | 1,512 hp | 0.20 g/hp-hr | 6348 03 | NOx - Nitrogen Oxides | PP | NA | Y
2015 | 903 | 0661005027 | E2 Appalachian LLC - Batesville | 58380 St John Rd | Quaker City | 43773 |  | Noble | P008 | 1,680 Hp. Waukesha (L7044GSI) natural gas-fired, rich burn, turbocharged, with oxidation catalyst, compressor engine | 2015-02-19 | C2708C(Catalytic Converter): Engine Catalyst | E2 Energy Services | 1,680 hp | 1.0 g/hp-hr | 1,512 hp | 0.20 g/hp-hr | 6348 03 | NOx - Nitrogen Oxides | PP | NA | Y
2015 | 905 | 0661005027 | E2 Appalachian LLC - Batesville | 58380 St John Rd | Quaker City | 43773 |  | Noble | P004 | 1,680 Hp. Waukesha (L7044GSI) natural gas-fired, rich burn, turbocharged, with oxidation catalyst, compressor engine | 2015-02-20 | C2704C(Catalytic Converter): Engine Catalyst | E2 Energy Services | 1,680 hp | 1.0 g/hp-hr | 1,510 hp | 0.14 g/hp-hr | 6348 03 | NOx - Nitrogen Oxides | PP | NA | Y
2015 | 908 | 0661005027 | E2 Appalachian LLC - Batesville | 58380 St John Rd | Quaker City | 43773 |  | Noble | P005 | 1,680 Hp. Waukesha (L7044GSI) natural gas-fired, rich burn, turbocharged, with oxidation catalyst, compressor engine | 2015-02-27 | C2705C(Catalytic Converter): Engine Catalyst | E2 Energy Services | 1,680 hp | 1.0 g/hp-hr | 1,295 hp | 0.20 g/hp-hr | 6348 03 | NOx - Nitrogen Oxides | PP | NA | Y
2016 | 289 | 0125064019 | Dublin Advanced Energy Partners - Dublin Rec Center | 5600 Post Road | Dublin | 43017 |  | Franklin | B001 | 349 bhp natural gas-fired stationary combustion engine | 2016-03-22 | None | Air Compliance Testing | 349 hp-hr | 1.0 g/hp-hr or 82 ppmvd at 15% O2 | 332.6 hp-hr | 81.4 ppmvd at 15% O2 | 7E | Nitrogen Dioxide | PP | Y | NA | This testing was performed to satisfy the initial testing requirements of 40 CFR Part 60 Subpart JJJJ - Standards of Performance for Stationary Spark Ignition Internal Combustion Engines.
2016 | 387 | 0210000046 | Tennessee Gas Pipeline - Station 214 | 2029 Cobbler Road NE | Carrollton | 44615 | 0000 | Carroll | P005 | 1320 HP (14.52 mmBtu/hr) natural gas-fired, spark ignition, 4-cycle/rich burn, reciprocating pipeline compressor engine with non-selective catalytic reduction | 2016-09-21 | Catalysts that are installed to control Multiple Pollutants. | Kinder Morgan Technical Services Group | 1320 Hp | 2.0 g/hp-hr | 1272 Hp | 0.2 g/hp-hr | 320 | NOx - Nitrogen Oxides | PP | Y | NA | Nox tested to comply with the NOx SIP. The Nox was tested via 7E.
2016 | 388 | 0210000046 | Tennessee Gas Pipeline - Station 214 | 2029 Cobbler Road NE | Carrollton | 44615 | 0000 | Carroll | P006 | 1320 HP (14.52 mmBtu/hr) natural gas-fired, spark ignition, 4-cycle/rich burn, reciprocating pipeline compressor engine with non-selective catalytic reduction | 2016-09-21 | Catalysts that are installed to control Multiple Pollutants. | Kinder Morgan Technical Services Group | 1320 Hp | 2.0 g/hp-hr | 1249 Hp | 0.1 g/hp-hr | 320 | NOx - Nitrogen Oxides | PP | Y | NA | Nox tested to comply with the NOx SIP. The Nox was tested via 7E.
2016 | 390 | 0210000046 | Tennessee Gas Pipeline - Station 214 | 2029 Cobbler Road NE | Carrollton | 44615 | 0000 | Carroll | P012 | 1320 HP (14.52 mmBtu/hr) natural gas-fired, spark ignition, 4-cycle/rich burn, reciprocating pipeline compressor engine with non-selective catalytic reduction | 2016-09-21 | Catalysts that are installed to control Multiple Pollutants. | Kinder Morgan Technical Services Group | 1320 Hp | 2.0 g/hp-hr | 1300 Hp | 0.2 g/hp-hr | 320 | NOx - Nitrogen Oxides | PP | Y | NA | Nox tested to comply with the NOx SIP. The Nox was tested via 7E.
2016 | 419 | 0210012030 | Blue Racer Midstream LLC - Carroll Co Field Station #1 | Cobbler Rd NE | Carrollton | 44615 |  | Carroll | P001 | 1,340 HP Caterpillar G3516LE 4SLB Compressor Engine #1 with Oxidation Catalyst. Engine model year: 2013. | 2016-10-14 | CC-1(Catalytic Converter): Oxidation Catalyst 1; CC-2(Catalytic Converter): Oxidation Catalyst 2; CC-3(Catalytic Converter): Oxidation Catalyst 3 | Montrose Air Quality Services | 1,340 Hp | 82 ppmvd@15% O2 & 0.5 g/bhp-hr | 1,129 HP or 82% | 31.3 ppmvd@15% O2 & 0.46 g/bhp-hr | 320 | NOx - Nitrogen Oxides | PP | Y | NA
2016 | 422 | 0210012030 | Blue Racer Midstream LLC - Carroll Co Field Station #1 | Cobbler Rd NE | Carrollton | 44615 |  | Carroll | P002 | 1,340 HP Caterpillar G3516LE 4SLB Compressor Engine #2 with Oxidation Catalyst. Engine model year: 2013. | 2016-10-14 | CC-1(Catalytic Converter): Oxidation Catalyst 1; CC-2(Catalytic Converter): Oxidation Catalyst 2; CC-3(Catalytic Converter): Oxidation Catalyst 3 | Montrose Air Quality Services | 1,340 Hp | 82 ppmvd@15% O2 & 0.5 g/bhp-hr | 1,053 HP or 76% | 30.0 ppmvd@15% O2 & 0.44 g/bhp-hr | 320 | NOx - Nitrogen Oxides | PP | Y | NA
2016 | 438 | 0210002039 | Kilgore Compressor Station-Utica Gas Services, LLC | Pontiff Rd | Kilgore | 43988 |  | Carroll | P001 | 1,775 hp NG-fired 4SLB Stationary ICE equipped w/catalyst Caterpillar G3606 Serial Number: 4ZS01713 | 2016-12-02 | CC001(Catalytic Converter): Compressor Engine #1 - Oxidation Catalyst; CC002(Catalytic Converter): Compressor Engine #2 - Oxidation Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - Oxidation Catalyst; CC004(Catalytic Converter): Compressor Eng | Technical Compliance Solutions LLC | 1775 | 2.0 g/Hp-hr, 1.96 lbs/hr | 1703 | 0.36 g/Hp-hr, 1.36 lbs/hr | 7E | Nitrogen Dioxide | PP | Y | NA
2016 | 439 | 0210002039 | Kilgore Compressor Station-Utica Gas Services, LLC | Pontiff Rd | Kilgore | 43988 |  | Carroll | P002 | 1,775 hp NG-fired 4SLB Stationary ICE equipped w/catalyst Caterpillar G3606: Serial Number: 4ZS01796 | 2016-12-02 | CC001(Catalytic Converter): Compressor Engine #1 - Oxidation Catalyst; CC002(Catalytic Converter): Compressor Engine #2 - Oxidation Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - Oxidation Catalyst; CC004(Catalytic Converter): Compressor Eng | Technical Compliance Solutions LLC | 1775 | 2.0 g/Hp-hr, 1.96 lbs/hr | 1664 | 0.46 g/Hp-hr, 1.68 lbs/hr | 7E | Nitrogen Dioxide | PP | Y | NA
2016 | 440 | 0210002039 | Kilgore Compressor Station-Utica Gas Services, LLC | Pontiff Rd | Kilgore | 43988 |  | Carroll | P003 | 1,775 hp NG-fired 4SLB Stationary ICE equipped w/catalyst Caterpillar G3606: Serial Number: 4ZS01797 | 2016-12-02 | CC001(Catalytic Converter): Compressor Engine #1 - Oxidation Catalyst; CC002(Catalytic Converter): Compressor Engine #2 - Oxidation Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - Oxidation Catalyst; CC004(Catalytic Converter): Compressor Eng | Technical Compliance Solutions LLC | 1775 | 2.0 g/Hp-hr, 1.96 lbs/hr | 1629 | 0.35 g/Hp-hr, 1.27 lbs/hr | 7E | Nitrogen Dioxide | PP | Y | NA
2016 | 441 | 0210002039 | Kilgore Compressor Station-Utica Gas Services, LLC | Pontiff Rd | Kilgore | 43988 |  | Carroll | P004 | 1,775 hp NG-fired 4SLB Stationary ICE equipped w/catalyst Caterpillar G3606: Serial Number: 4ZS01800 | 2016-12-02 | CC001(Catalytic Converter): Compressor Engine #1 - Oxidation Catalyst; CC002(Catalytic Converter): Compressor Engine #2 - Oxidation Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - Oxidation Catalyst; CC004(Catalytic Converter): Compressor Eng | Technical Compliance Solutions LLC | 1775 | 2.0 g/Hp-hr, 1.96 lbs/hr | 1626 | 0.39 g/Hp-hr, 1.38 lbs/hr | 7E | Nitrogen Dioxide | PP | Y | NA
2016 | 442 | 0210002039 | Kilgore Compressor Station-Utica Gas Services, LLC | Pontiff Rd | Kilgore | 43988 |  | Carroll | P005 | 1,775 hp NG-fired 4SLB Stationary ICE equipped w/catalyst Caterpillar G3606: Serial Number: 4ZS01804 | 2016-12-02 | CC001(Catalytic Converter): Compressor Engine #1 - Oxidation Catalyst; CC002(Catalytic Converter): Compressor Engine #2 - Oxidation Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - Oxidation Catalyst; CC004(Catalytic Converter): Compressor Eng | Technical Compliance Solutions LLC | 1775 | 2.0 g/Hp-hr, 1.96 lbs/hr | 1671 | 0.35 g/Hp-hr, 1.30 lbs/hr | 7E | Nitrogen Dioxide | PP | Y | NA
2016 | 443 | 0210002039 | Kilgore Compressor Station-Utica Gas Services, LLC | Pontiff Rd | Kilgore | 43988 |  | Carroll | P006 | 1,775 hp NG-fired 4SLB Stationary ICE equipped w/catalyst Caterpillar G3606: Serial Number: 4ZS01805 | 2016-12-02 | CC001(Catalytic Converter): Compressor Engine #1 - Oxidation Catalyst; CC002(Catalytic Converter): Compressor Engine #2 - Oxidation Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - Oxidation Catalyst; CC004(Catalytic Converter): Compressor Eng | Technical Compliance Solutions LLC | 1775 | 2.0 g/Hp-hr, 1.96 lbs/hr | 1615 | 0.42 g/Hp-hr, 1.50 lbs/hr | 7E | Nitrogen Dioxide | PP | Y | NA
2016 | 444 | 0210002039 | Kilgore Compressor Station-Utica Gas Services, LLC | Pontiff Rd | Kilgore | 43988 |  | Carroll | P007 | 1,775 hp NG-fired 4SLB Stationary ICE equipped w/catalyst Caterpillar G3606: Serial Number: 4ZS01807 | 2016-12-02 | CC001(Catalytic Converter): Compressor Engine #1 - Oxidation Catalyst; CC002(Catalytic Converter): Compressor Engine #2 - Oxidation Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - Oxidation Catalyst; CC004(Catalytic Converter): Compressor Eng | Technical Compliance Solutions LLC | 1775 | 2.0 g/Hp-hr, 1.96 lbs/hr | 1654 | 0.37 g/Hp-hr, 1.33 lbs/hr | 7E | Nitrogen Dioxide | PP | Y | NA
2016 | 445 | 0210002039 | Kilgore Compressor Station-Utica Gas Services, LLC | Pontiff Rd | Kilgore | 43988 |  | Carroll | P008 | 1,775 hp NG-fired 4SLB Stationary ICE equipped w/catalyst Caterpillar G3606: Serial Number: 4ZS01808 | 2016-12-02 | CC001(Catalytic Converter): Compressor Engine #1 - Oxidation Catalyst; CC002(Catalytic Converter): Compressor Engine #2 - Oxidation Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - Oxidation Catalyst; CC004(Catalytic Converter): Compressor Eng | Technical Compliance Solutions LLC | 1775 | 2.0 g/Hp-hr, 1.96 lbs/hr | 1667 | 0.44 g/Hp-hr, 1.61 lbs/hr | 7E | Nitrogen Dioxide | PP | Y | NA
2016 | 446 | 0210002039 | Kilgore Compressor Station-Utica Gas Services, LLC | Pontiff Rd | Kilgore | 43988 |  | Carroll | P009 | 1,775 hp NG-fired 4SLB Stationary ICE equipped w/catalyst Caterpillar G3606: Serial Number: 4ZS01776 | 2016-12-02 | CC001(Catalytic Converter): Compressor Engine #1 - Oxidation Catalyst; CC002(Catalytic Converter): Compressor Engine #2 - Oxidation Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - Oxidation Catalyst; CC004(Catalytic Converter): Compressor Eng | Technical Compliance Solutions LLC | 1775 | 2.0 g/Hp-hr, 1.96 lbs/hr | 1679 | 0.33 g/Hp-hr, 1.21 lbs/hr | 7E | Nitrogen Dioxide | PP | Y | NA
2016 | 447 | 0210002039 | Kilgore Compressor Station-Utica Gas Services, LLC | Pontiff Rd | Kilgore | 43988 |  | Carroll | P010 | 1,775 hp NG-fired 4SLB Stationary ICE equipped w/catalyst Caterpillar G3606: Serial Number: 4ZS01814 | 2016-12-02 | CC001(Catalytic Converter): Compressor Engine #1 - Oxidation Catalyst; CC002(Catalytic Converter): Compressor Engine #2 - Oxidation Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - Oxidation Catalyst; CC004(Catalytic Converter): Compressor Eng | Technical Compliance Solutions LLC | 1775 | 2.0 g/Hp-hr, 1.96 lbs/hr | 1740 | 0.40 g/Hp-hr, 1.53 lbs/hr | 7E | Nitrogen Dioxide | PP | Y | NA
2016 | 469 | 0210012002 | Utica Gas Services, LLC-Carrollton Compressor Facility | 2098 Panda Road SE | Carrollton | 44615 |  | Carroll | P004 | 1,775 HP natural gas-fired Caterpillar G3606 engine #1 equipped with an oxidation catalyst. | 2016-01-07 | Oxid. Cat.(Catalytic Converter): Oxidative Catalyst | Alliance Source Testing | 1775 HP | 1.96lbs/hr, 2.0g/hp-hr | 1644 HP | 1.13lbs/hr, 0.3 g/hp-hr | 7E | Nitrogen Oxide | PP | Y | NA
2016 | 470 | 0210012002 | Utica Gas Services, LLC-Carrollton Compressor Facility | 2098 Panda Road SE | Carrollton | 44615 |  | Carroll | P005 | 1,775 HP natural gas-fired Caterpillar G3606 engine #2 equipped with an oxidation catalyst | 2016-01-07 | Oxid. Cat.(Catalytic Converter): Oxidative Catalyst | Alliance Source Testing | 1775 HP | 1.96lbs/hr, 2.0g/hp-hr | 1737 HP | 1.10lbs/hr, 0.3 g/hp-hr | 7E | Nitrogen Oxide | PP | Y | NA
2016 | 471 | 0210012002 | Utica Gas Services, LLC-Carrollton Compressor Facility | 2098 Panda Road SE | Carrollton | 44615 |  | Carroll | P006 | 1,775 HP natural gas-fired Caterpillar G3606 engine #4 equipped with an oxidation catalyst | 2016-01-07 | Oxid. Cat.(Catalytic Converter): Oxidative Catalyst | Alliance Source Testing | 1775 HP | 1.96lbs/hr, 1.0g/hp-hr | 1627 HP | 1.96lbs/hr, 0.4 g/hp-hr | 7E | Nitrogen Oxide | PP | Y | NA
2016 | 472 | 0210012002 | Utica Gas Services, LLC-Carrollton Compressor Facility | 2098 Panda Road SE | Carrollton | 44615 |  | Carroll | P007 | 1,775 HP natural gas-fired Caterpillar G3606 engine #4 equipped with an oxidation catalyst | 2016-01-07 | Oxid. Cat.(Catalytic Converter): Oxidative Catalyst | Alliance Source Testing | 1775 HP | 1.96lbs/hr, 1.0g/hp-hr | 1710 HP | 1.11 lbs/hr, 0.3 g/hp-hr | 7E | Nitrogen Oxide | PP | Y | NA
2016 | 473 | 0210012002 | Utica Gas Services, LLC-Carrollton Compressor Facility | 2098 Panda Road SE | Carrollton | 44615 |  | Carroll | P008 | 1,775 HP natural gas-fired Caterpillar G3606 engine #5 equipped with an oxidation catalyst | 2016-01-07 | Oxid. Cat.(Catalytic Converter): Oxidative Catalyst | Alliance Source Testing | 1775 HP | 1.96lbs/hr, 1.0g/hp-hr | 1710 HP | 1.25 lbs/hr, 0.3 g/hp-hr | 7E | Nitrogen Oxide | PP | Y | NA
2016 | 474 | 0210012002 | Utica Gas Services, LLC-Carrollton Compressor Facility | 2098 Panda Road SE | Carrollton | 44615 |  | Carroll | P009 | 1,775 HP natural gas-fired Caterpillar G3606 engine #6 equipped with an oxidation catalyst | 2016-01-07 | Oxid. Cat.(Catalytic Converter): Oxidative Catalyst | Alliance Source Testing | 1775 HP | 1.96lbs/hr, 1.0g/hp-hr | 1656 HP | 1.35 lbs/hr, 0.4 g/hp-hr | 7E | Nitrogen Oxide | PP | Y | NA
2016 | 475 | 0210012002 | Utica Gas Services, LLC-Carrollton Compressor Facility | 2098 Panda Road SE | Carrollton | 44615 |  | Carroll | P010 | 1,775 HP natural gas-fired Caterpillar G3606 engine #7 equipped with an oxidation catalyst | 2016-01-07 | Oxid. Cat.(Catalytic Converter): Oxidative Catalyst | Alliance Source Testing | 1775 HP | 1.96lbs/hr, 1.0g/hp-hr | 1636 HP | 0.85 lbs/hr, 0.2 g/hp-hr | 7E | Nitrogen Oxide | PP | Y | NA
2016 | 476 | 0210012002 | Utica Gas Services, LLC-Carrollton Compressor Facility | 2098 Panda Road SE | Carrollton | 44615 |  | Carroll | P011 | 1,775 HP natural gas-fired Caterpillar G3606 engine #8 equipped with an oxidation catalyst | 2016-01-07 | Oxid. Cat.(Catalytic Converter): Oxidative Catalyst | Alliance Source Testing | 1775 HP | 1.96lbs/hr, 1.0g/hp-hr | 1657 HP | 1.38 lbs/hr, 0.4 g/hp-hr | 7E | Nitrogen Oxide | PP | Y | NA
2016 | 477 | 0210012002 | Utica Gas Services, LLC-Carrollton Compressor Facility | 2098 Panda Road SE | Carrollton | 44615 |  | Carroll | P012 | 1,775 HP natural gas-fired Caterpillar G3606 engine #9 equipped with an oxidation catalyst | 2016-01-07 | Oxid. Cat.(Catalytic Converter): Oxidative Catalyst | Alliance Source Testing | 1775 HP | 1.96lbs/hr, 1.0g/hp-hr | 16716 HP | 1.06 lbs/hr, 0.3 g/hp-hr | 7E | Nitrogen Oxide | PP | Y | NA
2016 | 478 | 0210012002 | Utica Gas Services, LLC-Carrollton Compressor Facility | 2098 Panda Road SE | Carrollton | 44615 |  | Carroll | P013 | 1,775 HP natural gas-fired Caterpillar G3606 engine #10equipped with an oxidation catalyst | 2016-01-07 | Oxid. Cat.(Catalytic Converter): Oxidative Catalyst | Alliance Source Testing | 1775 HP | 1.96lbs/hr, 1.0g/hp-hr | 1662 HP | 1.45 lbs/hr, 0.4 g/hp-hr | 7E | Nitrogen Oxide | PP | Y | NA
2016 | 501 | 0210012004 | Augusta Compressor Facility- Utica Gas Services, L.L.C. | 8034 Bane Rd NE | East Twp. | 44427 |  | Carroll | P006 | 1,775-hp Caterpillar G3606 Compressor Engine w/ Oxidation Catalyst | 2016-09-08 | Oxid. Cat. 3(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 4(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 5(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 6(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 7(Catalytic Converter): | EcoTest Energy Services | 1775 Hp | 1.96 lbs/hr, 1.0 g/hp/hr, 82 ppmvd@15%O2 | 1600 Hp or 90.1% of Max | 1.48 lbs/hr, .42 g/hp/hr, 36 ppmvd@15%O2 | 7E | Nitrogen Dioxide | PP | Y | NA
2016 | 502 | 0210012004 | Augusta Compressor Facility- Utica Gas Services, L.L.C. | 8034 Bane Rd NE | East Twp. | 44427 |  | Carroll | P007 | 1,775-hp Caterpillar G3606 Compressor Engine w/ Oxidation Catalyst | 2016-09-08 | Oxid. Cat. 3(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 4(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 5(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 6(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 7(Catalytic Converter): | EcoTest Energy Services | 1775 Hp | 1.96 lbs/hr, 1.0 g/hp/hr, 82 ppmvd@15%O2 | 1600 Hp or 90.1% of Max | 1.62 lbs/hr, .46 g/hp/hr, 40 ppmvd@15%O2 | 7E | Nitrogen Dioxide | PP | Y | NA
2016 | 503 | 0210012004 | Augusta Compressor Facility- Utica Gas Services, L.L.C. | 8034 Bane Rd NE | East Twp. | 44427 |  | Carroll | P008 | 1,775-hp Caterpillar G3606 Compressor Engine w/ Oxidation Catalyst | 2016-09-08 | Oxid. Cat. 3(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 4(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 5(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 6(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 7(Catalytic Converter): | EcoTest Energy Services | 1775 Hp | 1.96 lbs/hr, 1.0 g/hp/hr, 82 ppmvd@15%O2 | 1628 Hp or 91.7% of Max | 1.64 lbs/hr, .46 g/hp/hr, 39 ppmvd@15%O2 | 7E | Nitrogen Dioxide | PP | Y | NA
2016 | 504 | 0210012004 | Augusta Compressor Facility- Utica Gas Services, L.L.C. | 8034 Bane Rd NE | East Twp. | 44427 |  | Carroll | P009 | 1,775-hp Caterpillar G3606 Compressor Engine w/ Oxidation Catalyst | 2016-09-08 | Oxid. Cat. 3(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 4(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 5(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 6(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 7(Catalytic Converter): | EcoTest Energy Services | 1775 Hp | 1.96 lbs/hr, 1.0 g/hp/hr, 82 ppmvd@15%O2 | 1650 Hp or 93% of Max | 1.51 lbs/hr, .41 g/hp/hr, 37 ppmvd@15%O2 | 7E | Nitrogen Dioxide | PP | Y | NA
2016 | 505 | 0210012004 | Augusta Compressor Facility- Utica Gas Services, L.L.C. | 8034 Bane Rd NE | East Twp. | 44427 |  | Carroll | P010 | 1,775-hp Caterpillar G3606 Compressor Engine w/ Oxidation Catalyst | 2016-09-08 | Oxid. Cat. 3(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 4(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 5(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 6(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 7(Catalytic Converter): | EcoTest Energy Services | 1775 Hp | 1.96 lbs/hr, 1.0 g/hp/hr, 82 ppmvd@15%O2 | 1600 Hp or 90.1% of Max | 1.69 lbs/hr, .47 g/hp/hr, 40 ppmvd@15%O2 | 7E | Nitrogen Dioxide | PP | Y | NA
2016 | 506 | 0210012004 | Augusta Compressor Facility- Utica Gas Services, L.L.C. | 8034 Bane Rd NE | East Twp. | 44427 |  | Carroll | P011 | 1,775-hp Caterpillar G3606 Compressor Engine w/ Oxidation Catalyst | 2016-09-08 | Oxid. Cat. 3(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 4(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 5(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 6(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 7(Catalytic Converter): | EcoTest Energy Services | 1775 Hp | 1.96 lbs/hr, 1.0 g/hp/hr, 82 ppmvd@15%O2 | 1600 Hp or 90.1% of Max | 1.6 lbs/hr, .45 g/hp/hr, 40 ppmvd@15%O2 | 7E | Nitrogen Dioxide | PP | Y | NA
2016 | 507 | 0210012004 | Augusta Compressor Facility- Utica Gas Services, L.L.C. | 8034 Bane Rd NE | East Twp. | 44427 |  | Carroll | P012 | 1,775-hp Caterpillar G3606 Compressor Engine w/ Oxidation Catalyst | 2016-09-08 | Oxid. Cat. 3(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 4(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 5(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 6(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 7(Catalytic Converter): | EcoTest Energy Services | 1775 Hp | 1.96 lbs/hr, 1.0 g/hp/hr, 82 ppmvd@15%O2 | 1600 Hp or 90.1% of Max | 1.81 lbs/hr, .51 g/hp/hr, 44 ppmvd@15%O2 | 7E | Nitrogen Dioxide | PP | Y | NA
2016 | 508 | 0210012004 | Augusta Compressor Facility- Utica Gas Services, L.L.C. | 8034 Bane Rd NE | East Twp. | 44427 |  | Carroll | P013 | 1,775-hp Caterpillar G3606 Compressor Engine w/ Oxidation Catalyst | 2016-09-08 | Oxid. Cat. 3(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 4(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 5(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 6(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 7(Catalytic Converter): | EcoTest Energy Services | 1775 Hp | 1.96 lbs/hr, 1.0 g/hp/hr, 82 ppmvd@15%O2 | 1600 Hp or 90.1% of Max | 1.41 lbs/hr, .40 g/hp/hr, 35 ppmvd@15%O2 | 7E | Nitrogen Dioxide | PP | Y | NA
2016 | 517 | 0210012030 | Blue Racer Midstream LLC - Carroll Co Field Station #1 | Cobbler Rd NE | Carrollton | 44615 |  | Carroll | P003 | 1,340 HP Caterpillar G3516LE 4SLB Compressor Engine #3 with Oxidation Catalyst | 2016-10-14 | CC-1(Catalytic Converter): Oxidation Catalyst 1; CC-2(Catalytic Converter): Oxidation Catalyst 2; CC-3(Catalytic Converter): Oxidation Catalyst 3 | Montrose Air Quality Services | 1,340 Hp | 82 ppmvd@15% O2 & 0.5 g/bhp-hr | 1,086 HP or 79% | 30.5 ppmvd@15% O2 & 0.45 g/bhp-hr | 320 | NOx - Nitrogen Oxides | PP | Y | NA
2016 | 720 | 0285000366 | East Ohio Gas - Chippewa Station | 17045 Galehouse Road | Doylestown | 44230 |  | Wayne | B010 | 2,370 hp 4SLB SI ICE; CAT G3608 | 2016-05-18 | Engine 5 Converter(Catalytic Converter): Engine #5; Cat B010(Catalytic Converter): Catalytic Converter for B010, engine #6; Catalytic(Catalytic Converter): Engine 7 Catalytic converter | Environmental Quality Management | 2370 HP | 2.0 g/hp-hr, 3.66 lb/hr 160 ppmdv @ 15% O2 | 2180 Hp | 0.42 g/hp-hr, 2.04 lb/hr 30.8 ppmvd @ 15% O2 | 7E | Nitrogen Dioxide | PP | Y | NA | B010-2.75 Catalyst Pressure and 860 degF Catalyst temp, B014-1.2 Catalyst Pressure and 874 degF Catalyst Temperature
2016 | 721 | 0285000366 | East Ohio Gas - Chippewa Station | 17045 Galehouse Road | Doylestown | 44230 |  | Wayne | B014 | 2,370 hp 4SLB SI ICE: CAT 3608 w/catalyst | 2016-05-18 | Engine 5 Converter(Catalytic Converter): Engine #5; Cat B010(Catalytic Converter): Catalytic Converter for B010, engine #6; Catalytic(Catalytic Converter): Engine 7 Catalytic converter | Environmental Quality Management | 2370 Hp | 1.0 g/hp-hr, 2.61 lb/hr 82 ppmdv @ 15% O2 | 2228 Hp | 0.45 g/hp-hr, 2.19 lb/hr 33.0 ppmdv @ 15% O2 | 7E | Nitrogen Dioxide | PP | Y | NA | B010-2.75 Catalyst Pressure and 860 degF Catalyst temp, B014-1.2 Catalyst Pressure and 874 degF Catalyst Temperature
2016 | 725 | 0285000388 | East Ohio Gas Company - Paint | STATE RTE 250 | Wooster | 44624 |  | Wayne | B002 | Natural gas fired Internal Combustion Engine with max input capacity of 11.9 MMBtu/hr - Caterpillar G3516TALE with 1340 HP, 4-stroke, selective catalytic reduction (SCR) | 2016-07-07 | Three way Catalyst; CatOx(Catalytic Converter): Catalytic oxidizer for Engine 2 | Environmental Quality Management | 1340 Hp | 160 ppm @ 15% O2 and 2.0 g/hp-hr | 1259 HP or 94% | 106.7 ppm @ 15% O2 and 1.41 g/hp-hr | 7E | Nitrogen Oxide | PP | Y | NA
2016 | 893 | 0661005008 | Seneca Gas Plant | Zep Road | Summerfield | 43788 |  | Noble | P001 | Compressor Engine #1 - Natural gas-fired four-stroke lean burn (4SLB) internal combustion engine rated at an operating capacity of 4,735 horsepower (hp) and equipped with an oxidation catalyst. | 2016-03-17 | CC001(Catalytic Converter): Compressor Engine #1 - Catalyic Convertor; CC002(Catalytic Converter): Compressor Engine #2 - Catalytic Convertor | Air Hygiene International, Inc | 4735 hp | 0.50 g/hp-hr | 4182 hp | 0.38 g/hp-hr | 7E | Nitrogen Dioxide | PP | Y | NA
2016 | 894 | 0661005008 | Seneca Gas Plant | Zep Road | Summerfield | 43788 |  | Noble | P002 | Compressor Engine #2 - Natural gas-fired four-stroke lean burn (4SLB) internal combustion engine rated at an operating capacity of 4,735 horsepower (hp) and equipped with an oxidation catalyst. | 2016-03-17 | CC001(Catalytic Converter): Compressor Engine #1 - Catalyic Convertor; CC002(Catalytic Converter): Compressor Engine #2 - Catalytic Convertor | Air Hygiene International, Inc | 4735 hp | 0.50 g/hp-hr | 4187 hp | 0.46 g/hp-hr | 7E | Nitrogen Dioxide | PP | Y | NA
2016 | 897 | 0661005052 | Long Compressor Station | 55135 Batesville Rd | Quaker City | 43773 |  | Noble | P008 | 1,680 hp Waukesha 7044GSI NG Fired-rich burn-4stroke compressor engine | 2016-01-28 | C-01(Catalytic Converter): Non-selective catalyst reduction device for C-2000; C-02(Catalytic Converter): Non-selective catalyst reduction device for C-2100; C-03(Catalytic Converter): Non-selective catalyst reduction device for C-2200; C-04(Catalytic Con | Technical Compliance Solutions | 1680 hp | 1.0 g/hp-hr | 1544 hp | 0.02 g/hp-hr | 320 | NOx - Nitrogen Oxides | PP | Y | NA
2016 | 901 | 0661005052 | Long Compressor Station | 55135 Batesville Rd | Quaker City | 43773 |  | Noble | P009 | 1,680 hp Waukesha 7044GSI NG Fired-rich burn-4stroke compressor engine | 2016-01-28 | C-09(Catalytic Converter): Non-selective catalyst reduction device for C-2800 | Technical Compliance Solutions | 1680 hp | 1.0 g/hp-hr | 1617 hp | 0.02 g/hp-hr | 320 | NOx - Nitrogen Oxides | PP | Y | NA
2016 | 903 | 0661005060 | CNX Gas LLC - Noble 36 Well Pad | 45379 Gurewicz Rd | Summerfield | 43788 |  | Noble | P002 | NOT INSTALLED AT PERMIT ISSUANCE TIME One or multiple stationary natural gas-fired spark ignition (SI) internal combustion engines (ICE) with a combined total horsepower (HP) of no more than 1,000 HP for the site.* Includes 2007 and later model year eng | 2016-04-04 | NSCR | EcoTest Energy Services | VRU-68 hp Flash Gas-400 hp | 2.0 g/hp-hr | VRU-22 hp Flash gas -100 hp | 0.67 g/hp-hr | 320 | NOx - Nitrogen Oxides | PP | Y | NA | these two engines combined are permitted as P002
2016 | 1133 | 0546015002 | Bellefontaine Gas Producers, LLC | 2946 US Route 68 North | Bellefontaine | 43311 |  | Logan | P001 | 2275 Hp, 4-stroke lean burn, non-emergency, spark ignition RICE; Ch. 31 modification issued 1/8/2014. | 2016-04-12 | N/A | DTE Energy | 2275 BHp | 0.6 | =>2047.5 BHP | 0.36 | 7E | Nitrogen Oxide | PP | Y | Y
2016 | 1146 | 0607005013 | Texas Eastern Transmission LP - Colerain | 72784 Colerain-Mt. Pleasant Rd | Colerain Twp. | 43916 |  | Belmont | P003 | emergency engine | 2016-04-13 | TBC-01(Other): oxidation catalyst; TBC-02(Other): oxidation catalyst | Nordon Corp. | 880 hp | 160 ppm | 823 hp | 67 ppm | 7E | Nitrogen Dioxide | PP | Y | NA
2016 | 1147 | 0607005016 | Barnesville West Compressor Station | Hwy 801 | Warren Twp. | 43713 |  | Belmont | P006 | Compressor Engine #1 - Natural gas-fired four-stroke lean burn (4SLB) internal combustion engine rated at an operating capacity of 2,370 horsepower (hp) and equipped with an oxidation catalyst | 2016-03-21 | CC001(Catalytic Converter): Compressor Engine #1 Catalytic Converter; CC002(Catalytic Converter): Compressor Engine #2 Catalytic Converter; CC003(Catalytic Converter): Compressor Engine #3 Catalytic Converter | Air Hygiene, Inc. | 2370 hp | 0.50 g/hp-hr | 2270 hp | 0.38 g/hp-hr | 7E | Nitrogen Dioxide | PP | Y | NA
2016 | 1148 | 0607005016 | Barnesville West Compressor Station | Hwy 801 | Warren Twp. | 43713 |  | Belmont | P007 | Compressor Engine #1 - Natural gas-fired four-stroke lean burn (4SLB) internal combustion engine rated at an operating capacity of 2,370 horsepower (hp) and equipped with an oxidation catalyst | 2016-03-21 | CC001(Catalytic Converter): Compressor Engine #1 Catalytic Converter; CC002(Catalytic Converter): Compressor Engine #2 Catalytic Converter; CC003(Catalytic Converter): Compressor Engine #3 Catalytic Converter | Air Hygiene, Inc. | 2370 hp | 0.50 g/hp-hr | 2264 hp | 0.41 g/hp-hr | 7E | Nitrogen Dioxide | PP | Y | NA
2016 | 1149 | 0607005016 | Barnesville West Compressor Station | Hwy 801 | Warren Twp. | 43713 |  | Belmont | P008 | Compressor Engine #3 - Natural gas-fired four-stroke lean burn (4SLB) internal combustion engine rated at an operating capacity of 2,370 horsepower (hp) and equipped with an oxidation catalyst | 2016-03-21 | CC001(Catalytic Converter): Compressor Engine #1 Catalytic Converter; CC002(Catalytic Converter): Compressor Engine #2 Catalytic Converter; CC003(Catalytic Converter): Compressor Engine #3 Catalytic Converter | Air Hygiene, Inc. | 2370 hp | 0.50 g/hp-hr | 2329 hp | 0.41 g/hp-hr | 7E | Nitrogen Dioxide | PP | Y | NA
2016 | 1156 | 0607005016 | Barnesville West Compressor Station | Hwy 801 | Warren Twp. | 43713 |  | Belmont | P009 | Compressor Engine #4 - Natural gas-fired four-stroke lean burn (4SLB) internal combustion engine rated at an operating capacity of 2,370 horsepower (hp) and equipped with an oxidation catalyst | 2016-03-22 | CC005(Catalytic Converter): Compressor Engine #5 Catalytic Converter; CC004(Catalytic Converter): Compressor Engine #4 Catalytic Converter; CC006(Catalytic Converter): Compressor Engine #6 Catalytic Converter | Air Hygiene, Inc. | 2370 hp | 0.5 g/hp-hr | 2198 hp | 0.43 g/hp-hr | 7E | Nitrogen Dioxide | PP | Y | NA
2016 | 1157 | 0607005016 | Barnesville West Compressor Station | Hwy 801 | Warren Twp. | 43713 |  | Belmont | P010 | Compressor Engine #5 - Natural gas-fired four-stroke lean burn (4SLB) internal combustion engine rated at an operating capacity of 2,370 horsepower (hp) and equipped with an oxidation catalyst | 2016-03-22 | CC005(Catalytic Converter): Compressor Engine #5 Catalytic Converter; CC004(Catalytic Converter): Compressor Engine #4 Catalytic Converter; CC006(Catalytic Converter): Compressor Engine #6 Catalytic Converter | Air Hygiene, Inc. | 2370 hp | 0.5 g/hp-hr | 2277 hp | 0.43 g/hp-hr | 7E | Nitrogen Dioxide | PP | Y | NA
2016 | 1158 | 0607005016 | Barnesville West Compressor Station | Hwy 801 | Warren Twp. | 43713 |  | Belmont | P011 | Compressor Engine #6 - Natural gas-fired four-stroke lean burn (4SLB) internal combustion engine rated at an operating capacity of 2,370 horsepower (hp) and equipped with an oxidation catalyst | 2016-03-22 | CC005(Catalytic Converter): Compressor Engine #5 Catalytic Converter; CC004(Catalytic Converter): Compressor Engine #4 Catalytic Converter; CC006(Catalytic Converter): Compressor Engine #6 Catalytic Converter | Air Hygiene, Inc. | 2370 hp | 0.5 g/hp-hr | 2281 hp | 0.41 g/hp-hr | 7E | Nitrogen Dioxide | PP | Y | NA
2016 | 1165 | 0607015001 | Tri-County Compressor Station (MarkWest / Ohio Oil Gath | N of intersection of Hwy 379 and Town | Barnesville | 43713 |  | Belmont | P003 | Compressor Engine #3 - 1980 HP (15.43 MMBtu/hr) Waukesha P9390 - natural gas-fired four-stroke rich burn internal combustion engine equipped with a three-way oxidation catalyst controlling CH2O, CO, NOx, & VOCs by 80, 97, 98.5 & 66 percent respectively | 2016-08-17 | CC002(Catalytic Converter): Compressor Engine #2 - 3-way Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - 3-way Catalyst; CC004(Catalytic Converter): Compressor Engine #4 - 3-way Catalyst; CC005(Catalytic Converter): Compressor Engine #5 - 3-w | Air Hygiene Internatinal, Inc | 1,980 hp | 1.00 g/hp-hr | 1,681 hp | 0.13 g/hp-hr | 7E | Nitrogen Dioxide | PP | Y | NA
2016 | 1166 | 0607015001 | Tri-County Compressor Station (MarkWest / Ohio Oil Gath | N of intersection of Hwy 379 and Town | Barnesville | 43713 |  | Belmont | P004 | Compressor Engine #4 - 1980 HP (15.43 MMBtu/hr) Waukesha P9390 - natural gas-fired four-stroke rich burn internal combustion engine equipped with a three-way oxidation catalyst controlling CH2O, CO, NOx, & VOCs by 80, 97, 98.5 & 66 percent respectively | 2016-08-17 | CC002(Catalytic Converter): Compressor Engine #2 - 3-way Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - 3-way Catalyst; CC004(Catalytic Converter): Compressor Engine #4 - 3-way Catalyst; CC005(Catalytic Converter): Compressor Engine #5 - 3-w | Air Hygiene Internatinal, Inc | 1,980 hp | 1.00 g/hp-hr | 1,668 hp | 0.01 g/hp-hr | 7E | Nitrogen Dioxide | PP | Y | NA
2016 | 1167 | 0607015001 | Tri-County Compressor Station (MarkWest / Ohio Oil Gath | N of intersection of Hwy 379 and Town | Barnesville | 43713 |  | Belmont | P005 | Compressor Engine #5 - 1980 HP (15.43 MMBtu/hr) Waukesha P9390 - natural gas-fired four-stroke rich burn internal combustion engine equipped with a three-way oxidation catalyst controlling CH2O, CO, NOx, & VOCs by 80, 97, 98.5 & 66 percent respectively | 2016-08-17 | CC002(Catalytic Converter): Compressor Engine #2 - 3-way Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - 3-way Catalyst; CC004(Catalytic Converter): Compressor Engine #4 - 3-way Catalyst; CC005(Catalytic Converter): Compressor Engine #5 - 3-w | Air Hygiene Internatinal, Inc | 1,980 hp | 1.00 g/hp-hr | 1,733 hp | 0.10 g/hp-hr | 7E | Nitrogen Dioxide | PP | Y | NA
2016 | 1168 | 0607015001 | Tri-County Compressor Station (MarkWest / Ohio Oil Gath | N of intersection of Hwy 379 and Town | Barnesville | 43713 |  | Belmont | P006 | Compressor Engine #6 - 1980 HP (15.43 MMBtu/hr) Waukesha P9390 - natural gas-fired four-stroke rich burn internal combustion engine equipped with a three-way oxidation catalyst controlling CH2O, CO, NOx, & VOCs by 80, 97, 98.5 & 66 percent respectively | 2016-08-17 | CC002(Catalytic Converter): Compressor Engine #2 - 3-way Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - 3-way Catalyst; CC004(Catalytic Converter): Compressor Engine #4 - 3-way Catalyst; CC005(Catalytic Converter): Compressor Engine #5 - 3-w | Air Hygiene Internatinal, Inc | 1,980 hp | 1.00 g/hp-hr | 1,709 hp | 0.01 g/hp-hr | 7E | Nitrogen Dioxide | PP | Y | NA
2016 | 1169 | 0607015001 | Tri-County Compressor Station (MarkWest / Ohio Oil Gath | N of intersection of Hwy 379 and Town | Barnesville | 43713 |  | Belmont | P007 | Compressor Engine #7 - 1980 HP (15.43 MMBtu/hr) Waukesha P9390 - natural gas-fired four-stroke rich burn internal combustion engine equipped with a three-way oxidation catalyst controlling CH2O, CO, NOx, & VOCs by 80, 97, 98.5 & 66 percent respectively | 2016-08-17 | CC002(Catalytic Converter): Compressor Engine #2 - 3-way Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - 3-way Catalyst; CC004(Catalytic Converter): Compressor Engine #4 - 3-way Catalyst; CC005(Catalytic Converter): Compressor Engine #5 - 3-w | Air Hygiene Internatinal, Inc | 1,980 hp | 1.00 g/hp-hr | 1,568 hp | 0.14 g/hp-hr | 7E | Nitrogen Dioxide | PP | Y | NA
2016 | 1170 | 0607015001 | Tri-County Compressor Station (MarkWest / Ohio Oil Gath | N of intersection of Hwy 379 and Town | Barnesville | 43713 |  | Belmont | P008 | Compressor Engine #8 - 1980 HP (15.43 MMBtu/hr) Waukesha P9390 - natural gas-fired four-stroke rich burn internal combustion engine equipped with a three-way oxidation catalyst controlling CH2O, CO, NOx, & VOCs by 80, 97, 98.5 & 66 percent respectively | 2016-08-17 | CC002(Catalytic Converter): Compressor Engine #2 - 3-way Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - 3-way Catalyst; CC004(Catalytic Converter): Compressor Engine #4 - 3-way Catalyst; CC005(Catalytic Converter): Compressor Engine #5 - 3-w | Air Hygiene Internatinal, Inc | 1,980 hp | 1.00 g/hp-hr | 1,757 hp | 0.11 g/hp-hr | 7E | Nitrogen Dioxide | PP | Y | NA
2016 | 1183 | 0607015007 | Humphreys Compressor Station | Johnson Ridge Rd | Barnesville | 43713 |  | Belmont | P001 | Compressor Engine #1 - Caterpillar G3612TA - natural gas fired four-stroke, lean burn internal combustion engine rated at an operating capacity of 3,550 horsepower equipped with a double oxidation catalyst. | 2016-04-12 | CC001(Catalytic Converter): Compressor Engine #1 - Oxidation Catalyst; CC002(Catalytic Converter): Compressor Engine #2 - Oxidation Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - Oxidation Catalyst | Air Hygiene, Inc | 3550 hp | 0.50 g/hp-hr | 3345 hp | 0.38 g/hp-hr | 7E | Nitrogen Dioxide | PP | Y | NA
2016 | 1184 | 0607015007 | Humphreys Compressor Station | Johnson Ridge Rd | Barnesville | 43713 |  | Belmont | P002 | Compressor Engine #1 - Caterpillar G3612TA - natural gas fired four-stroke, lean burn internal combustion engine rated at an operating capacity of 3,550 horsepower equipped with a double oxidation catalyst. | 2016-04-12 | CC001(Catalytic Converter): Compressor Engine #1 - Oxidation Catalyst; CC002(Catalytic Converter): Compressor Engine #2 - Oxidation Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - Oxidation Catalyst | Air Hygiene, Inc | 3550 hp | 0.50 g/hp-hr | 3318 hp | 0.35 g/hp-hr | 7E | Nitrogen Dioxide | PP | Y | NA
2016 | 1185 | 0607015007 | Humphreys Compressor Station | Johnson Ridge Rd | Barnesville | 43713 |  | Belmont | P003 | Compressor Engine #1 - Caterpillar G3612TA - natural gas fired four-stroke, lean burn internal combustion engine rated at an operating capacity of 3,550 horsepower equipped with a double oxidation catalyst. | 2016-04-12 | CC001(Catalytic Converter): Compressor Engine #1 - Oxidation Catalyst; CC002(Catalytic Converter): Compressor Engine #2 - Oxidation Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - Oxidation Catalyst | Air Hygiene, Inc | 3550 hp | 0.50 g/hp-hr | 3402 hp | 0.33 g/hp-hr | 7E | Nitrogen Dioxide | PP | Y | NA
2016 | 1192 | 0607015007 | Humphreys Compressor Station | Johnson Ridge Rd | Barnesville | 43713 |  | Belmont | P004 | Compressor Engine #1 - Caterpillar G3612TA - natural gas fired four-stroke, lean burn internal combustion engine rated at an operating capacity of 3,550 horsepower equipped with a double oxidation catalyst. | 2016-04-13 | CC004(Catalytic Converter): Compressor Engine #4 - Oxidation Catalyst; CC005(Catalytic Converter): Compressor Engine #5 - Oxidation Catalyst; CC006(Catalytic Converter): Compressor Engine #6 - Oxidation Catalyst | Air Hygiene, Inc | 3550 hp | 0.50 g/hp-hr | 3345 hp | 0.33 g/hp-hr | 7E | Nitrogen Dioxide | PP | Y | NA
2016 | 1193 | 0607015007 | Humphreys Compressor Station | Johnson Ridge Rd | Barnesville | 43713 |  | Belmont | P005 | Compressor Engine #1 - Caterpillar G3612TA - natural gas fired four-stroke, lean burn internal combustion engine rated at an operating capacity of 3,550 horsepower equipped with a double oxidation catalyst. | 2016-04-13 | CC004(Catalytic Converter): Compressor Engine #4 - Oxidation Catalyst; CC005(Catalytic Converter): Compressor Engine #5 - Oxidation Catalyst; CC006(Catalytic Converter): Compressor Engine #6 - Oxidation Catalyst | Air Hygiene, Inc | 3550 hp | 0.50 g/hp-hr | 3341 hp | 0.34 g/hp-hr | 7E | Nitrogen Dioxide | PP | Y | NA
2016 | 1194 | 0607015007 | Humphreys Compressor Station | Johnson Ridge Rd | Barnesville | 43713 |  | Belmont | P006 | Compressor Engine #1 - Caterpillar G3612TA - natural gas fired four-stroke, lean burn internal combustion engine rated at an operating capacity of 3,550 horsepower equipped with a double oxidation catalyst. | 2016-04-13 | CC004(Catalytic Converter): Compressor Engine #4 - Oxidation Catalyst; CC005(Catalytic Converter): Compressor Engine #5 - Oxidation Catalyst; CC006(Catalytic Converter): Compressor Engine #6 - Oxidation Catalyst | Air Hygiene, Inc | 3550 hp | 0.50 g/hp-hr | 3297 | 0.35 g/hp-hr | 7E | Nitrogen Dioxide | PP | Y | NA
2016 | 1198 | 0607075002 | Ascent Resources - Utica, LLC - CHC Dutton (Wheeling) | 43125 Dutton Drive | Flushing | 43977 |  | Belmont | P007 | Natural Gas Compression engine | 2016-06-28 | Comp Engine(Catalytic Converter): Natural Gas Compressor Engine Catalytic Converter | EcoTest Energy Resources | 211 hp | 0.5 g/hp-hr | 139 hp | 0.28 g/hp-hr | 320 | NOx - Nitrogen Oxides | PP | Y | NA
2016 | 1240 | 0630005035 | Ascent Resources - Utica LLC - Coad 12-9N-7W | 25595 Oxford Rd | Quaker City | 43773 |  | Guernsey | P002 | One or multiple stationary natural gas-fired spark ignition (SI) internal combustion engines (ICE) with a combined total horsepower (HP) of no more than 1,800 HP for the site. Includes 2007 and later model year engines manufactured after the applicable e | 2016-03-08 | catalyst | Great Plains Analytical Services | 211 hp | 1.0 g/hp-hr | 116 hp | 0.12 g/hp-hr | 6348 03 | NOx - Nitrogen Oxides | PP | Y | NA
2016 | 1243 | 0630005037 | Blue Racer Midstream LLC - Guernsey Co Field Station #1 | East of I-70E and US 40E | Fairview | 43736 |  | Guernsey | P011 | Compressor engine 1875 HP Cat 3606 4 stroke lean burn oxidation catalyst | 2016-10-18 | CC-2(Catalytic Converter): Catalytic Converter 2; CC-3(Catalytic Converter): Catalytic Converter 3 | Great Plains Analytical Services | 1,875 hp | 1.00 g/hp-hr | 1,822 hp | 0.445 g/hp-hr | 6348 03 | NOx - Nitrogen Oxides | PP | N | NA
2016 | 1246 | 0630005037 | Blue Racer Midstream LLC - Guernsey Co Field Station #1 | East of I-70E and US 40E | Fairview | 43736 |  | Guernsey | P012 | Compressor engine 1875 HP Cat 3606 4 stroke lean burn oxidation catalyst | 2016-10-18 | CC-2(Catalytic Converter): Catalytic Converter 2; CC-3(Catalytic Converter): Catalytic Converter 3 | Great Plains Analytical Services | 1,875 hp | 1.00 g/hp-hr | 1,800 hp | 0.381 g/hp-hr | 6348 03 | NOx - Nitrogen Oxides | PP | N | NA
2016 | 1260 | 0630005039 | E2 Ohio Compression LLC - Hayes | 21260 Grape Hollow Rd | Salesville | 43778 |  | Guernsey | P032 | Cat G350B 690 HP NG engine | 2016-08-31 | Cat01(Catalytic Converter): Oxidation Catalyst for 4SLB RICE | E2Energy Services | 690 hp | 0.5 g/hp-hr | 345 hp | 0.42 g/hp-hr | 6348 03 | NOx - Nitrogen Oxides | PP | Y | NA
2016 | 1262 | 0630005041 | E2 Energy Services - Borton | 65483 Lydick Rd | Quaker City | 43773 |  | Guernsey | P002 | 1,680 Hp. Waukesha (L7044GSI) natural gas-fired, rich burn, turbocharged, with oxidation catalyst, compressor engine (Model Year 2014) | 2016-03-02 | C-2701C(Catalytic Converter): Engine Catalyst | E2 Energy Services | 1680 hp | 0.28 g/hp-hr | 1519 hp | 0.14 g/hp-hr | 6348 03 | NOx - Nitrogen Oxides | PP | N | NA
2016 | 1266 | 0630005041 | E2 Energy Services - Borton | 65483 Lydick Rd | Quaker City | 43773 |  | Guernsey | P004 | 1,680 Hp. Waukesha (L7044GSI) natural gas-fired, rich burn, turbocharged, with oxidation catalyst, compressor engine (Model Year 2014) | 2016-05-12 | C-2703C(Catalytic Converter): Engine Catalyst | E2 Energy Services | 1680 hp | 0.28 g/hp-hr | 1348 hp | 0.278 g/hp-hr | 6348 03 | NOx - Nitrogen Oxides | PP | Y | NA
2016 | 1268 | 0630005050 | Carrizo Utica LLC- Wagler Production Facility | Deck Rd | Londonderry Twp. | 45647 |  | Guernsey | P002 | One or multiple stationary natural gas-fired spark ignition (SI) internal combustion engines (ICE) with a combined total horsepower of 1,800 HP for the site. Includes 2007 or later model year engines manufactured after the applicable effective date iden | 2016-04-11 | catalyst | Alliance Source Testing | 275 hp | 1.0 g/hp-hr | 263 hp | 0.2 g/hp-hr | 7E | Nitrogen Dioxide | PP | Y | NA
2016 | 1271 | 0630005054 | Ascent Resources - Utica LLC - J Bar J Wellpad | 25204 Oxford Rd | Quaker City | 43773 |  | Guernsey | P002 | One or multiple stationary natural gas-fired spark ignition (SI) internal combustion engines (ICE) with a combined total horsepower (HP) of no more than 1,800 HP for the site. Includes 2007 and later model year engines manufactured after the applicable e | 2016-03-08 | catalyst | Great Plains Analytical Services, Inc | 211 hp | 1.0 g/hp-hr | 117 hp | 0.473 hp | 6348 03 | NOx - Nitrogen Oxides | PP | Y | NA
2016 | 1275 | 0630005055 | Ascent Resources - Utica LLC - Eggleston Wellpad | 17146 Easton Rd | Salesville | 43778 |  | Guernsey | P002 | One or multiple stationary natural gas-fired spark ignition (SI) internal combustion engines (ICE) with a combined total horsepower (HP) of no more than 1,800 HP for the site. Includes 2007 and later model year engines manufactured after the applicable e | 2016-06-28 | catalyst | EcoTest Energy Resources | 211 hp | 1.0 g/hp-hr | 80 hp | 0.05 g/hp-hr | 320 | NOx - Nitrogen Oxides | PP | Y | NA
2016 | 1279 | 0634005027 | Arrowhead Compressor Station | E of Clements Rd and S of Jockey Hollow | Athens Twp. | 43977 |  | Harrison | P008 | Compressor Engine #5 - Caterpillar G3608 - natural gas fired four-stroke, lean burn internal combustion engine rated at an operating capacity of 2,370 horsepower equipped with a catalytic convertor | 2016-10-31 | CC005(Catalytic Converter): Compressor Engine #5 Catalytic Convertor; CC006(Catalytic Converter): Compressor Engine #6 Catalytic Convertor | Air Hygiene International Inc. | 2,370 hp | 1.00 g/hp-hr | 2,264 hp | 0.34 g/hp-hr | 7E | Nitrogen Dioxide | PP | Y | NA
2016 | 1280 | 0634005027 | Arrowhead Compressor Station | E of Clements Rd and S of Jockey Hollow | Athens Twp. | 43977 |  | Harrison | P009 | Compressor Engine #6 - Caterpillar G3608 - natural gas fired four-stroke, lean burn internal combustion engine rated at an operating capacity of 2,370 horsepower equipped with a catalytic convertor | 2016-10-31 | CC005(Catalytic Converter): Compressor Engine #5 Catalytic Convertor; CC006(Catalytic Converter): Compressor Engine #6 Catalytic Convertor | Air Hygiene International Inc. | 2,370 hp | 1.00 g/hp-hr | 2,202 hp | 0.32 g/hp-hr | 7E | Nitrogen Dioxide | PP | Y | NA
2016 | 1285 | 0634005027 | Arrowhead Compressor Station | E of Clements Rd and S of Jockey Hollow | Athens Twp. | 43977 |  | Harrison | P010 | Compressor Engine #7 - Caterpillar G3608 - natural gas fired four-stroke, lean burn internal combustion engine rated at an operating capacity of 2,370 horsepower equipped with a catalytic convertor | 2016-11-01 | CC07(Catalytic Converter): Compressor Engine #7 Catalytic Convertor; CC008(Catalytic Converter): Compressor Engine #8 Catalytic Convertor | Air Hygiene International Inc. | 2,370 hp | 1.00 g/hp-hr | 2,210 hp | 0.38 g/hp-hr | 7E | Nitrogen Dioxide | PP | Y | NA
2016 | 1286 | 0634005027 | Arrowhead Compressor Station | E of Clements Rd and S of Jockey Hollow | Athens Twp. | 43977 |  | Harrison | P011 | Compressor Engine #8 - Caterpillar G3608 - natural gas fired four-stroke, lean burn internal combustion engine rated at an operating capacity of 2,370 horsepower equipped with a catalytic convertor | 2016-11-01 | CC07(Catalytic Converter): Compressor Engine #7 Catalytic Convertor; CC008(Catalytic Converter): Compressor Engine #8 Catalytic Convertor | Air Hygiene International Inc. | 2,370 hp | 1.00 g/hp-hr | 2,194 hp | 0.37 g/hp-hr | 7E | Nitrogen Dioxide | PP | Y | NA
2016 | 1291 | 0634005033 | Harrison West Compressor Station | Possum Hollow Road | Freeport | 43973 |  | Harrison | P005 | Compressor Engine #5 - 1980 HP (15.43 MMBtu/hr) Waukesha P9390 - natural gas-fired four-stroke rich burn internal combustion engine equipped with a three-way oxidation catalyst controlling CH2O, CO, NOx, & VOCs by 80, 97, 98.5 & 66 percent respectively | 2016-05-13 | CC005(Catalytic Converter): Compressor Engine #5 - 3-way Catalyst; CC006(Catalytic Converter): Compressor Engine #6 - 3-way Catalyst; CC007(Catalytic Converter): Compressor Engine #7 - 3-way Catalyst | Air Hygiene International | 1980 hp | 1.0 g/hp-hr | 1612 hp | 0.04 g/hp-hr | 7E | Nitrogen Dioxide | PP | Y | NA
2016 | 1292 | 0634005033 | Harrison West Compressor Station | Possum Hollow Road | Freeport | 43973 |  | Harrison | P006 | Compressor Engine #6 - 1980 HP (15.43 MMBtu/hr) Waukesha P9390 - natural gas-fired four-stroke rich burn internal combustion engine equipped with a three-way oxidation catalyst controlling CH2O, CO, NOx, & VOCs by 80, 97, 98.5 & 66 percent respectively | 2016-05-13 | CC005(Catalytic Converter): Compressor Engine #5 - 3-way Catalyst; CC006(Catalytic Converter): Compressor Engine #6 - 3-way Catalyst; CC007(Catalytic Converter): Compressor Engine #7 - 3-way Catalyst | Air Hygiene International | 1980 hp | 1.0 g/hp-hr | 1638 hp | 0.06 g/hp-hr | 7E | Nitrogen Dioxide | PP | Y | NA
2016 | 1293 | 0634005033 | Harrison West Compressor Station | Possum Hollow Road | Freeport | 43973 |  | Harrison | P007 | Compressor Engine #7 - 1980 HP (15.43 MMBtu/hr) Waukesha P9390 - natural gas-fired four-stroke rich burn internal combustion engine equipped with a three-way oxidation catalyst controlling CH2O, CO, NOx, & VOCs by 80, 97, 98.5 & 66 percent respectively | 2016-05-13 | CC005(Catalytic Converter): Compressor Engine #5 - 3-way Catalyst; CC006(Catalytic Converter): Compressor Engine #6 - 3-way Catalyst; CC007(Catalytic Converter): Compressor Engine #7 - 3-way Catalyst | Air Hygiene International | 1980 hp | 1.0 g/hp-hr | 1613 hp | 0.01 g/hp-hr | 7E | Nitrogen Dioxide | PP | Y | NA
2016 | 1300 | 0634005033 | Harrison West Compressor Station | Possum Hollow Road | Freeport | 43973 |  | Harrison | P001 | Compressor Engine #1 - 1480 HP (11.39 MMBtu/hr) Waukesha L7042 - natural gas-fired four-stroke rich burn internal combustion engine equipped with a three-way oxidation catalyst controlling CH2O, CO, NOx, & VOCs by 80, 97, 98.5 & 66 percent respectively | 2016-04-28 | CC001(Catalytic Converter): Compressor Engine #1 - 3-way Catalyst; CC002(Catalytic Converter): Compressor Engine #2 - 3-way Catalyst; CC004(Catalytic Converter): Compressor Engine #4 - 3-way Catalyst | Air Hygiene, Inc | 1480 hp | 1 g/hp-hr | 1181 hp | 0.04 g/hp-hr | 7E | Nitrogen Dioxide | PP | Y | NA
2016 | 1301 | 0634005033 | Harrison West Compressor Station | Possum Hollow Road | Freeport | 43973 |  | Harrison | P002 | Compressor Engine #2 - 1480 HP (11.39 MMBtu/hr) Waukesha L7042 - natural gas-fired four-stroke rich burn internal combustion engine equipped with a three-way oxidation catalyst controlling CH2O, CO, NOx, & VOCs by 80, 97, 98.5 & 66 percent respectively | 2016-04-28 | CC001(Catalytic Converter): Compressor Engine #1 - 3-way Catalyst; CC002(Catalytic Converter): Compressor Engine #2 - 3-way Catalyst; CC004(Catalytic Converter): Compressor Engine #4 - 3-way Catalyst | Air Hygiene, Inc | 1480 hp | 1 g/hp-hr | 1611 hp | 0.07 g/hp-hr | 7E | Nitrogen Dioxide | PP | Y | NA
2016 | 1302 | 0634005033 | Harrison West Compressor Station | Possum Hollow Road | Freeport | 43973 |  | Harrison | P004 | Compressor Engine #4 - 1980 HP (15.43 MMBtu/hr) Waukesha P9390 - natural gas-fired four-stroke rich burn internal combustion engine equipped with a three-way oxidation catalyst controlling CH2O, CO, NOx, & VOCs by 80, 97, 98.5 & 66 percent respectively | 2016-04-28 | CC001(Catalytic Converter): Compressor Engine #1 - 3-way Catalyst; CC002(Catalytic Converter): Compressor Engine #2 - 3-way Catalyst; CC004(Catalytic Converter): Compressor Engine #4 - 3-way Catalyst | Air Hygiene, Inc | 1980 hp | 1 g/hp-hr | 1589 hp | 0.13 g/hp-hr | 7E | Nitrogen Dioxide | PP | Y | NA
2016 | 1309 | 0634005034 | Lake Compressor Station | County Highway 21 | Freeport | 43973 |  | Harrison | P001 | Compressor Engine #1 - 1480 HP (11.39 MMBtu/hr) Waukesha L7042 - natural gas-fired four-stroke rich burn internal combustion engine equipped with a three-way oxidation catalyst controlling CH2O, CO, NOx, & VOCs by 80, 97, 98.5 & 66 percent respectively | 2016-03-28 | CC001(Catalytic Converter): Compressor Engine #1 - 3-way Catalyst; CC002(Catalytic Converter): Compressor Engine #2 - 3-way Catalyst | Air Hygiene, Inc. | 1480 hp | 0.2 g/hp-hr | 1233 hp | 0.12 g/hp-hr | 7E | Nitrogen Dioxide | PP | Y | NA
2016 | 1310 | 0634005034 | Lake Compressor Station | County Highway 21 | Freeport | 43973 |  | Harrison | P002 | Compressor Engine #2 - 1480 HP (11.39 MMBtu/hr) Waukesha L7042 - natural gas-fired four-stroke rich burn internal combustion engine equipped with a three-way oxidation catalyst controlling CH2O, CO, NOx, & VOCs by 80, 97, 98.5 & 66 percent respectively | 2016-03-28 | CC001(Catalytic Converter): Compressor Engine #1 - 3-way Catalyst; CC002(Catalytic Converter): Compressor Engine #2 - 3-way Catalyst | Air Hygiene, Inc. | 1480 hp | 0.2 g/hp-hr | 1374 hp | 0.14 g/hp-hr | 7E | Nitrogen Dioxide | PP | Y | NA
2016 | 1315 | 0634005034 | Lake Compressor Station | County Highway 21 | Freeport | 43973 |  | Harrison | P004 | Compressor Engine #4 - 1980 HP (15.43 MMBtu/hr) Waukesha P9390 - natural gas-fired four-stroke rich burn internal combustion engine equipped with a three-way oxidation catalyst controlling CH2O, CO, NOx, & VOCs by 80, 97, 98.5 & 66 percent respectively | 2016-04-14 | CC004(Catalytic Converter): Compressor Engine #4 - 3-way Catalyst; CC005(Catalytic Converter): Compressor Engine #5 - 3-way Catalyst; CC011(Catalytic Converter): Compressor Engine #9 - 3-way Catalyst | Air Hygiene, Inc | 1980 hp | 1.0 g/hp-hr | 1647 hp | 0.13 g/hp-hr | 7E | Nitrogen Dioxide | PP | N | NA | test did conform to test method-document locked
2016 | 1316 | 0634005034 | Lake Compressor Station | County Highway 21 | Freeport | 43973 |  | Harrison | P005 | Compressor Engine #5 - 1980 HP (15.43 MMBtu/hr) Waukesha P9390 - natural gas-fired four-stroke rich burn internal combustion engine equipped with a three-way oxidation catalyst controlling CH2O, CO, NOx, & VOCs by 80, 97, 98.5 & 66 percent respectively | 2016-04-14 | CC004(Catalytic Converter): Compressor Engine #4 - 3-way Catalyst; CC005(Catalytic Converter): Compressor Engine #5 - 3-way Catalyst; CC011(Catalytic Converter): Compressor Engine #9 - 3-way Catalyst | Air Hygiene, Inc | 1980 hp | 1.0 g/hp-hr | 1642 hp | 0.08 g/hp-hr | 7E | Nitrogen Dioxide | PP | N | NA | test did conform to test method-document locked
2016 | 1317 | 0634005034 | Lake Compressor Station | County Highway 21 | Freeport | 43973 |  | Harrison | P011 | Compressor Engine #9 - Waukesha L7042 - natural gas fired four-stroke, rich burn internal combustion engine rated at an operating capacity of 1,480 horsepower equipped with a three-way oxidation catalyst. | 2016-04-14 | CC004(Catalytic Converter): Compressor Engine #4 - 3-way Catalyst; CC005(Catalytic Converter): Compressor Engine #5 - 3-way Catalyst; CC011(Catalytic Converter): Compressor Engine #9 - 3-way Catalyst | Air Hygiene, Inc | 1980 hp | 1.0 g/hp-hr | 1079 hp | 0.18 g/hp-hr | 7E | Nitrogen Dioxide | PP | N | NA | test did conform to test method-document locked
2016 | 1324 | 0634005048 | Gulfport Energy - Boy Scout Well Pad | 79900 Adams Rd | Tippecanoe | 44699 |  | Harrison | P002 | One 630 hp Caterpillar 630 and one 118 hp Cummins G8.3C natural gas-fired engines for compressors. | 2016-08-24 | catalyst | Ecotest Inc. | 630 hp | 2.00 g/hp-hr | 455 hp | 1.00 g/hp-hr | 6348 03 | NOx - Nitrogen Oxides | PP | Y | NA
2016 | 1329 | 0634005056 | Scio Compressor Station | 37650 Bower Rd | Scio | 43988 |  | Harrison | P001 | Compressor Engine #1 - 1,775 HP Caterpillar G3606 (4S-LB) - natural gas-fired four-cycle lean burn internal combustion engine equipped with an oxidation catalyst controlling CO & VOC emissions. | 2016-06-06 | CC001(Catalytic Converter): Compressor Engine #1 - Oxidation Catalyst | EcoTest Energy Services | 1775 hp | 1.00 g/hp-hr | 1700 hp | 0.31 g/hp-hr | 320 | NOx - Nitrogen Oxides | PP | Y | NA
2016 | 1330 | 0634005056 | Scio Compressor Station | 37650 Bower Rd | Scio | 43988 |  | Harrison | P002 | Compressor Engine #2 - 1,775 HP Caterpillar G3606 (4S-LB) - natural gas-fired four-cycle lean burn internal combustion engine equipped with an oxidation catalyst controlling CO & VOC emissions | 2016-06-06 | CC002(Catalytic Converter): Compressor Engine #2 - Oxidation Catalyst | EcoTest Energy Services | 1775 hp | 1.00 g/hp-hr | 1695 hp | 0.36 g/hp-hr | 320 | NOx - Nitrogen Oxides | PP | Y | NA
2016 | 1333 | 0634005056 | Scio Compressor Station | 37650 Bower Rd | Scio | 43988 |  | Harrison | P003 | Compressor Engine #3 - 1,775 HP Caterpillar G3606 (4S-LB) - natural gas-fired four-cycle lean burn internal combustion engine equipped with an oxidation catalyst controlling CO & VOC emissions | 2016-06-06 | CC003(Catalytic Converter): Compressor Engine #3 - Oxidation Catalyst | EcoTest Energy Services | 1775 hp | 1.00 g/hp-hr | 1680 hp | 0.36 g/hp-hr | 320 | NOx - Nitrogen Oxides | PP | Y | NA
2016 | 1337 | 0634005056 | Scio Compressor Station | 37650 Bower Rd | Scio | 43988 |  | Harrison | P004 | Compressor Engine #4 - 1,775 HP Caterpillar G3606 (4S-LB) - natural gas-fired four-cycle lean burn internal combustion engine equipped with an oxidation catalyst controlling CO & VOC emissions | 2016-06-06 | CC004(Catalytic Converter): Compressor Engine #4 - Oxidation Catalyst | EcoTest Energy Services | 1775 hp | 1.00 g/hp-hr | 1750 hp | 0.32 g/hp-hr | 320 | NOx - Nitrogen Oxides | PP | Y | NA
2016 | 1340 | 0634005056 | Scio Compressor Station | 37650 Bower Rd | Scio | 43988 |  | Harrison | P005 | Compressor Engine #5 - 1,775 HP Caterpillar G3606 (4S-LB) - natural gas-fired four-cycle lean burn internal combustion engine equipped with an oxidation catalyst controlling CO & VOC emissions | 2016-06-06 | CC005(Catalytic Converter): Compressor Engine #5 - Oxidation Catalyst | EcoTest Energy Services | 1775 hp | 1.00 g/hp-hr | 1720 hp | 0.47 g/hp-hr | 320 | NOx - Nitrogen Oxides | PP | Y | NA
2016 | 1342 | 0634005056 | Scio Compressor Station | 37650 Bower Rd | Scio | 43988 |  | Harrison | P006 | Compressor Engine #6 - 1,775 HP Caterpillar G3606 (4S-LB) - natural gas-fired four-cycle lean burn internal combustion engine equipped with an oxidation catalyst controlling CO & VOC emissions | 2016-06-06 | CC006(Catalytic Converter): Compressor Engine #6 - Oxidation Catalyst | EcoTest Energy Services | 1775 hp | 1.00 g/hp-hr | 1720 hp | 0.32 g/hp-hr | 320 | NOx - Nitrogen Oxides | PP | Y | NA
2016 | 1345 | 0634005056 | Scio Compressor Station | 37650 Bower Rd | Scio | 43988 |  | Harrison | P007 | Compressor Engine #7 - 1,775 HP Caterpillar G3606 (4S-LB) - natural gas-fired four-cycle lean burn internal combustion engine equipped with an oxidation catalyst controlling CO & VOC emissions | 2016-06-07 | CC007(Catalytic Converter): Compressor Engine #7 - Oxidation Catalyst | EcoTest Energy Services | 1775 hp | 1.00 g/hp-hr | 1700 hp | 0.37 g/hp-hr | 320 | NOx - Nitrogen Oxides | PP | Y | NA
2016 | 1348 | 0634005056 | Scio Compressor Station | 37650 Bower Rd | Scio | 43988 |  | Harrison | P008 | Compressor Engine #8 - 1,775 HP Caterpillar G3606 (4S-LB) - natural gas-fired four-cycle lean burn internal combustion engine equipped with an oxidation catalyst controlling CO & VOC emissions | 2016-06-07 | CC008(Catalytic Converter): Compressor Engine #8 - Oxidation Catalyst | EcoTest Energy Services | 1775 hp | 1.00 g/hp-hr | 1707 hp | 0.42 g/hp-hr | 320 | NOx - Nitrogen Oxides | PP | Y | NA
2016 | 1352 | 0634005056 | Scio Compressor Station | 37650 Bower Rd | Scio | 43988 |  | Harrison | P009 | Compressor Engine #9 - 1,775 HP Caterpillar G3606 (4S-LB) - natural gas-fired four-cycle lean burn internal combustion engine equipped with an oxidation catalyst controlling CO & VOC emissions | 2016-06-07 | CC009(Catalytic Converter): Compressor Engine #9 - Oxidation Catalyst | EcoTest Energy Services | 1775 hp | 1.00 g/hp-hr | 1760 hp | 0.36 g/hp-hr | 320 | NOx - Nitrogen Oxides | PP | Y | NA
2016 | 1355 | 0634005056 | Scio Compressor Station | 37650 Bower Rd | Scio | 43988 |  | Harrison | P010 | Compressor Engine #10 - 1,775 HP Caterpillar G3606 (4S-LB) - natural gas-fired four-cycle lean burn internal combustion engine equipped with an oxidation catalyst controlling CO & VOC emissions | 2016-06-07 | CC010(Catalytic Converter): Compressor Engine #10 - Oxidation Catalyst | EcoTest Energy Services | 1775 hp | 1.00 g/hp-hr | 1725 hp | 0.30 g/hp-hr | 320 | NOx - Nitrogen Oxides | PP | Y | NA
2016 | 1359 | 0634005070 | Gulfport Energy - County Line II - Gustina-Bear | 34011 Cadiz-Piedmont Rd | Flushing | 43977 |  | Harrison | P002 | One or multiple stationary natural gas-fired spark ignition (SI) internal combustion engines (ICE) wiht a combined total horsepower (HP) of no more than 1,800 HP for the site. | 2016-02-17 | cagalyst | Ecotest Energy Services | 118 hp | 2.0 g/hp-hr | 90 hp | 1.38 g/hp-hr | 6348 03 | NOx - Nitrogen Oxides | PP | Y | NA
2016 | 1361 | 0634005086 | Ascent Resources - Utica LLC - Hamilton 19-11N-6W | 34385 Kennedy Ridge Rd | Flushing | 43977 |  | Harrison | P002 | One or multiple stationary natural gas-fired spark ignition (SI) internal combustion engines (ICE) with a combined total horsepower (HP) of no more than 1,800 HP for the site. Includes 2007 and later model year engines manufactured after the applicable e | 2016-05-23 | catalyst | Great Plaines Analytical Services | 400 hp 203 hp | 2.0 g/hp-hr | 338 hp 188 hp | 1.76 g/hp-hr | 6348 03 | NOx - Nitrogen Oxides | PP | Y | NA | P002 two engines on allowable rate
2016 | 1365 | 0634005086 | Ascent Resources - Utica LLC - Hamilton 19-11N-6W | 34385 Kennedy Ridge Rd | Flushing | 43977 |  | Harrison | P002 | One or multiple stationary natural gas-fired spark ignition (SI) internal combustion engines (ICE) with a combined total horsepower (HP) of no more than 1,800 HP for the site. Includes 2007 and later model year engines manufactured after the applicable e | 2016-05-26 | catalyst | Great Plaines Analytical Services | 400 hp 203 hp | 2.0 g/hp-hr | 338 hp 188 hp | 1.76 g/hp-hr | 6348 03 | NOx - Nitrogen Oxides | PP | Y | NA | P002 two engines on allowable rate
2016 | 1366 | 0634005090 | E2 Ohio Compression LLC - Mizer | 84500 Addy Rd | Cadiz | 43907 |  | Harrison | P010 | One stationary natural gas-fired spark ignition (SI) internal combustion engine (ICE) with a total horsepower (HP) of 1680 HP. Includes a 2007 and later model year engine manufactured after the applicable effective date identified in 40 CFR 60.4230(a)(3) | 2016-02-25 | Cat03(Catalytic Converter): 3-Way NSCR for 4SRB RICE | E2 Energy Services | 1680 hp | 0.27 g/hp-hr | 1534 hp | 0.22 g/hp-hr | 6348 03 | NOx - Nitrogen Oxides | PP | Y | NA
2016 | 1370 | 0634005090 | E2 Ohio Compression LLC - Mizer | 84500 Addy Rd | Cadiz | 43907 |  | Harrison | P009 | One stationary natural gas-fired spark ignition (SI) internal combustion engine (ICE) with a total horsepower (HP) of 1680 HP. Includes a 2007 and later model year engine manufactured after the applicable effective date identified in 40 CFR 60.4230(a)(3) | 2016-02-24 | Cat02(Catalytic Converter): 3-Way NSCR for 4SRB RICE | E2 Energy Services | 1680 hp | 0.27 g/hp-hr | 1563 hp | 0.03 g/hp-hr | 6348 03 | NOx - Nitrogen Oxides | PP | Y | NA
2016 | 1373 | 0634005090 | E2 Ohio Compression LLC - Mizer | 84500 Addy Rd | Cadiz | 43907 |  | Harrison | P011 | One stationary natural gas-fired spark ignition (SI) internal combustion engine (ICE) with a total horsepower (HP) of 1680 HP. Includes a 2007 and later model year engine manufactured after the applicable effective date identified in 40 CFR 60.4230(a)(3) | 2016-02-26 | Cat04(Catalytic Converter): 3-Way NSCR for 4SLB Rice | E2 Energy Services | 1680 hp | 0.27 g/hp-hr | 1431 hp | 0.05 g/hp-hr | 6348 03 | NOx - Nitrogen Oxides | PP | Y | NA
2016 | 1377 | 0634005121 | Ascent Resources - Utica LLC - Pettay Well Pad | 3440 Huff Run Rd | Cadiz | 43907 |  | Harrison | P002 | One or multiple stationary natural gas-fired spark ignition (SI) internal combustion engines (ICE) with a combined total horsepower (HP) of no more than 1,800 HP for the site. Includes 2007 and later model year engines manufactured after the applicable e | 2016-05-25 | catalyst | Great Plains Analytical Services | 276 hp 225 hp | 2.0 g/h--hr | 216 hp 154 hp | 0.95 g/hp-hr | 6348 03 | NOx - Nitrogen Oxides | PP | N | NA | two engines 276 hp and 225 hp. emissions rates and allowable combined
2016 | 1378 | 0634005123 | Yoder Compressor Station | 79300 Cassville Rd | Cadiz | 43907 |  | Harrison | P001 | Natural gas-fired four-stroke lean burn (4SLB) internal combustion engine rated at an operating capacity of 2,370 horsepower (hp) and equipped with an oxidation catalyst. | 2016-05-19 | CC001(Catalytic Converter): Compressor Engine #1 Catalytic Converter; CC002(Catalytic Converter): Compressor Engine #2 Catalytic Converter; CC003(Catalytic Converter): Compressor Engine #3 Catalytic Converter | Air Hygiene International | 2370 hp | 2.61 lb/hr | 2889 hp | 1.85 lb/hr | 7E | Nitrogen Dioxide | PP | Y | NA
2016 | 1379 | 0634005123 | Yoder Compressor Station | 79300 Cassville Rd | Cadiz | 43907 |  | Harrison | P002 | Natural gas-fired four-stroke lean burn (4SLB) internal combustion engine rated at an operating capacity of 2,370 horsepower (hp) and equipped with an oxidation catalyst. | 2016-05-19 | CC001(Catalytic Converter): Compressor Engine #1 Catalytic Converter; CC002(Catalytic Converter): Compressor Engine #2 Catalytic Converter; CC003(Catalytic Converter): Compressor Engine #3 Catalytic Converter | Air Hygiene International | 2370 hp | 2.61 lb/hr | 2202 hp | 2.03 lb/hr | 7E | Nitrogen Dioxide | PP | Y | NA
2016 | 1380 | 0634005123 | Yoder Compressor Station | 79300 Cassville Rd | Cadiz | 43907 |  | Harrison | P003 | Natural gas-fired four-stroke lean burn (4SLB) internal combustion engine rated at an operating capacity of 2,370 horsepower (hp) and equipped with an oxidation catalyst. | 2016-05-19 | CC001(Catalytic Converter): Compressor Engine #1 Catalytic Converter; CC002(Catalytic Converter): Compressor Engine #2 Catalytic Converter; CC003(Catalytic Converter): Compressor Engine #3 Catalytic Converter | Air Hygiene International | 2370 hp | 2.61 lb/hr | 2185 hp | 1.95 lb/hr | 7E | Nitrogen Dioxide | PP | Y | NA
2016 | 1387 | 0634005127 | Chesapeake Exploration LLC - Wright 35-11-5 Pad | Lightner House Rd | Scio | 43988 |  | Harrison | P002 | One or multiple stationary natural gas-fired spark ignition (SI) internal combustion engines (ICE) with a combined total horsepower (HP) of no more than 1,800 HP for the site.* Includes 2007 and later model year engines manufactured after the applicable | 2016-02-12 | catalyst | Alliance Source Testing | 211 hp | 2.0 g/hp-hr | 190 hp | 0.07 g/hp-hr | 7E | Nitrogen Dioxide | PP | Y | NA
2016 | 1440 | 0656005010 | Dominion East Ohio - Switzerland Compressor Station | German Ridge Road | Switzerland Twp. | 43942 |  | Monroe | P001 | 3550 Hp Natural gas-fired (4SLB) Caterpillar model 3612 LE DM5309-06 compressor engines equipped with catalytic reduction (three-way). | 2016-09-22 | catalyst | Environmental Quality management | 3,550 hp | 1.0 g/hp-hr | 3,307 hp | 0.52 g/hp-hr | 7E | Nitrogen Dioxide | PP | Y | NA
2016 | 1441 | 0656005010 | Dominion East Ohio - Switzerland Compressor Station | German Ridge Road | Switzerland Twp. | 43942 |  | Monroe | P002 | 3550 Hp Natural gas-fired (4SLB) Caterpillar model 3612 LE DM5309-06 compressor engines equipped with catalytic reduction (three-way). | 2016-09-22 | catalyst | Environmental Quality management | 3,550 hp | 1.0 g/hp-hr | 3,343 hp | 0.59 g/hp-hr | 7E | Nitrogen Dioxide | PP | Y | NA
2016 | 1442 | 0656005010 | Dominion East Ohio - Switzerland Compressor Station | German Ridge Road | Switzerland Twp. | 43942 |  | Monroe | P003 | 3550 Hp Natural gas-fired (4SLB) Caterpillar model 3612 LE DM5309-06 compressor engines equipped with catalytic reduction (three-way). | 2016-09-22 | catalyst | Environmental Quality management | 3,550 hp | 1.0 g/hp-hr | 3,361 hp | 0.47 g/hp-hr | 7E | Nitrogen Dioxide | PP | Y | NA
2016 | 1450 | 0656005011 | Ormet Production Facility | 43879 St Rte 7 | Hannibal | 43931 |  | Monroe | P006 | CAT 3508BLE SI combustion engine 690 bhp | 2016-07-28 | catalyst | EcoTest Energy Services | 690 hp | 0.50 g/hp-hr | 670 hp | 0.40 g/hp-hr | 320 | NOx - Nitrogen Oxides | PP | Y | NA
2016 | 1453 | 0656005011 | Ormet Production Facility | 43879 St Rte 7 | Hannibal | 43931 |  | Monroe | P001 | CAT 3516BLE SI combustion engine 1380 bhp | 2016-06-02 | CD-1(Catalytic Converter): Control Device for Compressor Engine-1 | EcoTest Energy Services | 1380 hp | 1.00 g/hp-hr | 850 hp | 0.48 g/hp-hr | 320 | NOx - Nitrogen Oxides | PP | Y | NA
2016 | 1455 | 0656005014 | StatOil USA Onshore Properties Inc - Dangle PAD | 49675 Dangel Lane | Sardis | 43946 |  | Monroe | P002 | One or multiple stationary natural gas-fired spark ignition (SI) internal combustion engines (ICE) with a combined total horsepower (HP) of no more than 1,800 HP for the site.* Includes 2007 and later model year engines manufactured after the applicable | 2016-02-23 | catalyst | Ecotest Energy Services | 1775 hp | 1.0 g/hp-hr | 1600 hp | 0.37 g/hp-hr | 320 | NOx - Nitrogen Oxides | PP | Y | NA
2016 | 1460 | 0656005017 | Triad Hunter, LLC, Stalder Pad | 49947 Twp 724 | Sardis | 43946 |  | Monroe | P002 | Natural Gas Engines | 2016-03-04 | C003(Catalytic Converter): Oxidation Catalyst | EcoTest Energy Services | 630 hp | 2.00 g/hp-hr | 590 hp | 1.52 g/hp-hr | 320 | NOx - Nitrogen Oxides | PP | Y | NA
2016 | 1461 | 0656005025 | REX Booster Station | Twp Rd 964 | Switzerland Twp. | 43915 |  | Monroe | P001 | Caterpillar 3616 Compressor Engine. This is a natural gas fired engine associated with the Compressor Unit | 2016-05-04 | C001(Catalytic Converter): Oxidation Catalysts; C002(Catalytic Converter): Oxidation Catalysts; C003(Catalytic Converter): Oxidation Catalysts | Alliance Source Testing | 4725hp | 5.22 lbs/hr | 4451 hp | 2.6 lbs/hr | 7E | Nitrogen Dioxide | PP | Y | NA
2016 | 1462 | 0656005025 | REX Booster Station | Twp Rd 964 | Switzerland Twp. | 43915 |  | Monroe | P002 | Caterpillar 3616 Compressor Engine. This is a natural gas fired engine associated with the Compressor Unit | 2016-05-04 | C001(Catalytic Converter): Oxidation Catalysts; C002(Catalytic Converter): Oxidation Catalysts; C003(Catalytic Converter): Oxidation Catalysts | Alliance Source Testing | 4725 hp | 5.22 lbs/hr | 4451 hp | 3.59 lbs/hr | 7E | Nitrogen Dioxide | PP | Y | NA
2016 | 1463 | 0656005025 | REX Booster Station | Twp Rd 964 | Switzerland Twp. | 43915 |  | Monroe | P003 | Caterpillar 3616 Compressor Engine. This is a natural gas fired engine associated with the Compressor Unit | 2016-05-04 | C001(Catalytic Converter): Oxidation Catalysts; C002(Catalytic Converter): Oxidation Catalysts; C003(Catalytic Converter): Oxidation Catalysts | Alliance Source Testing | 4725 hp | 5.22 lbs/hr | 4514 hp | 4.05 lbs/hr | 7E | Nitrogen Dioxide | PP | Y | NA
2016 | 1479 | 0656005028 | Miller Compressor Station | 51103 Twp Rd 847 | Seneca Twp. | 43788 |  | Monroe | P005 | Waukesha 1680 bhp Model L7044GSI 4-stroke Natural Gas Rich Burn Gas Compressor Engine Model Year 2014 controlled by a catalyst | 2016-02-05 | C-2705C(Catalytic Converter): Engine Catalyst | E2 Energy Services | 1680 hp | 0.25 g/hp-hr | 1542 hp | 2.40 g/hp-hr | 6348 03 | NOx - Nitrogen Oxides | FF | Y | NA
2016 | 1481 | 0656005028 | Miller Compressor Station | 51103 Twp Rd 847 | Seneca Twp. | 43788 |  | Monroe | P006 | Waukesha 1680 bhp Model L7044GSI 4-stroke Natural Gas Rich Burn Gas Compressor Engine Model Year 2014 controlled by a catalyst | 2016-01-29 | C-2706C(Catalytic Converter): Engine Catalyst | E2 Energy Services | 1680 hp | 0.25 g/hp-hr | 1545 hp | 1.15 g/hp-hr | 6348 03 | NOx - Nitrogen Oxides | FF | Y | NA
2016 | 1483 | 0656005028 | Miller Compressor Station | 51103 Twp Rd 847 | Seneca Twp. | 43788 |  | Monroe | P007 | Waukesha 1680 bhp Model L7044GSI 4-stroke Natural Gas Rich Burn Gas Compressor Engine Model Year 2014 controlled by a catalyst | 2016-01-27 | C-2707C(Catalytic Converter): Engine Catalyst | E2 Energy Services | 1680 hp | 0.25 g/hp-hr | 1542 hp | 0.18 g/hp-hr | 6348 03 | NOx - Nitrogen Oxides | PP | Y | NA
2016 | 1486 | 0656005028 | Miller Compressor Station | 51103 Twp Rd 847 | Seneca Twp. | 43788 |  | Monroe | P008 | Waukesha 1680 bhp Model L7044GSI 4-stroke Natural Gas Rich Burn Gas Compressor Engine Model Year 2014 controlled by a catalyst | 2016-01-21 | C-2708C(Catalytic Converter): Engine Catalyst | E2 Energy Services | 1680 hp | 0.25 g/hp-hr | 1510 hp | 0.42 g/hp-hr | 6348 03 | NOx - Nitrogen Oxides | FF | Y | NA
2016 | 1490 | 0656005028 | Miller Compressor Station | 51103 Twp Rd 847 | Seneca Twp. | 43788 |  | Monroe | P009 | Waukesha 1680 bhp Model L7044GSI 4-stroke Natural Gas Rich Burn Gas Compressor Engine Model Year 2014 controlled by a catalyst | 2016-01-22 | C-2709C(Catalytic Converter): Engine Catalyst | E2 Energy Services | 1680 hp | 0.25 g/hp-hr | 1477 hp | 0.80 g/hp-hr | 6348 03 | NOx - Nitrogen Oxides | FF | Y | NA
2016 | 1492 | 0656005028 | Miller Compressor Station | 51103 Twp Rd 847 | Seneca Twp. | 43788 |  | Monroe | P001 | Waukesha 1680 bhp Model L7044GSI 4-stroke Natural Gas Rich Burn Gas Compressor Engine Model Year 2014 controlled by a catalyst | 2016-06-22 | C-2701C(Catalytic Converter): Engine Catalyst; C-2702C(Catalytic Converter): Engine Catalyst; C-2703C(Catalytic Converter): Engine Catalyst; C-2704C(Catalytic Converter): Engine Catalyst; C-2705C(Catalytic Converter): Engine Catalyst; C-2706C(Catalytic Co | Alliance Source Testing | 1680 hp | 0.25 g/hp-hr | 1680 hp | 0.06 g/hp-hr | 7E | Nitrogen Dioxide | PP | N | NA
2016 | 1493 | 0656005028 | Miller Compressor Station | 51103 Twp Rd 847 | Seneca Twp. | 43788 |  | Monroe | P002 | Waukesha 1680 bhp Model L7044GSI 4-stroke Natural Gas Rich Burn Gas Compressor Engine Model Year 2014 controlled by a catalyst | 2016-06-22 | C-2701C(Catalytic Converter): Engine Catalyst; C-2702C(Catalytic Converter): Engine Catalyst; C-2703C(Catalytic Converter): Engine Catalyst; C-2704C(Catalytic Converter): Engine Catalyst; C-2705C(Catalytic Converter): Engine Catalyst; C-2706C(Catalytic Co | Alliance Source Testing | 1680 hp | 0.25 g/hp-hr | 1680 hp | 0.15 g/hp-hr | 7E | Nitrogen Dioxide | PP | N | NA
2016 | 1494 | 0656005028 | Miller Compressor Station | 51103 Twp Rd 847 | Seneca Twp. | 43788 |  | Monroe | P003 | Waukesha 1680 bhp Model L7044GSI 4-stroke Natural Gas Rich Burn Gas Compressor Engine Model Year 2014 controlled by a catalyst | 2016-06-22 | C-2701C(Catalytic Converter): Engine Catalyst; C-2702C(Catalytic Converter): Engine Catalyst; C-2703C(Catalytic Converter): Engine Catalyst; C-2704C(Catalytic Converter): Engine Catalyst; C-2705C(Catalytic Converter): Engine Catalyst; C-2706C(Catalytic Co | Alliance Source Testing | 1680 hp | 0.25 g/hp-hr | 1680 hp | 0.06 g/hp-hr | 7E | Nitrogen Dioxide | PP | N | NA
2016 | 1495 | 0656005028 | Miller Compressor Station | 51103 Twp Rd 847 | Seneca Twp. | 43788 |  | Monroe | P004 | Waukesha 1680 bhp Model L7044GSI 4-stroke Natural Gas Rich Burn Gas Compressor Engine Model Year 2014 controlled by a catalyst | 2016-06-22 | C-2701C(Catalytic Converter): Engine Catalyst; C-2702C(Catalytic Converter): Engine Catalyst; C-2703C(Catalytic Converter): Engine Catalyst; C-2704C(Catalytic Converter): Engine Catalyst; C-2705C(Catalytic Converter): Engine Catalyst; C-2706C(Catalytic Co | Alliance Source Testing | 1680 hp | 0.25 g/hp-hr | 1680 hp | 0.04 g/hp-hr | 7E | Nitrogen Dioxide | PP | N | NA
2016 | 1496 | 0656005028 | Miller Compressor Station | 51103 Twp Rd 847 | Seneca Twp. | 43788 |  | Monroe | P005 | Waukesha 1680 bhp Model L7044GSI 4-stroke Natural Gas Rich Burn Gas Compressor Engine Model Year 2014 controlled by a catalyst | 2016-06-22 | C-2701C(Catalytic Converter): Engine Catalyst; C-2702C(Catalytic Converter): Engine Catalyst; C-2703C(Catalytic Converter): Engine Catalyst; C-2704C(Catalytic Converter): Engine Catalyst; C-2705C(Catalytic Converter): Engine Catalyst; C-2706C(Catalytic Co | Alliance Source Testing | 1680 hp | 0.25 g/hp-hr | 1680 hp | 0.05 g/hp-hr | 7E | Nitrogen Dioxide | PP | N | NA
2016 | 1497 | 0656005028 | Miller Compressor Station | 51103 Twp Rd 847 | Seneca Twp. | 43788 |  | Monroe | P006 | Waukesha 1680 bhp Model L7044GSI 4-stroke Natural Gas Rich Burn Gas Compressor Engine Model Year 2014 controlled by a catalyst | 2016-06-22 | C-2701C(Catalytic Converter): Engine Catalyst; C-2702C(Catalytic Converter): Engine Catalyst; C-2703C(Catalytic Converter): Engine Catalyst; C-2704C(Catalytic Converter): Engine Catalyst; C-2705C(Catalytic Converter): Engine Catalyst; C-2706C(Catalytic Co | Alliance Source Testing | 1680 hp | 0.25 g/hp-hr | 1680 hp | 0.06 g/hp-hr | 7E | Nitrogen Dioxide | PP | N | NA
2016 | 1498 | 0656005028 | Miller Compressor Station | 51103 Twp Rd 847 | Seneca Twp. | 43788 |  | Monroe | P007 | Waukesha 1680 bhp Model L7044GSI 4-stroke Natural Gas Rich Burn Gas Compressor Engine Model Year 2014 controlled by a catalyst | 2016-06-22 | C-2701C(Catalytic Converter): Engine Catalyst; C-2702C(Catalytic Converter): Engine Catalyst; C-2703C(Catalytic Converter): Engine Catalyst; C-2704C(Catalytic Converter): Engine Catalyst; C-2705C(Catalytic Converter): Engine Catalyst; C-2706C(Catalytic Co | Alliance Source Testing | 1680 hp | 0.25 g/hp-hr | 1680 hp | 0.07 g/hp-hr | 7E | Nitrogen Dioxide | PP | N | NA
2016 | 1499 | 0656005028 | Miller Compressor Station | 51103 Twp Rd 847 | Seneca Twp. | 43788 |  | Monroe | P008 | Waukesha 1680 bhp Model L7044GSI 4-stroke Natural Gas Rich Burn Gas Compressor Engine Model Year 2014 controlled by a catalyst | 2016-06-22 | C-2701C(Catalytic Converter): Engine Catalyst; C-2702C(Catalytic Converter): Engine Catalyst; C-2703C(Catalytic Converter): Engine Catalyst; C-2704C(Catalytic Converter): Engine Catalyst; C-2705C(Catalytic Converter): Engine Catalyst; C-2706C(Catalytic Co | Alliance Source Testing | 1680 hp | 0.25 g/hp-hr | 1680 hp | 0.08 g/hp-hr | 7E | Nitrogen Dioxide | PP | N | NA
2016 | 1500 | 0656005028 | Miller Compressor Station | 51103 Twp Rd 847 | Seneca Twp. | 43788 |  | Monroe | P009 | Waukesha 1680 bhp Model L7044GSI 4-stroke Natural Gas Rich Burn Gas Compressor Engine Model Year 2014 controlled by a catalyst | 2016-06-22 | C-2701C(Catalytic Converter): Engine Catalyst; C-2702C(Catalytic Converter): Engine Catalyst; C-2703C(Catalytic Converter): Engine Catalyst; C-2704C(Catalytic Converter): Engine Catalyst; C-2705C(Catalytic Converter): Engine Catalyst; C-2706C(Catalytic Co | Alliance Source Testing | 1680 hp | 0.25 g/hp-hr | 1680 hp | 0.14 g/hp-hr | 7E | Nitrogen Dioxide | PP | N | NA
2016 | 1519 | 0656025005 | Gulfport Energy - Campbell | Seal Road | Beallsville | 43716 |  | Monroe | P002 | One or multiple stationary natural gas-fired spark ignition (SI) internal combustion engines (ICE) with a combined total horsepower (HP) of no more than 1,800 HP for the site.* Includes 2007 and later model year engines manufactured after the applicable | 2016-09-27 | catalyst | Ecotest | 1,775 hp | 1.45 g/hp-hr | 1,500 hp | 0.49 g/hp-hr | 7E | Nitrogen Dioxide | PP | Y | NA
2016 | 1522 | 0656025008 | Gulfport Energy - Howell | Twp Hwy 145 | Beallsville | 43716 |  | Monroe | P002 | One or multiple stationary natural gas-fired spark ignition (SI) internal combustion engines (ICE) with a combined total horsepower (HP) of no more than 1,800 HP for the site.* Includes 2007 and later model year engines manufactured after the applicable | 2016-09-27 | catalyst | Ecotest | 1,775 hp | 1.45 g/hp-hr | 1,500 hp | 0.63 g/hp-hr | 7E | Nitrogen Dioxide | PP | Y | NA
2016 | 1527 | 0656025012 | Goliath Compressor Station | 48208 St Rte 556 | Beallsville | 43716 |  | Monroe | P001 | Compressor #1 - driven by Caterpillar G3608 engine | 2016-01-13 | C301Catalyst(Other): null | Technical Compliance Solutions | 2370 hp | 0.5 g/hp-hr | 1497 hp | 0.48 g/hp-hr | 320 | NOx - Nitrogen Oxides | PP | Y | NA
2016 | 1530 | 0656025012 | Goliath Compressor Station | 48208 St Rte 556 | Beallsville | 43716 |  | Monroe | P002 | Compressor #2 - driven by Caterpillar G3608 engine | 2016-01-13 | C302Catalyst(Other): null | Technical Compliance Solutions | 2370 hp | 0.5 g/hp-hr | 1501 hp | 0.38 g/hp-hr | 320 | NOx - Nitrogen Oxides | PP | Y | NA
2016 | 1534 | 0656025012 | Goliath Compressor Station | 48208 St Rte 556 | Beallsville | 43716 |  | Monroe | P003 | Compressor #3 - driven by Caterpillar G3608 engine | 2016-01-14 | C303Catalyst(Other): | Technical Compliance Solutions | 2370 hp | 0.5 g/hp-hr | 1523 hp | 0.35 g/hp-hr | 320 | NOx - Nitrogen Oxides | PP | Y | NA
2016 | 1539 | 0656025012 | Goliath Compressor Station | 48208 St Rte 556 | Beallsville | 43716 |  | Monroe | P004 | Compressor #4 - driven by Caterpillar G3608 engine | 2016-01-13 | C304Catalyst(Other): null | Technical Compliance Solutions | 2370 hp | 0.5 g/hp-hr | 1501 hp | 0.47 g/hp-hr | 320 | NOx - Nitrogen Oxides | PP | Y | NA
2016 | 1542 | 0656025012 | Goliath Compressor Station | 48208 St Rte 556 | Beallsville | 43716 |  | Monroe | P005 | Compressor #5 - driven by Caterpillar G3608 engine | 2016-01-13 | C305Catalyst(Other): null | Technical Compliance Solutions | 2370 hp | 0.5 g/hp-hr | 1497 hp | 0.43 g/hp/hr | 320 | NOx - Nitrogen Oxides | PP | Y | NA
2016 | 1546 | 0656035009 | Eureka Midstream-Zink Compressor Station | 51213 Krebs Hill Rd | Clarington | 43915 |  | Monroe | P006 | Natural Gas Fueled Lean Burn 4-Stroke Caterpillar G3608TALE Compressor Engine | 2016-04-12 | catalyst | EcoTest Energy Services | 2370 hp | 0.50 g/hp-hr | 2150 hp | 0.20 g/hp-hr | 320 | NOx - Nitrogen Oxides | PP | Y | NA | P006 serial number BEN00694 P007 serial number BEN00693
2016 | 1548 | 0656035009 | Eureka Midstream-Zink Compressor Station | 51213 Krebs Hill Rd | Clarington | 43915 |  | Monroe | P007 | Natural Gas Fueled Lean Burn 4-Stroke Caterpillar G3608TALE Compressor Engine | 2016-04-12 | catalyst | EcoTest Energy Services | 2370 hp | 0.50 g/hp-hr | 2150 hp | 0.18 g/hp-hr | 320 | NOx - Nitrogen Oxides | PP | Y | NA | P006 serial number BEN00694 P007 serial number BEN00693
2016 | 1552 | 0656035012 | CNX Gas LLC - Switz 6 Production Facility | 49498 SR 556 | Clarington | 43915 |  | Monroe | P002 | NOT INSTALLED AT PERMIT ISSUANCE TIME NG engine | 2016-05-16 | catalyst | Ecotest Energy Services | 68 hp, 276 hp 425 hp | 2.0 g/hp-hr | 35 hp, 102 hp, 188 hp | 2.0 g/hp-hr | 320 | NOx - Nitrogen Oxides | PP | Y | NA | 425 hp engine, 276 hp and 68 hp engine combined allowable for P002
2016 | 1556 | 0656035012 | CNX Gas LLC - Switz 6 Production Facility | 49498 SR 556 | Clarington | 43915 |  | Monroe | P002 | NOT INSTALLED AT PERMIT ISSUANCE TIME NG engine | 2016-06-01 | catalyst | Ecotest Energy Services | 68 hp, 276 hp 425 hp | 2.0 g/hp-hr | 35 hp, 102 hp, 188 hp | 2.0 g/hp-hr | 320 | NOx - Nitrogen Oxides | PP | Y | NA | 425 hp engine, 276 hp and 68 hp engine combined allowable for P002
2016 | 1559 | 0656065002 | Antero Resources- Webb Pad | 42006 Sandbar Rd | Lewisville | 43754 |  | Monroe | P002 | One or multiple stationary natural gas-fired spark ignition (SI) internal combustion engines (ICE) with a combined total horsepower (HP) of no more than 1,800 HP for the site.* Includes 2007 and later model year engines manufactured after the applicable | 2016-02-05 | catalyst | Techhical Compliance Solutions | 400 hp | 2.0 g/hp-hr | 379 hp | 0.36 g/hp-hr | 320 | NOx - Nitrogen Oxides | PP | N | NA
2016 | 1560 | 0656065006 | Antero Resources - Hercher Pad | 39886 Township Rd | Lewisville | 43754 |  | Monroe | P002 | One or multiple stationary natural gas-fired spark ignition (SI) internal combustion engines (ICE) with a combined total horsepower (HP) of no more than 1,800 HP for the site.* Includes 2007 and later model year engines manufactured after the applicable | 2016-02-05 | catalyst | Technical Compliance Solutions | 1,775 hp | 1.45 g/hp-hr | 1,605 hp | 0.30 g/hp-hr | 320 | NOx - Nitrogen Oxides | PP | Y | NA
2016 | 1564 | 0656105005 | E2 Appalachian Compression LLC - Reusser | Twp Hwy 68 and Twp Hwy 66 | Woodsfield | 43793 |  | Monroe | P001 | 1680 Hp. natural gas rich burn compressor engine - Waukesha L7044GSI | 2016-03-18 | C-1(Catalytic Converter): Engine Catalyst | E2 Energy Services | 1680 hp | 0.99 lb/hr | 1538 hp | 2.10 lb/hr | 6348 03 | NOx - Nitrogen Oxides | FF | Y | NA
2016 | 1567 | 0656105005 | E2 Appalachian Compression LLC - Reusser | Twp Hwy 68 and Twp Hwy 66 | Woodsfield | 43793 |  | Monroe | P004 | 1680 Hp. natural gas rich burn compressor engine - Waukesha L7044GSI | 2016-03-09 | C-4(Catalytic Converter): Engine #4 Catalyst | E2 Energy Services | 1680 hp | 0.99 lb/hr | 1481 hp | 0.08 lb/hr | 6348 03 | NOx - Nitrogen Oxides | PP | Y | NA
2016 | 1570 | 0656105005 | E2 Appalachian Compression LLC - Reusser | Twp Hwy 68 and Twp Hwy 66 | Woodsfield | 43793 |  | Monroe | P005 | 1680 Hp. natural gas rich burn compressor engine - Waukesha L7044GSI | 2016-03-10 | C-5(Catalytic Converter): Engine #5 Catalyst | E2 Energy Services | 1680 hp | 0.99 lb/hr | 1479 hp | 0.18 lb/hr | 6348 03 | NOx - Nitrogen Oxides | PP | Y | NA
2016 | 1574 | 0656105005 | E2 Appalachian Compression LLC - Reusser | Twp Hwy 68 and Twp Hwy 66 | Woodsfield | 43793 |  | Monroe | P006 | 1680 Hp. natural gas rich burn compressor engine - Waukesha L7044GSI | 2016-03-10 | C-6(Catalytic Converter): Engine #6Catalyst | E2 Energy Services | 1680 hp | 0.99 lb/hr | 1592 hp | 0.29 lb/hr | 6348 03 | NOx - Nitrogen Oxides | PP | Y | NA
2016 | 1576 | 0656105005 | E2 Appalachian Compression LLC - Reusser | Twp Hwy 68 and Twp Hwy 66 | Woodsfield | 43793 |  | Monroe | P007 | 1680 Hp. natural gas rich burn compressor engine - Waukesha L7044GSI | 2016-03-18 | C-7(Catalytic Converter): Engine #7Catalyst | E2 Energy Services | 1680 hp | 0.99 lb/hr | 1535 hp | 0.02 l/bhr | 6348 03 | NOx - Nitrogen Oxides | PP | Y | NA
2016 | 1579 | 0656105005 | E2 Appalachian Compression LLC - Reusser | Twp Hwy 68 and Twp Hwy 66 | Woodsfield | 43793 |  | Monroe | P008 | 1680 Hp. natural gas rich burn compressor engine - Waukesha L7044GSI | 2016-03-11 | C-7(Catalytic Converter): Engine #7Catalyst | E2 Energy Services | 1680 hp | 0.99 lb/hr | 1548 hp | 0.16 lb/hr | 6348 03 | NOx - Nitrogen Oxides | PP | Y | NA
2016 | 1581 | 0656105005 | E2 Appalachian Compression LLC - Reusser | Twp Hwy 68 and Twp Hwy 66 | Woodsfield | 43793 |  | Monroe | P001 | 1680 Hp. natural gas rich burn compressor engine - Waukesha L7044GSI | 2016-07-14 | C-1(Catalytic Converter): Engine Catalyst; C-2(Catalytic Converter): Engine Catalyst; C-3(Catalytic Converter): Engine #3 Catalyst; C-4(Catalytic Converter): Engine #4 Catalyst; C-5(Catalytic Converter): Engine #5 Catalyst; C-6(Catalytic Converter): Engin | Alliance Source Testing | 1680 hp | 0.99 lb/hr | 1646 hp | 0.72 lb/hr | 7E | Nitrogen Dioxide | PP | Y | NA
2016 | 1582 | 0656105005 | E2 Appalachian Compression LLC - Reusser | Twp Hwy 68 and Twp Hwy 66 | Woodsfield | 43793 |  | Monroe | P002 | 1680 Hp. natural gas rich burn compressor engine - Waukesha L7044GSI | 2016-07-14 | C-1(Catalytic Converter): Engine Catalyst; C-2(Catalytic Converter): Engine Catalyst; C-3(Catalytic Converter): Engine #3 Catalyst; C-4(Catalytic Converter): Engine #4 Catalyst; C-5(Catalytic Converter): Engine #5 Catalyst; C-6(Catalytic Converter): Engin | Alliance Source Testing | 1680 hp | 0.99 lb/hr | 1457 hp | 0.82 lb/hr | 7E | Nitrogen Dioxide | PP | Y | NA
2016 | 1583 | 0656105005 | E2 Appalachian Compression LLC - Reusser | Twp Hwy 68 and Twp Hwy 66 | Woodsfield | 43793 |  | Monroe | P003 | 1680 Hp. natural gas rich burn compressor engine - Waukesha L7044GSI | 2016-07-14 | C-1(Catalytic Converter): Engine Catalyst; C-2(Catalytic Converter): Engine Catalyst; C-3(Catalytic Converter): Engine #3 Catalyst; C-4(Catalytic Converter): Engine #4 Catalyst; C-5(Catalytic Converter): Engine #5 Catalyst; C-6(Catalytic Converter): Engin | Alliance Source Testing | 1680 hp | 0.99 lb/hr | 1658 hp | 0.89 lb/hr | 7E | Nitrogen Dioxide | PP | Y | NA
2016 | 1584 | 0656105005 | E2 Appalachian Compression LLC - Reusser | Twp Hwy 68 and Twp Hwy 66 | Woodsfield | 43793 |  | Monroe | P004 | 1680 Hp. natural gas rich burn compressor engine - Waukesha L7044GSI | 2016-07-14 | C-1(Catalytic Converter): Engine Catalyst; C-2(Catalytic Converter): Engine Catalyst; C-3(Catalytic Converter): Engine #3 Catalyst; C-4(Catalytic Converter): Engine #4 Catalyst; C-5(Catalytic Converter): Engine #5 Catalyst; C-6(Catalytic Converter): Engin | Alliance Source Testing | 1680 hp | 0.99 lb/hr | 1680 hp | 0.006 lb/hr | 7E | Nitrogen Dioxide | PP | Y | NA
2016 | 1585 | 0656105005 | E2 Appalachian Compression LLC - Reusser | Twp Hwy 68 and Twp Hwy 66 | Woodsfield | 43793 |  | Monroe | P005 | 1680 Hp. natural gas rich burn compressor engine - Waukesha L7044GSI | 2016-07-14 | C-1(Catalytic Converter): Engine Catalyst; C-2(Catalytic Converter): Engine Catalyst; C-3(Catalytic Converter): Engine #3 Catalyst; C-4(Catalytic Converter): Engine #4 Catalyst; C-5(Catalytic Converter): Engine #5 Catalyst; C-6(Catalytic Converter): Engin | Alliance Source Testing | 1680 hp | 0.99 lb/hr | 1613 hp | 0.44 lb/hr | 7E | Nitrogen Dioxide | PP | Y | NA
2016 | 1586 | 0656105005 | E2 Appalachian Compression LLC - Reusser | Twp Hwy 68 and Twp Hwy 66 | Woodsfield | 43793 |  | Monroe | P006 | 1680 Hp. natural gas rich burn compressor engine - Waukesha L7044GSI | 2016-07-14 | C-1(Catalytic Converter): Engine Catalyst; C-2(Catalytic Converter): Engine Catalyst; C-3(Catalytic Converter): Engine #3 Catalyst; C-4(Catalytic Converter): Engine #4 Catalyst; C-5(Catalytic Converter): Engine #5 Catalyst; C-6(Catalytic Converter): Engin | Alliance Source Testing | 1680 hp | 0.99 lb/hr | 1646 hp | 0.38 lb/hr | 7E | Nitrogen Dioxide | PP | Y | NA
2016 | 1587 | 0656105005 | E2 Appalachian Compression LLC - Reusser | Twp Hwy 68 and Twp Hwy 66 | Woodsfield | 43793 |  | Monroe | P007 | 1680 Hp. natural gas rich burn compressor engine - Waukesha L7044GSI | 2016-07-14 | C-1(Catalytic Converter): Engine Catalyst; C-2(Catalytic Converter): Engine Catalyst; C-3(Catalytic Converter): Engine #3 Catalyst; C-4(Catalytic Converter): Engine #4 Catalyst; C-5(Catalytic Converter): Engine #5 Catalyst; C-6(Catalytic Converter): Engin | Alliance Source Testing | 1680 hp | 0.99 lb/hr | 1680 hp | 0.001 lb/hr | 7E | Nitrogen Dioxide | PP | Y | NA
2016 | 1588 | 0656105005 | E2 Appalachian Compression LLC - Reusser | Twp Hwy 68 and Twp Hwy 66 | Woodsfield | 43793 |  | Monroe | P008 | 1680 Hp. natural gas rich burn compressor engine - Waukesha L7044GSI | 2016-07-14 | C-1(Catalytic Converter): Engine Catalyst; C-2(Catalytic Converter): Engine Catalyst; C-3(Catalytic Converter): Engine #3 Catalyst; C-4(Catalytic Converter): Engine #4 Catalyst; C-5(Catalytic Converter): Engine #5 Catalyst; C-6(Catalytic Converter): Engin | Alliance Source Testing | 1680 hp | 0.99 lb/hr | 1680 hp | 0.14 lb/hr | 7E | Nitrogen Dioxide | PP | Y | NA
2016 | 1589 | 0656105005 | E2 Appalachian Compression LLC - Reusser | Twp Hwy 68 and Twp Hwy 66 | Woodsfield | 43793 |  | Monroe | P009 | 1680 Hp. natural gas rich burn compressor engine - Waukesha L7044GSI | 2016-07-14 | C-1(Catalytic Converter): Engine Catalyst; C-2(Catalytic Converter): Engine Catalyst; C-3(Catalytic Converter): Engine #3 Catalyst; C-4(Catalytic Converter): Engine #4 Catalyst; C-5(Catalytic Converter): Engine #5 Catalyst; C-6(Catalytic Converter): Engin | Alliance Source Testing | 1680 hp | 0.99 lb/hr | 1404 hp | 0.49 lb/hr | 7E | Nitrogen Dioxide | PP | Y | NA
2016 | 1603 | 0661005010 | E2 Appalachian Compression LLC - Upper Hill | Opossum Run Rd and Town Hwy 120 | Sarahsville | 43779 |  | Noble | P003 | 1,680 Hp. Waukesha (L7044GSI) natural gas-fired, rich burn, turbocharged, with oxidation catalyst, compressor engine. | 2016-04-29 | C-3(Catalytic Converter): Engine Catalyst; C-9(Catalytic Converter): Engine Catalyst | Alliance Source Testing | 1680 hp | 2.0 g/hp-hr | 1658 hp | 3.19 g/hp-hr | 7E | Nitrogen Dioxide | FF | Y | NA
2016 | 1604 | 0661005010 | E2 Appalachian Compression LLC - Upper Hill | Opossum Run Rd and Town Hwy 120 | Sarahsville | 43779 |  | Noble | P009 | 1,680 Hp. Waukesha (L7044GSI) natural gas-fired, rich burn, turbocharged, with oxidation catalyst, compressor engine. | 2016-04-29 | C-3(Catalytic Converter): Engine Catalyst; C-9(Catalytic Converter): Engine Catalyst | Alliance Source Testing | 1680 hp | 2.0 g/hp-hr | 1646 hp | 0.15 g/hp-hr | 7E | Nitrogen Dioxide | PP | Y | NA
2016 | 1609 | 0661005010 | E2 Appalachian Compression LLC - Upper Hill | Opossum Run Rd and Town Hwy 120 | Sarahsville | 43779 |  | Noble | P007 | 1,680 Hp. Waukesha (L7044GSI) natural gas-fired, rich burn, turbocharged, with oxidation catalyst, compressor engine. | 2016-03-17 | C-7(Catalytic Converter): Engine Catalyst; C-8(Catalytic Converter): Engine Catalyst | Alliance Source Testing | 1680 hp | 2.0 g/hp-hr | 1464 hp | 0.22 g/hp-hr | 7E | Nitrogen Dioxide | PP | Y | NA
2016 | 1610 | 0661005010 | E2 Appalachian Compression LLC - Upper Hill | Opossum Run Rd and Town Hwy 120 | Sarahsville | 43779 |  | Noble | P008 | 1,680 Hp. Waukesha (L7044GSI) natural gas-fired, rich burn, turbocharged, with oxidation catalyst, compressor engine. | 2016-03-17 | C-7(Catalytic Converter): Engine Catalyst; C-8(Catalytic Converter): Engine Catalyst | Alliance Source Testing | 1680 hp | 2.0 g/hp-hr | 1406 hp | 0.42 g/hp-hr | 7E | Nitrogen Dioxide | PP | Y | NA
2016 | 1615 | 0661005010 | E2 Appalachian Compression LLC - Upper Hill | Opossum Run Rd and Town Hwy 120 | Sarahsville | 43779 |  | Noble | P003 | 1,680 Hp. Waukesha (L7044GSI) natural gas-fired, rich burn, turbocharged, with oxidation catalyst, compressor engine. | 2016-04-29 | C-3(Catalytic Converter): Engine Catalyst; C-9(Catalytic Converter): Engine Catalyst | Ecotest Energy Services | 1680 hp | 2.0 g/hp-hr | 1658 hp | 3.19 g/hp-hr | 6348 03 | NOx - Nitrogen Oxides | FF | Y | NA
2016 | 1620 | 0661005010 | E2 Appalachian Compression LLC - Upper Hill | Opossum Run Rd and Town Hwy 120 | Sarahsville | 43779 |  | Noble | P009 | 1,680 Hp. Waukesha (L7044GSI) natural gas-fired, rich burn, turbocharged, with oxidation catalyst, compressor engine. | 2016-04-29 | C-3(Catalytic Converter): Engine Catalyst; C-9(Catalytic Converter): Engine Catalyst | Ecotest Energy Services | 1680 hp | 2.0 g/hp-hr | 1646 hp | 0.15 g/hp-hr | 6348 03 | NOx - Nitrogen Oxides | PP | Y | NA
2016 | 1621 | 0661005010 | E2 Appalachian Compression LLC - Upper Hill | Opossum Run Rd and Town Hwy 120 | Sarahsville | 43779 |  | Noble | P002 | 1,680 Hp. Waukesha (L7044GSI) natural gas-fired, rich burn, turbocharged, with oxidation catalyst, compressor engine. | 2016-07-13 | C-2(Catalytic Converter): Engine Catalyst; C-8(Catalytic Converter): Engine Catalyst | Alliance Source Testing | 1,680 hp | 160 ppm | 1,529 hp | 7.0 ppm | 7E | Nitrogen Dioxide | PP | Y | NA
2016 | 1622 | 0661005010 | E2 Appalachian Compression LLC - Upper Hill | Opossum Run Rd and Town Hwy 120 | Sarahsville | 43779 |  | Noble | P008 | 1,680 Hp. Waukesha (L7044GSI) natural gas-fired, rich burn, turbocharged, with oxidation catalyst, compressor engine. | 2016-07-13 | C-2(Catalytic Converter): Engine Catalyst; C-8(Catalytic Converter): Engine Catalyst | Alliance Source Testing | 1,680 hp | 160 ppm | 1,528 hp | 4.3 ppm | 7E | Nitrogen Dioxide | PP | Y | NA
2016 | 1629 | 0661005027 | E2 Appalachian LLC - Batesville | 58380 St John Rd | Quaker City | 43773 |  | Noble | P001 | 1,680 Hp. Waukesha (L7044GSI) natural gas-fired, rich burn, turbocharged, with oxidation catalyst, compressor engine | 2016-04-13 | C2701C(Catalytic Converter): Engine Catalyst | E2 Appalachian | 1680 hp | 1.0 g/hp-hr | 1539 hp | 0.278 g/hp-hr | 6348 03 | NOx - Nitrogen Oxides | PP | Y | NA
2016 | 1631 | 0661005027 | E2 Appalachian LLC - Batesville | 58380 St John Rd | Quaker City | 43773 |  | Noble | P002 | 1,680 Hp. Waukesha (L7044GSI) natural gas-fired, rich burn, turbocharged, with oxidation catalyst, compressor engine | 2016-03-24 | C2702C(Catalytic Converter): Engine Catalyst | E2 Appalachian | 1680 hp | 1.0 g/hp-hr | 1473 hp | 0.1360 g/hp-hr | 6348 03 | NOx - Nitrogen Oxides | PP | Y | NA
2016 | 1634 | 0661005027 | E2 Appalachian LLC - Batesville | 58380 St John Rd | Quaker City | 43773 |  | Noble | P003 | 1,680 Hp. Waukesha (L7044GSI) natural gas-fired, rich burn, turbocharged, with oxidation catalyst, compressor engine | 2016-03-23 | C2703C(Catalytic Converter): Engine Catalyst | E2 Appalachian | 1680 hp | 1.0 g/hp-hr | 1348 hp | 0.0882 g/hp-hr | 6348 03 | NOx - Nitrogen Oxides | PP | Y | NA
2016 | 1638 | 0661005027 | E2 Appalachian LLC - Batesville | 58380 St John Rd | Quaker City | 43773 |  | Noble | P004 | 1,680 Hp. Waukesha (L7044GSI) natural gas-fired, rich burn, turbocharged, with oxidation catalyst, compressor engine | 2016-03-30 | C2704C(Catalytic Converter): Engine Catalyst | E2 Appalachian | 1680 hp | 1.0 g/hp-hr | 1470 hp | 0.1056 g/hp-hr | 6348 03 | NOx - Nitrogen Oxides | PP | Y | NA
2016 | 1639 | 0661005027 | E2 Appalachian LLC - Batesville | 58380 St John Rd | Quaker City | 43773 |  | Noble | P005 | 1,680 Hp. Waukesha (L7044GSI) natural gas-fired, rich burn, turbocharged, with oxidation catalyst, compressor engine | 2016-03-31 | C2705C(Catalytic Converter): Engine Catalyst | E2 Appalachian | 1680 hp | 1.0 g/hp-hr | 1425 hp | 0.1406 g/hp-hr | 6348 03 | NOx - Nitrogen Oxides | PP | Y | NA
2016 | 1643 | 0661005027 | E2 Appalachian LLC - Batesville | 58380 St John Rd | Quaker City | 43773 |  | Noble | P006 | 1,680 Hp. Waukesha (L7044GSI) natural gas-fired, rich burn, turbocharged, with oxidation catalyst, compressor engine | 2016-04-01 | C2705C(Catalytic Converter): Engine Catalyst | E2 Appalachian | 1680 hp | 0.268 g/hp-hr | 1551 hp | 0.3119 g/hp-hr | 6348 03 | NOx - Nitrogen Oxides | FF | Y | NA
2016 | 1645 | 0661005027 | E2 Appalachian LLC - Batesville | 58380 St John Rd | Quaker City | 43773 |  | Noble | P008 | 1,680 Hp. Waukesha (L7044GSI) natural gas-fired, rich burn, turbocharged, with oxidation catalyst, compressor engine | 2016-04-14 | C2708C(Catalytic Converter): Engine Catalyst | E2 Appalachian | 1680 hp | 1.0 g/hp-hr | 1475 hp | 0.1731 g/hp-hr | 6348 03 | NOx - Nitrogen Oxides | PP | Y | NA
2016 | 1649 | 0661005027 | E2 Appalachian LLC - Batesville | 58380 St John Rd | Quaker City | 43773 |  | Noble | P002 | 1,680 Hp. Waukesha (L7044GSI) natural gas-fired, rich burn, turbocharged, with oxidation catalyst, compressor engine | 2016-04-14 | C2702C(Catalytic Converter): Engine Catalyst | E2 Energy Services | 1680 hp | 1.0 g/hp-hr | 1473 hp | 0.122 g/hp-hr | 6348 03 | NOx - Nitrogen Oxides | PP | N | NA
2016 | 1651 | 0661005027 | E2 Appalachian LLC - Batesville | 58380 St John Rd | Quaker City | 43773 |  | Noble | P002 | 1,680 Hp. Waukesha (L7044GSI) natural gas-fired, rich burn, turbocharged, with oxidation catalyst, compressor engine | 2016-04-28 | C2702C(Catalytic Converter): Engine Catalyst | Alliance Source Testing | 1680 hp | 1.0 g/hp-hr | 1529 hp | 0.129 g/hp-hr | 7E | Nitrogen Dioxide | PP | N | NA
2016 | 1654 | 0661005027 | E2 Appalachian LLC - Batesville | 58380 St John Rd | Quaker City | 43773 |  | Noble | P001 | 1,680 Hp. Waukesha (L7044GSI) natural gas-fired, rich burn, turbocharged, with oxidation catalyst, compressor engine | 2016-07-11 | C2701C(Catalytic Converter): Engine Catalyst; C2707C(Catalytic Converter): Engine Catalyst; C2708C(Catalytic Converter): Engine Catalyst | Alliance Source Testing | 1,680 hp | 1.0 g/hp-hr | 1,529 hp | 0 g/hp-hr | 7E | Nitrogen Dioxide | PP | Y | NA
2016 | 1655 | 0661005027 | E2 Appalachian LLC - Batesville | 58380 St John Rd | Quaker City | 43773 |  | Noble | P007 | 1,680 Hp. Waukesha (L7044GSI) natural gas-fired, rich burn, turbocharged, with oxidation catalyst, compressor engine | 2016-07-11 | C2701C(Catalytic Converter): Engine Catalyst; C2707C(Catalytic Converter): Engine Catalyst; C2708C(Catalytic Converter): Engine Catalyst | Alliance Source Testing | 1,680 hp | 1.0 g/hp-hr | 1,607 hp | 0.134 g/hp-hr | 7E | Nitrogen Dioxide | PP | Y | NA
2016 | 1656 | 0661005027 | E2 Appalachian LLC - Batesville | 58380 St John Rd | Quaker City | 43773 |  | Noble | P008 | 1,680 Hp. Waukesha (L7044GSI) natural gas-fired, rich burn, turbocharged, with oxidation catalyst, compressor engine | 2016-07-11 | C2701C(Catalytic Converter): Engine Catalyst; C2707C(Catalytic Converter): Engine Catalyst; C2708C(Catalytic Converter): Engine Catalyst | Alliance Source Testing | 1,680 hp | 1.0 g/hp-hr | 1,568 hp | 0.212 g/hp-hr | 7E | Nitrogen Dioxide | PP | Y | NA
2016 | 1663 | 0661005027 | E2 Appalachian LLC - Batesville | 58380 St John Rd | Quaker City | 43773 |  | Noble | P006 | 1,680 Hp. Waukesha (L7044GSI) natural gas-fired, rich burn, turbocharged, with oxidation catalyst, compressor engine | 2016-07-12 | C2706C(Catalytic Converter): Engine Catalyst | Alliance Source Testing | 1,680 hp | 0.268 g/hp-hr | 1,490 hp | 0.037 g/hp-hr | 7E | Nitrogen Dioxide | PP | Y | NA
2016 | 1666 | 0661005040 | Crum Compressor Station | 52934 Town Highway 192 | Seneca Twp. | 43780 |  | Noble | P001 | One (1) Waukesha 7044GSI 1,680 hp compressor engine fitted with a 5-element non-selective catalytic reduction catalyst. | 2016-08-31 | C-1(Catalytic Converter): 5-element NSCR for compressor engine C-100; C-2(Catalytic Converter): 5-element NSCR for compressor engine C-200; C-3(Catalytic Converter): 5-element NSCR for compressor engine C-300; C-4(Catalytic Converter): 5-element NSCR for | Alliance Source Testing | 1680 hp | 1.0 g/hp-hr | 1568 hp | 0.03 g/hp-hr | 7E | Nitrogen Dioxide | PP | Y | NA
2016 | 1667 | 0661005040 | Crum Compressor Station | 52934 Town Highway 192 | Seneca Twp. | 43780 |  | Noble | P002 | One (1) Waukesha 7044GSI 1,680 hp compressor engine fitted with a 5-element non-selective catalytic reduction catalyst. | 2016-08-31 | C-1(Catalytic Converter): 5-element NSCR for compressor engine C-100; C-2(Catalytic Converter): 5-element NSCR for compressor engine C-200; C-3(Catalytic Converter): 5-element NSCR for compressor engine C-300; C-4(Catalytic Converter): 5-element NSCR for | Alliance Source Testing | 1680 hp | 1.0 g/hp-hr | 1584 hp | 0.22 g/hp-hr | 7E | Nitrogen Dioxide | PP | Y | NA
2016 | 1668 | 0661005040 | Crum Compressor Station | 52934 Town Highway 192 | Seneca Twp. | 43780 |  | Noble | P003 | One (1) Waukesha 7044GSI 1,680 hp compressor engine fitted with a 5-element non-selective catalytic reduction catalyst. | 2016-08-31 | C-1(Catalytic Converter): 5-element NSCR for compressor engine C-100; C-2(Catalytic Converter): 5-element NSCR for compressor engine C-200; C-3(Catalytic Converter): 5-element NSCR for compressor engine C-300; C-4(Catalytic Converter): 5-element NSCR for | Alliance Source Testing | 1680 hp | 1.0 g/hp-hr | 1558 hp | 0.26 g/hp-hr | 7E | Nitrogen Dioxide | PP | Y | NA
2016 | 1669 | 0661005040 | Crum Compressor Station | 52934 Town Highway 192 | Seneca Twp. | 43780 |  | Noble | P004 | One (1) Waukesha 7044GSI 1,680 hp compressor engine fitted with a 5-element non-selective catalytic reduction catalyst. | 2016-08-31 | C-1(Catalytic Converter): 5-element NSCR for compressor engine C-100; C-2(Catalytic Converter): 5-element NSCR for compressor engine C-200; C-3(Catalytic Converter): 5-element NSCR for compressor engine C-300; C-4(Catalytic Converter): 5-element NSCR for | Alliance Source Testing | 1680 hp | 1.0 g/hp-hr | 1563 hp | 0.11 g/hp-hr | 7E | Nitrogen Dioxide | PP | Y | NA
2016 | 1670 | 0661005040 | Crum Compressor Station | 52934 Town Highway 192 | Seneca Twp. | 43780 |  | Noble | P005 | One (1) Waukesha 7044GSI 1,680 hp compressor engine fitted with a 5-element non-selective catalytic reduction catalyst. | 2016-08-31 | C-1(Catalytic Converter): 5-element NSCR for compressor engine C-100; C-2(Catalytic Converter): 5-element NSCR for compressor engine C-200; C-3(Catalytic Converter): 5-element NSCR for compressor engine C-300; C-4(Catalytic Converter): 5-element NSCR for | Alliance Source Testing | 1680 hp | 1.0 g/hp-hr | 1503 hp | 0.03 g/hp-hr | 7E | Nitrogen Dioxide | PP | Y | NA
2016 | 1671 | 0661005040 | Crum Compressor Station | 52934 Town Highway 192 | Seneca Twp. | 43780 |  | Noble | P006 | One (1) Waukesha 7044GSI 1,680 hp compressor engine fitted with a 5-element non-selective catalytic reduction catalyst. | 2016-08-31 | C-1(Catalytic Converter): 5-element NSCR for compressor engine C-100; C-2(Catalytic Converter): 5-element NSCR for compressor engine C-200; C-3(Catalytic Converter): 5-element NSCR for compressor engine C-300; C-4(Catalytic Converter): 5-element NSCR for | Alliance Source Testing | 1680 hp | 1.0 g/hp-hr | 1533 hp | 0.05 g/hp-hr | 7E | Nitrogen Dioxide | PP | Y | NA
2016 | 1672 | 0661005040 | Crum Compressor Station | 52934 Town Highway 192 | Seneca Twp. | 43780 |  | Noble | P007 | One (1) Waukesha 7044GSI 1,680 hp compressor engine fitted with a 5-element non-selective catalytic reduction catalyst. | 2016-08-31 | C-1(Catalytic Converter): 5-element NSCR for compressor engine C-100; C-2(Catalytic Converter): 5-element NSCR for compressor engine C-200; C-3(Catalytic Converter): 5-element NSCR for compressor engine C-300; C-4(Catalytic Converter): 5-element NSCR for | Alliance Source Testing | 1680 hp | 1.0 g/hp-hr | 1330 hp | 0.05 g/hp-hr | 7E | Nitrogen Dioxide | PP | Y | NA
2016 | 1673 | 0661005040 | Crum Compressor Station | 52934 Town Highway 192 | Seneca Twp. | 43780 |  | Noble | P008 | One (1) Waukesha 7044GSI 1,680 hp compressor engine fitted with a 5-element non-selective catalytic reduction catalyst. | 2016-08-31 | C-1(Catalytic Converter): 5-element NSCR for compressor engine C-100; C-2(Catalytic Converter): 5-element NSCR for compressor engine C-200; C-3(Catalytic Converter): 5-element NSCR for compressor engine C-300; C-4(Catalytic Converter): 5-element NSCR for | Alliance Source Testing | 1680 hp | 1.0 g/hp-hr | 1451 hp | 0.02 g/hp-hr | 7E | Nitrogen Dioxide | PP | Y | NA
2016 | 1674 | 0661005040 | Crum Compressor Station | 52934 Town Highway 192 | Seneca Twp. | 43780 |  | Noble | P009 | One (1) Waukesha 7044GSI 1,680 hp compressor engine fitted with a 5-element non-selective catalytic reduction catalyst. | 2016-08-31 | C-1(Catalytic Converter): 5-element NSCR for compressor engine C-100; C-2(Catalytic Converter): 5-element NSCR for compressor engine C-200; C-3(Catalytic Converter): 5-element NSCR for compressor engine C-300; C-4(Catalytic Converter): 5-element NSCR for | Alliance Source Testing | 1680 hp | 1.0 g/hp-hr | 1430 hp | 0.03 g/hp-hr | 7E | Nitrogen Dioxide | PP | Y | NA
2016 | 1694 | 0661005042 | CNX Gas LLC., Noble 19 | 51109 Lew Martin Rd | Summerfield | 43778 |  | Noble | P002 | One or multiple stationary natural gas-fired spark ignition (SI) internal combustion engines (ICE) with a combined total horsepower of 1,800 HP for the site. Includes 2007 or later model year engines manufactured after the applicable effective date iden | 2016-05-17 | catalyst | Ecotest Energy Services | 380 hp 84 hp | 2.0 g/hp-hr | 165 hp 55 hp | 0.18 g/hp-hr | 6348 03 | NOx - Nitrogen Oxides | PP | Y | NA | 380 hp flash gas unit and 84 hp VRU compressor engine-P002 allowable combined and results combined
2016 | 1697 | 0661005052 | Long Compressor Station | 55135 Batesville Rd | Quaker City | 43773 |  | Noble | P001 | 1,680 hp Waukesha 7044GSI NG Fired-rich burn-4stroke compressor engine | 2016-01-28 | C-01(Catalytic Converter): Non-selective catalyst reduction device for C-2000; C-02(Catalytic Converter): Non-selective catalyst reduction device for C-2100; C-03(Catalytic Converter): Non-selective catalyst reduction device for C-2200; C-04(Catalytic Con | Technical Compliance Solutions | 1680 hp | 1.0 g/hp-hr | 1628 hp | 0.05 g/hp-hr | 320 | NOx - Nitrogen Oxides | PP | Y | NA
2016 | 1701 | 0661005052 | Long Compressor Station | 55135 Batesville Rd | Quaker City | 43773 |  | Noble | P002 | 1,680 hp Waukesha 7044GSI NG Fired-rich burn-4stroke compressor engine | 2016-01-28 | C-01(Catalytic Converter): Non-selective catalyst reduction device for C-2000; C-02(Catalytic Converter): Non-selective catalyst reduction device for C-2100; C-03(Catalytic Converter): Non-selective catalyst reduction device for C-2200; C-04(Catalytic Con | Technical Compliance Solutions | 1680 hp | 1.0 g/hp-hr | 1610 hp | 0.05 g/hp-hr | 320 | NOx - Nitrogen Oxides | PP | Y | NA
2016 | 1703 | 0661005052 | Long Compressor Station | 55135 Batesville Rd | Quaker City | 43773 |  | Noble | P003 | 1,680 hp Waukesha 7044GSI NG Fired-rich burn-4stroke compressor engine | 2016-01-28 | C-01(Catalytic Converter): Non-selective catalyst reduction device for C-2000; C-02(Catalytic Converter): Non-selective catalyst reduction device for C-2100; C-03(Catalytic Converter): Non-selective catalyst reduction device for C-2200; C-04(Catalytic Con | Technical Compliance Solutions | 1680 hp | 1.0 g/hp-hr | 1606 hp | 0.07 g/hp-hr | 320 | NOx - Nitrogen Oxides | PP | Y | NA
2016 | 1705 | 0661005052 | Long Compressor Station | 55135 Batesville Rd | Quaker City | 43773 |  | Noble | P004 | 1,680 hp Waukesha 7044GSI NG Fired-rich burn-4stroke compressor engine | 2016-01-28 | C-01(Catalytic Converter): Non-selective catalyst reduction device for C-2000; C-02(Catalytic Converter): Non-selective catalyst reduction device for C-2100; C-03(Catalytic Converter): Non-selective catalyst reduction device for C-2200; C-04(Catalytic Con | Technical Compliance Solutions | 1680 hp | 1.0 g/hp-hr | 1627 hp | 0.01 g/hp-hr | 320 | NOx - Nitrogen Oxides | PP | Y | NA
2016 | 1708 | 0661005052 | Long Compressor Station | 55135 Batesville Rd | Quaker City | 43773 |  | Noble | P005 | 1,680 hp Waukesha 7044GSI NG Fired-rich burn-4stroke compressor engine | 2016-01-28 | C-01(Catalytic Converter): Non-selective catalyst reduction device for C-2000; C-02(Catalytic Converter): Non-selective catalyst reduction device for C-2100; C-03(Catalytic Converter): Non-selective catalyst reduction device for C-2200; C-04(Catalytic Con | Technical Compliance Solutions | 1680 hp | 1.0 g/hp-hr | 1628 hp | 0.03 g/hp-hr | 320 | NOx - Nitrogen Oxides | PP | Y | NA
2016 | 1712 | 0661005052 | Long Compressor Station | 55135 Batesville Rd | Quaker City | 43773 |  | Noble | P006 | 1,680 hp Waukesha 7044GSI NG Fired-rich burn-4stroke compressor engine | 2016-01-28 | C-01(Catalytic Converter): Non-selective catalyst reduction device for C-2000; C-02(Catalytic Converter): Non-selective catalyst reduction device for C-2100; C-03(Catalytic Converter): Non-selective catalyst reduction device for C-2200; C-04(Catalytic Con | Technical Compliance Solutions | 1680 hp | 1.0 g/hp-hr | 1623 hp | 0.04 g/hp-hr | 320 | NOx - Nitrogen Oxides | PP | Y | NA
2016 | 1715 | 0661005052 | Long Compressor Station | 55135 Batesville Rd | Quaker City | 43773 |  | Noble | P007 | 1,680 hp Waukesha 7044GSI NG Fired-rich burn-4stroke compressor engine | 2016-01-28 | C-01(Catalytic Converter): Non-selective catalyst reduction device for C-2000; C-02(Catalytic Converter): Non-selective catalyst reduction device for C-2100; C-03(Catalytic Converter): Non-selective catalyst reduction device for C-2200; C-04(Catalytic Con | Technical Compliance Solutions | 1680 hp | 1.0 g/hp-hr | 1616 hp | 0.00 g/hp-hr | 320 | NOx - Nitrogen Oxides | PP | Y | NA
2016 | 1961 | 0857103154 | PINNACLE GAS PRODUCERS LLC | 4220 PINNACLE RD | MORAINE | 45439 |  | Montgomery | B003 | Natural Gas Fired Compressor Engine, 12 MMBtu/hour nominal heat input | 2016-02-24 | n/a | DTE Energy | 12MMBtu/hr heat input | 160ppmvd@15%O2 | 867 RPM | 93ppmvd@15%O2 | 7E | Nitrogen Dioxide | PP | Y | NA | Average fuel content at 984 BTU/scf with combustion temperature at 1503 degrees Fahrenheit.
2016 | 1962 | 0857103154 | PINNACLE GAS PRODUCERS LLC | 4220 PINNACLE RD | MORAINE | 45439 |  | Montgomery | B003 | Natural Gas Fired Compressor Engine, 12 MMBtu/hour nominal heat input | 2016-02-24 | n/a | DTE Energy | 12MMBtu/hr heat input | 160ppmvd@15%O2 | 867 RPM | 93ppmvd@15%O2 | 7E | Nitrogen Oxide | PP | Y | NA | Average fuel content at 984 BTU/scf with combustion temperature at 1503 degrees Fahrenheit.
2005 | 1141 | 1409090081 | Miami University | Cole Service Building | Oxford | 45056 |  | Butler | P002 | 5732 KW Lean Burn Natural Gas Fired 4-stroke Reciprocating Engine | 2005-08-17 | CO CATALYST | ENVIRONMENTAL QUALITY MANAGEMENT |  |  |  |  | 7 | Nitrogen Dioxide | PASS | NA | Y |  | Yes
2005 | 1144 | 1409090081 | Miami University | Cole Service Building | Oxford | 45056 |  | Butler | P002 | 5732 KW Lean Burn Natural Gas Fired 4-stroke Reciprocating Engine | 2005-08-17 | CO CATALYST | ENVIRONMENTAL QUALITY MANAGEMENT |  |  |  |  | 7 | Nitrogen Oxide | PASS | NA | Y |  | Yes
2005 | 1146 | 1409090081 | Miami University | Cole Service Building | Oxford | 45056 |  | Butler | P001 | 5732 KW Lean Burn Natural Gas Fired 4-stroke Reciprocating Engine | 2005-08-18 | CO CATALYST | ENVIRONMENTAL QUALITY MANAGEMENT |  |  |  |  | 7 | Nitrogen Dioxide | PASS | NA | Y |  | Yes
2005 | 1147 | 1409090081 | Miami University | Cole Service Building | Oxford | 45056 |  | Butler | P001 | 5732 KW Lean Burn Natural Gas Fired 4-stroke Reciprocating Engine | 2005-08-18 | CO CATALYST | ENVIRONMENTAL QUALITY MANAGEMENT |  |  |  |  | 7 | Nitrogen Oxide | PASS | NA | Y |  | Yes
2007 | 1057 | 0630000001 | Tennessee Gas Pipeline Station 209 | 3428 Clay Pike Road | Cumberland | 43732 |  | Guernsey | B012 | Recip. Engine 11A, Cooper Bessemer GMWA-10 | 2007-04-23 | N/A | Clean Air Engineering |  |  |  |  | 7 | Nitrogen Oxide | PASS | NA | Y |  | Yes
2007 | 1058 | 0630000001 | Tennessee Gas Pipeline Station 209 | 3428 Clay Pike Road | Cumberland | 43732 |  | Guernsey | B012 | Recip. Engine 11A, Cooper Bessemer GMWA-10 | 2007-04-23 | N/A | Clean Air Engineering |  |  |  |  | 7 | Nitrogen Dioxide | PASS | NA | Y |  | Yes
2007 | 1059 | 0630000001 | Tennessee Gas Pipeline Station 209 | 3428 Clay Pike Road | Cumberland | 43732 |  | Guernsey | B014 | Recip. Engine 13A, Cooper Bessemer GMWA-10 | 2007-04-24 | N/A | Clean Air Engineering |  |  |  |  | 7 | Nitrogen Dioxide | PASS | NA | Y |  | Yes
2007 | 1060 | 0630000001 | Tennessee Gas Pipeline Station 209 | 3428 Clay Pike Road | Cumberland | 43732 |  | Guernsey | B014 | Recip. Engine 13A, Cooper Bessemer GMWA-10 | 2007-04-24 | N/A | Clean Air Engineering |  |  |  |  | 7 | Nitrogen Oxide | PASS | NA | Y |  | Yes
2007 | 1061 | 0630000001 | Tennessee Gas Pipeline Station 209 | 3428 Clay Pike Road | Cumberland | 43732 |  | Guernsey | B013 | Recip. Engine 12A, Cooper Bessemer GMWA-10 | 2007-04-30 | N/A | Stork Southweatern Laboratories |  |  |  |  | 7 | Nitrogen Oxide | PASS | NA | Y |  | Yes
2007 | 1062 | 0630000001 | Tennessee Gas Pipeline Station 209 | 3428 Clay Pike Road | Cumberland | 43732 |  | Guernsey | B013 | Recip. Engine 12A, Cooper Bessemer GMWA-10 | 2007-04-30 | N/A | Stork Southweatern Laboratories |  |  |  |  | 7 | Nitrogen Dioxide | PASS | NA | Y |  | Yes
2008 | 1182 | 0630000001 | Tennessee Gas Pipeline Station 209 | 3428 Clay Pike Road | Cumberland | 43732 |  | Guernsey | B012 | Recip. Engine 11A, Cooper Bessemer GMWA-10 | 2008-09-03 | N/A | El Paso Pipeline Group |  |  |  |  | 7E | Nitrogen Oxide | PASS | NA | Y |  | Yes
2008 | 1183 | 0630000001 | Tennessee Gas Pipeline Station 209 | 3428 Clay Pike Road | Cumberland | 43732 |  | Guernsey | B012 | Recip. Engine 11A, Cooper Bessemer GMWA-10 | 2008-09-03 | N/A | El Paso Pipeline Group |  |  |  |  | 7E | Nitrogen Dioxide | PASS | NA | Y |  | Yes
2008 | 1184 | 0630000001 | Tennessee Gas Pipeline Station 209 | 3428 Clay Pike Road | Cumberland | 43732 |  | Guernsey | B013 | Recip. Engine 12A, Cooper Bessemer GMWA-10 | 2008-09-03 | N/A | El Paso Pipeline Group |  |  |  |  | 7E | Nitrogen Dioxide | PASS | NA | Y |  | Yes
2008 | 1185 | 0630000001 | Tennessee Gas Pipeline Station 209 | 3428 Clay Pike Road | Cumberland | 43732 |  | Guernsey | B013 | Recip. Engine 12A, Cooper Bessemer GMWA-10 | 2008-09-03 | N/A | El Paso Pipeline Group |  |  |  |  | 7E | Nitrogen Oxide | PASS | NA | Y |  | Yes
2008 | 1186 | 0630000001 | Tennessee Gas Pipeline Station 209 | 3428 Clay Pike Road | Cumberland | 43732 |  | Guernsey | B014 | Recip. Engine 13A, Cooper Bessemer GMWA-10 | 2008-09-04 | N/A | El Paso Pipeline Group |  |  |  |  | 7E | Nitrogen Oxide | PASS | NA | Y |  | Yes
2008 | 1187 | 0630000001 | Tennessee Gas Pipeline Station 209 | 3428 Clay Pike Road | Cumberland | 43732 |  | Guernsey | B014 | Recip. Engine 13A, Cooper Bessemer GMWA-10 | 2008-09-04 | N/A | El Paso Pipeline Group |  |  |  |  | 7E | Nitrogen Dioxide | PASS | NA | Y |  | Yes
2009 | 51 | 0630000001 | Tennessee Gas Pipeline Station 209 | 3428 Clay Pike Road | Cumberland | 43732 |  | Guernsey | B012 | Recip. Engine 11A, Cooper Bessemer GMWA-10 | 2009-06-03 | N/A | El Paso Pipeline Group |  |  |  |  | 7E | Nitrogen Dioxide | PASS | NA | Y |  | Yes
2009 | 52 | 0630000001 | Tennessee Gas Pipeline Station 209 | 3428 Clay Pike Road | Cumberland | 43732 |  | Guernsey | B012 | Recip. Engine 11A, Cooper Bessemer GMWA-10 | 2009-06-03 | N/A | El Paso Pipeline Group |  |  |  |  | 7E | Nitrogen Oxide | PASS | NA | Y |  | Yes
2009 | 53 | 0630000001 | Tennessee Gas Pipeline Station 209 | 3428 Clay Pike Road | Cumberland | 43732 |  | Guernsey | B013 | Recip. Engine 12A, Cooper Bessemer GMWA-10 | 2009-06-03 | N/A | El Paso Pipeline Group |  |  |  |  | 7E | Nitrogen Oxide | PASS | NA | Y |  | Yes
2009 | 54 | 0630000001 | Tennessee Gas Pipeline Station 209 | 3428 Clay Pike Road | Cumberland | 43732 |  | Guernsey | B013 | Recip. Engine 12A, Cooper Bessemer GMWA-10 | 2009-06-03 | N/A | El Paso Pipeline Group |  |  |  |  | 7E | Nitrogen Dioxide | PASS | NA | Y |  | Yes
2009 | 55 | 0630000001 | Tennessee Gas Pipeline Station 209 | 3428 Clay Pike Road | Cumberland | 43732 |  | Guernsey | B014 | Recip. Engine 13A, Cooper Bessemer GMWA-10 | 2009-06-04 | N/A | El Paso Pipeline Group |  |  |  |  | 7E | Nitrogen Oxide | PASS | NA | Y |  | Yes
2009 | 56 | 0630000001 | Tennessee Gas Pipeline Station 209 | 3428 Clay Pike Road | Cumberland | 43732 |  | Guernsey | B014 | Recip. Engine 13A, Cooper Bessemer GMWA-10 | 2009-06-04 | N/A | El Paso Pipeline Group |  |  |  |  | 7E | Nitrogen Dioxide | PASS | NA | Y |  | Yes
2010 | 14 | 0630000001 | Tennessee Gas Pipeline Station 209 | 3428 Clay Pike Road | Cumberland | 43732 |  | Guernsey | B012 | Recip. Engine 11A, Cooper Bessemer GMWA-10 | 2010-08-17 | N/A | El Paso Pipeline Group |  |  |  |  | 7E | Nitrogen Dioxide | PASS | NA | Y | Tested pollutants:NO2, NO; Permitted Allowable Emission Rate = 8.0 grams/bhp-hr; Permitted Maximum Operating Rate = 2500 HP; Average Tested Emission Rate = 1.46 grams/bhp-hr; Average Tested Operating Rate = 2171 HP; Results = Passed; AFS Date = 2010-12-27 00:00:00.0; AFS ID = legacy) | Yes
2010 | 19 | 0630000001 | Tennessee Gas Pipeline Station 209 | 3428 Clay Pike Road | Cumberland | 43732 |  | Guernsey | B014 | Recip. Engine 13A, Cooper Bessemer GMWA-10 | 2010-08-17 | N/A | El Paso Pipeline Group |  |  |  |  | 7E | Nitrogen Oxide | PASS | NA | Y | Tested pollutants:NO2, NO; Permitted Allowable Emission Rate = 8.0 grams/bhp-hr; Permitted Maximum Operating Rate = 2500 HP; Average Tested Emission Rate = 3.52 grams/bhp-hr; Average Tested Operating Rate = 2484 HP; Results = Passed; AFS Date = 2010-12-27 00:00:00.0; AFS ID = legacy) | Yes
2010 | 21 | 0630000001 | Tennessee Gas Pipeline Station 209 | 3428 Clay Pike Road | Cumberland | 43732 |  | Guernsey | B013 | Recip. Engine 12A, Cooper Bessemer GMWA-10 | 2010-08-17 | N/A | El Paso Pipeline Group |  |  |  |  | 7E | Nitrogen Dioxide | PASS | NA | Y | Tested pollutants:NO2, NO; Permitted Allowable Emission Rate = 8.0 grams/bhp-hr; Permitted Maximum Operating Rate = 2500 HP; Average Tested Emission Rate = 4.81 grams/bhp-hr; Average Tested Operating Rate = 2526 HP; Results = Passed; AFS Date = 2010-12-27 00:00:00.0; AFS ID = legacy) | Yes
2011 | 721 | 0630000001 | Tennessee Gas Pipeline Station 209 | 3428 Clay Pike Road | Cumberland | 43732 |  | Guernsey | B012 | Recip. Engine 11A, Cooper Bessemer GMWA-10 | 2011-08-24 | N/A | El Paso Pipeline Group |  |  |  |  | 7E | Nitrogen Dioxide | INVALID | NA | Y | Tested pollutants: NO2, NO; Permitted Allowable Emission Rate = 8.0 grams/bhp-hr; Permitted Maximum Operating Rate = 2500 HP; Average Tested Emission Rate = 5.45 grams/bhp-hr; Average Tested Operating Rate = 2482 HP; Results = Invalid; AFS Date = ; AFS ID = ) Failed to conduct linearity and stability checks | Yes
2011 | 722 | 0630000001 | Tennessee Gas Pipeline Station 209 | 3428 Clay Pike Road | Cumberland | 43732 |  | Guernsey | B012 | Recip. Engine 11A, Cooper Bessemer GMWA-10 | 2011-08-24 | N/A | El Paso Pipeline Group |  |  |  |  | 7E | Nitrogen Oxide | INVALID | NA | Y | Tested pollutants: NO2, NO; Permitted Allowable Emission Rate = 8.0 grams/bhp-hr; Permitted Maximum Operating Rate = 2500 HP; Average Tested Emission Rate = 5.45 grams/bhp-hr; Average Tested Operating Rate = 2482 HP; Results = Invalid; AFS Date = ; AFS ID = ) Failed to conduct linearity and stability checks | Yes
2011 | 723 | 0630000001 | Tennessee Gas Pipeline Station 209 | 3428 Clay Pike Road | Cumberland | 43732 |  | Guernsey | B013 | Recip. Engine 12A, Cooper Bessemer GMWA-10 | 2011-08-24 | N/A | El Paso Pipeline Group |  |  |  |  | 7E | Nitrogen Dioxide | INVALID | NA | Y | Tested pollutants: NO2, NO; Permitted Allowable Emission Rate = 8.0 grams/bhp-hr; Permitted Maximum Operating Rate = 2500 HP; Average Tested Emission Rate = 5.49 grams/bhp-hr; Average Tested Operating Rate = 2511 HP; Results = Invalid; AFS Date = ; AFS ID = ) Failed to conduct linearity and stability checks | Yes
2011 | 724 | 0630000001 | Tennessee Gas Pipeline Station 209 | 3428 Clay Pike Road | Cumberland | 43732 |  | Guernsey | B013 | Recip. Engine 12A, Cooper Bessemer GMWA-10 | 2011-08-24 | N/A | El Paso Pipeline Group |  |  |  |  | 7E | Nitrogen Oxide | INVALID | NA | Y | Tested pollutants: NO2, NO; Permitted Allowable Emission Rate = 8.0 grams/bhp-hr; Permitted Maximum Operating Rate = 2500 HP; Average Tested Emission Rate = 5.49 grams/bhp-hr; Average Tested Operating Rate = 2511 HP; Results = Invalid; AFS Date = ; AFS ID = ) Failed to conduct linearity and stability checks | Yes
2011 | 725 | 0630000001 | Tennessee Gas Pipeline Station 209 | 3428 Clay Pike Road | Cumberland | 43732 |  | Guernsey | B014 | Recip. Engine 13A, Cooper Bessemer GMWA-10 | 2011-08-24 | N/A | El Paso Pipeline Group |  |  |  |  | 7E | Nitrogen Oxide | INVALID | NA | Y | Tested pollutants: NO2, NO; Permitted Allowable Emission Rate = 8.0 grams/bhp-hr; Permitted Maximum Operating Rate = 2500 HP; Average Tested Emission Rate = 4.30 grams/bhp-hr; Average Tested Operating Rate = 2490 HP; Results = Invalid; AFS Date = ; AFS ID = ) Failed to conduct linearity and stability checks | Yes
2011 | 726 | 0630000001 | Tennessee Gas Pipeline Station 209 | 3428 Clay Pike Road | Cumberland | 43732 |  | Guernsey | B014 | Recip. Engine 13A, Cooper Bessemer GMWA-10 | 2011-08-24 | N/A | El Paso Pipeline Group |  |  |  |  | 7E | Nitrogen Dioxide | INVALID | NA | Y | Tested pollutants: NO2, NO; Permitted Allowable Emission Rate = 8.0 grams/bhp-hr; Permitted Maximum Operating Rate = 2500 HP; Average Tested Emission Rate = 4.30 grams/bhp-hr; Average Tested Operating Rate = 2490 HP; Results = Invalid; AFS Date = ; AFS ID = ) Failed to conduct linearity and stability checks | Yes
2011 | 727 | 0630000001 | Tennessee Gas Pipeline Station 209 | 3428 Clay Pike Road | Cumberland | 43732 |  | Guernsey | B012 | Recip. Engine 11A, Cooper Bessemer GMWA-10 | 2011-09-20 | N/A | El Paso Pipeline Group |  |  |  |  | 7E | Nitrogen Dioxide | PASS | NA | Y | Tested pollutants: NO2, NO; Permitted Allowable Emission Rate = 8.0 grams/bhp-hr; Permitted Maximum Operating Rate = 2500 HP; Average Tested Emission Rate = 2.37 grams/bhp-hr; Average Tested Operating Rate = 2297 HP; Results = Passed; AFS Date = 2011-10-27 00:00:00.0; AFS ID = legacy) verified results from previous tests | Yes
2011 | 728 | 0630000001 | Tennessee Gas Pipeline Station 209 | 3428 Clay Pike Road | Cumberland | 43732 |  | Guernsey | B012 | Recip. Engine 11A, Cooper Bessemer GMWA-10 | 2011-09-20 | N/A | El Paso Pipeline Group |  |  |  |  | 7E | Nitrogen Oxide | PASS | NA | Y | Tested pollutants: NO2, NO; Permitted Allowable Emission Rate = 8.0 grams/bhp-hr; Permitted Maximum Operating Rate = 2500 HP; Average Tested Emission Rate = 2.37 grams/bhp-hr; Average Tested Operating Rate = 2297 HP; Results = Passed; AFS Date = 2011-10-27 00:00:00.0; AFS ID = legacy) verified results from previous tests | Yes
2012 | 663 | 0630000001 | Tennessee Gas Pipeline Station 209 | 3428 Clay Pike Road | Cumberland | 43732 |  | Guernsey | B012 | Recip. Engine 11A, Cooper Bessemer GMWA-10 | 2012-06-12 | N/A | El Paso Pipeline Group |  |  |  |  | 7E | Nitrogen Oxide | PASS | NA | Y | Tested pollutants: NO2, NO; Permitted Allowable Emission Rate = 8.0 grams/bhp-hr; Permitted Maximum Operating Rate = 2,500 HP; Average Tested Emission Rate = 2.67 grams/bhp-hr; Average Tested Operating Rate = 2,330 HP; Results = Passed; AFS Date = 2012-09-27 00:00:00.0; AFS ID = legacy) | Yes
2012 | 664 | 0630000001 | Tennessee Gas Pipeline Station 209 | 3428 Clay Pike Road | Cumberland | 43732 |  | Guernsey | B012 | Recip. Engine 11A, Cooper Bessemer GMWA-10 | 2012-06-12 | N/A | El Paso Pipeline Group |  |  |  |  | 7E | Nitrogen Dioxide | PASS | NA | Y | Tested pollutants: NO2, NO; Permitted Allowable Emission Rate = 8.0 grams/bhp-hr; Permitted Maximum Operating Rate = 2,500 HP; Average Tested Emission Rate = 2.67 grams/bhp-hr; Average Tested Operating Rate = 2,330 HP; Results = Passed; AFS Date = 2012-09-27 00:00:00.0; AFS ID = legacy) | Yes
2012 | 665 | 0630000001 | Tennessee Gas Pipeline Station 209 | 3428 Clay Pike Road | Cumberland | 43732 |  | Guernsey | B013 | Recip. Engine 12A, Cooper Bessemer GMWA-10 | 2012-06-12 | N/A | El Paso Pipeline Group |  |  |  |  | 7E | Nitrogen Oxide | PASS | NA | Y | Tested pollutants: NO2, NO; Permitted Allowable Emission Rate = 8.0 grams/bhp-hr; Permitted Maximum Operating Rate = 2,500 HP; Average Tested Emission Rate = 2.57 grams/bhp-hr; Average Tested Operating Rate = 2,393 HP; Results = Passed; AFS Date = 2012-09-27 00:00:00.0; AFS ID = legacy) | Yes
2012 | 666 | 0630000001 | Tennessee Gas Pipeline Station 209 | 3428 Clay Pike Road | Cumberland | 43732 |  | Guernsey | B013 | Recip. Engine 12A, Cooper Bessemer GMWA-10 | 2012-06-12 | N/A | El Paso Pipeline Group |  |  |  |  | 7E | Nitrogen Dioxide | PASS | NA | Y | Tested pollutants: NO2, NO; Permitted Allowable Emission Rate = 8.0 grams/bhp-hr; Permitted Maximum Operating Rate = 2,500 HP; Average Tested Emission Rate = 2.57 grams/bhp-hr; Average Tested Operating Rate = 2,393 HP; Results = Passed; AFS Date = 2012-09-27 00:00:00.0; AFS ID = legacy) | Yes
2012 | 667 | 0630000001 | Tennessee Gas Pipeline Station 209 | 3428 Clay Pike Road | Cumberland | 43732 |  | Guernsey | B014 | Recip. Engine 13A, Cooper Bessemer GMWA-10 | 2012-06-12 | N/A | El Paso Pipeline Group |  |  |  |  | 7E | Nitrogen Oxide | PASS | NA | Y | Tested pollutants: NO2, NO; Permitted Allowable Emission Rate = 8.0 grams/bhp-hr; Permitted Maximum Operating Rate = 2,500 HP; Average Tested Emission Rate = 2.68 grams/bhp-hr; Average Tested Operating Rate = 2,448 HP; Results = Passed; AFS Date = 2012-09-27 00:00:00.0; AFS ID = legacy) | Yes
2012 | 668 | 0630000001 | Tennessee Gas Pipeline Station 209 | 3428 Clay Pike Road | Cumberland | 43732 |  | Guernsey | B014 | Recip. Engine 13A, Cooper Bessemer GMWA-10 | 2012-06-12 | N/A | El Paso Pipeline Group |  |  |  |  | 7E | Nitrogen Dioxide | PASS | NA | Y | Tested pollutants: NO2, NO; Permitted Allowable Emission Rate = 8.0 grams/bhp-hr; Permitted Maximum Operating Rate = 2,500 HP; Average Tested Emission Rate = 2.68 grams/bhp-hr; Average Tested Operating Rate = 2,448 HP; Results = Passed; AFS Date = 2012-09-27 00:00:00.0; AFS ID = legacy) | Yes
2014 | 1609 | 0546015002 | Bellefontaine Gas Producers, LLC | 2946 US Route 68 North | Bellefontaine | 43311 |  | Logan | P001 | 2275 Hp, 4-stroke lean burn, non-emergency, spark ignition RICE; Ch. 31 modification issued 1/8/2014. | 2014-04-29 | N/A | DTE Energy | 1600 KW | 0.6 g/bhp-hr | 1600 KW | 0.5 g/bhp-hr | 7E | Nitrogen Oxide | PASS | NA | Y |  | Yes
2014 | 1726 | 0630000001 | Tennessee Gas Pipeline Station 209 | 3428 Clay Pike Road | Cumberland | 43732 |  | Guernsey | B012 | Recip. Engine 11A, Cooper Bessemer GMWA-10 | 2014-09-24 | none | Kindermorgan Corp. | 2500 Hp | 8 g/Hp-hr | 2483 Hp | 4.77 g/Hp-hr | 7E | Nitrogen Dioxide | PASS | NA | Y | Method 7E was not used. ASTM 6522-00 method was used. | Yes
2014 | 1727 | 0630000001 | Tennessee Gas Pipeline Station 209 | 3428 Clay Pike Road | Cumberland | 43732 |  | Guernsey | B013 | Recip. Engine 12A, Cooper Bessemer GMWA-10 | 2014-09-24 | none | Kindermorgan Corp. | 2500 Hp | 8 g/Hp-hr | 2512 Hp | 4.76 g/Hp-hr | 7E | Nitrogen Dioxide | PASS | NA | Y | Method 7E was not used. ASTM 6522-00 method was used. | Yes
2015 | 340 | 0238000187 | Trailway Wood II | 2261 County Rd 168 | Dundee | 44624 |  | Holmes | B004 | 4SLB Stationary RICE Natural Gas Engine #1 | 2015-04-16 | Engineered to meet the standard | Custom Stack Analysis | 452.8 KW | 82 ppm @ 15% O2 | 188.6 KW | 71.63 ppm @ 15% O2 | 7E | Nitrogen Oxide | PP | NA | Y | Operated at only 41.78 % of load. . If operated at a rate higher than 10% of the tested a new test will be required. | Yes
2015 | 735 | 0630000001 | Tennessee Gas Pipeline Station 209 | 3428 Clay Pike Road | Cumberland | 43732 |  | Guernsey | B012 | Recip. Engine 11A, Cooper Bessemer GMWA-10 | 2015-08-26 | none | Kindermorgan Corp | 2500 hp | 8.0 g/hp-hr | 2502 hp | 5.73 g/hp-hr | 6348 03 | NOx - Nitrogen Oxides | PP | NA | Y |  | Yes
2015 | 736 | 0630000001 | Tennessee Gas Pipeline Station 209 | 3428 Clay Pike Road | Cumberland | 43732 |  | Guernsey | B013 | Recip. Engine 12A, Cooper Bessemer GMWA-10 | 2015-08-26 | none | Kindermorgan Corp | 2500 hp | 8.0 g/hp-hr | 2499 hp | 4.29 g/hp-hr | 6348 03 | NOx - Nitrogen Oxides | PP | NA | Y |  | Yes
2015 | 737 | 0630000001 | Tennessee Gas Pipeline Station 209 | 3428 Clay Pike Road | Cumberland | 43732 |  | Guernsey | B012 | Recip. Engine 11A, Cooper Bessemer GMWA-10 | 2015-08-27 | none | Kindermorgan Corp | 3400 hp | 11.0 g/hp-hr | 3399 hp | 5.07 g/hp-hr | 6348 03 | NOx - Nitrogen Oxides | PP | NA | N | ASTM method 6522-00 used | Yes
2015 | 738 | 0630000001 | Tennessee Gas Pipeline Station 209 | 3428 Clay Pike Road | Cumberland | 43732 |  | Guernsey | B013 | Recip. Engine 12A, Cooper Bessemer GMWA-10 | 2015-08-27 | none | Kindermorgan Corp | 3400 hp | 11.0 g/hp-hr | 3262 hp | 6.19 g/hp-hr | 6348 03 | NOx - Nitrogen Oxides | PP | NA | N | ASTM method 6522-00 used | Yes
2013 | 319 | 0210012004 | Augusta Compressor Facility- Utica Gas Services, L.L.C. | 8034 Bane Rd NE | East Twp. | 44427 |  | Carroll | P014 | 605-hp Baldor IGLC420-2N Engine Driven Emergency Generator | 2013-10-10 | Oxid. Cat. 3(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 4(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 5(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 6(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 7(Catalytic Converter): | Alliance Source Testing | 605 Hp | 1.33 lbs/hr, 2.0 g/hp/hr, 160ppmvd@15%O2 | 551 Hp or 91% of Max | 0.12 lbs/hr, 0.1 g/hp/hr, 7.2 ppmvd@15%O2 | 7E | Nitrogen Oxide | PASS | NA | Y
2013 | 324 | 0210012004 | Augusta Compressor Facility- Utica Gas Services, L.L.C. | 8034 Bane Rd NE | East Twp. | 44427 |  | Carroll | P015 | 605-hp Baldor IGLC420-2N Engine Driven Emergency Generator | 2013-10-10 | Oxid. Cat. 3(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 4(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 5(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 6(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 7(Catalytic Converter): | Alliance Source Testing | 605 Hp | 1.33 lbs/hr, 2.0 g/hp/hr, 160ppmvd@15%O2 | 551 Hp or 91% of Max | 0.14 lbs/hr, 0.1 g/hp/hr, 8.1 ppmvd@15%O2 | 7E | Nitrogen Oxide | PASS | NA | Y
2013 | 289 | 0210012004 | Augusta Compressor Facility- Utica Gas Services, L.L.C. | 8034 Bane Rd NE | East Twp. | 44427 |  | Carroll | P014 | 605-hp Baldor IGLC420-2N Engine Driven Emergency Generator | 2013-10-09 | Oxid. Cat. 3(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 4(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 5(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 6(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 7(Catalytic Converter): | Alliance Source Testing | 605 Hp | 1.33 lbs/hr, 2.0 g/hp/hr, 160ppmvd@15%O2 | 551 Hp or 91% of Max | 0.12 lbs/hr, 0.1 g/hp/hr, 7.2 ppmvd@15%O2 | 7E | Nitrogen Oxide | PASS | NA | Y
2013 | 293 | 0210012004 | Augusta Compressor Facility- Utica Gas Services, L.L.C. | 8034 Bane Rd NE | East Twp. | 44427 |  | Carroll | P015 | 605-hp Baldor IGLC420-2N Engine Driven Emergency Generator | 2013-10-09 | Oxid. Cat. 3(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 4(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 5(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 6(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 7(Catalytic Converter): | Alliance Source Testing | 605 Hp | 1.33 lbs/hr, 2.0 g/hp/hr, 160ppmvd@15%O2 | 551 Hp or 91% of Max | 0.14 lbs/hr, 0.1 g/hp/hr, 8.1 ppmvd@15%O2 | 7E | Nitrogen Oxide | PASS | NA | Y
2013 | 153 | 0210012004 | Augusta Compressor Facility- Utica Gas Services, L.L.C. | 8034 Bane Rd NE | East Twp. | 44427 |  | Carroll | P014 | 605-hp Baldor IGLC420-2N Engine Driven Emergency Generator | 2013-10-08 | Oxid. Cat. 3(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 4(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 5(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 6(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 7(Catalytic Converter): | Alliance Source Testing | 605 Hp | 1.33 lbs/hr, 2.0 g/hp/hr, 160ppmvd@15%O2 | 551 Hp or 91% of Max | 0.12 lbs/hr, 0.1 g/hp/hr, 7.2 ppmvd@15%O2 | 7E | Nitrogen Oxide | PASS | NA | Y
2013 | 158 | 0210012004 | Augusta Compressor Facility- Utica Gas Services, L.L.C. | 8034 Bane Rd NE | East Twp. | 44427 |  | Carroll | P015 | 605-hp Baldor IGLC420-2N Engine Driven Emergency Generator | 2013-10-08 | Oxid. Cat. 3(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 4(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 5(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 6(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 7(Catalytic Converter): | Alliance Source Testing | 605 Hp | 1.33 lbs/hr, 2.0 g/hp/hr, 160ppmvd@15%O2 | 551 Hp or 91% of Max | 0.14 lbs/hr, 0.1 g/hp/hr, 8.1 ppmvd@15%O2 | 7E | Nitrogen Oxide | PASS | NA | Y
2014 | 1929 | 0634005058 | Atlas Noble, LLC - Cramblett Well Pad | Bowers Road | North Twp. | 43988 |  | Harrison | P003 | NA - One or multiple stationary diesel-fired compression ignition (CI) (diesel) internal combustion engines (ICE), certified to meet the Tier 3 emission standards for diesel engines, with a combined total horsepower (HP) of no more than 250 HP for the site . | 2014-03-04 | none | Air Compliance Consultants | 68 hp | 160 ppm | 33 hp | 12 ppm | 7E | Nitrogen Dioxide | PASS | NA | Y | VRU engine 2- 68 hp caterpillar engine
2011 | 776 | 0664000056 | Waste Management of Ohio (Suburban South Recycling) | 3415 Township Road 447 | Glenford | 43739 |  | Perry | P004 | 1148 HP CAT 3516 Reciprocating LFG Engine | 2011-05-24 | NA | Custom Statck Analysis , LLC |  |  |  |  | 7E | Nitrogen Oxide | PASS | NA | Y | Tested pollutants: NO2, NO; Permitted Allowable Emission Rate = 3.0 grams/hp-hr; Permitted Maximum Operating Rate = 1148 Hp/ 800 Kw; Average Tested Emission Rate = 1.16 grams/hp-hr; Average Tested Operating Rate = 1148 grams/hr-hr/812 Kw; Results = Passed; AFS Date = 2011-10-27 00:00:00.0; AFS ID = legacy)
2011 | 779 | 0664000056 | Waste Management of Ohio (Suburban South Recycling) | 3415 Township Road 447 | Glenford | 43739 |  | Perry | P004 | 1148 HP CAT 3516 Reciprocating LFG Engine | 2011-05-24 | NA | Custom Statck Analysis , LLC |  |  |  |  | 7E | Nitrogen Dioxide | PASS | NA | Y | Tested pollutants: NO2, NO; Permitted Allowable Emission Rate = 3.0 grams/hp-hr; Permitted Maximum Operating Rate = 1148 Hp/ 800 Kw; Average Tested Emission Rate = 1.16 grams/hp-hr; Average Tested Operating Rate = 1148 grams/hr-hr/812 Kw; Results = Passed; AFS Date = 2011-10-27 00:00:00.0; AFS ID = legacy)
2011 | 782 | 0664000056 | Waste Management of Ohio (Suburban South Recycling) | 3415 Township Road 447 | Glenford | 43739 |  | Perry | P006 | 1148 HP CAT 3516 Reciprocating LFG Engine | 2011-05-25 | NA | Custom Statck Analysis , LLC |  |  |  |  | 7E | Nitrogen Oxide | PASS | NA | Y | Tested pollutants: NO2, NO; Permitted Allowable Emission Rate = 3.0 grams/hp-hr; Permitted Maximum Operating Rate = 1148 Hp/ 800 Kw; Average Tested Emission Rate = 1.04 grams/hp-hr; Average Tested Operating Rate = 1148 grams/hr-hr/815 Kw; Results = Passed; AFS Date = 2011-10-27 00:00:00.0; AFS ID = legacy)
2011 | 783 | 0664000056 | Waste Management of Ohio (Suburban South Recycling) | 3415 Township Road 447 | Glenford | 43739 |  | Perry | P006 | 1148 HP CAT 3516 Reciprocating LFG Engine | 2011-05-25 | NA | Custom Statck Analysis , LLC |  |  |  |  | 7E | Nitrogen Dioxide | PASS | NA | Y | Tested pollutants: NO2, NO; Permitted Allowable Emission Rate = 3.0 grams/hp-hr; Permitted Maximum Operating Rate = 1148 Hp/ 800 Kw; Average Tested Emission Rate = 1.04 grams/hp-hr; Average Tested Operating Rate = 1148 grams/hr-hr/815 Kw; Results = Passed; AFS Date = 2011-10-27 00:00:00.0; AFS ID = legacy)
2011 | 784 | 0664000056 | Waste Management of Ohio (Suburban South Recycling) | 3415 Township Road 447 | Glenford | 43739 |  | Perry | P003 | 1148 HP CAT 3516 Reciprocating LFG Engine | 2011-05-26 | NA | Custom Statck Analysis , LLC |  |  |  |  | 7E | Nitrogen Oxide | PASS | NA | Y | Tested pollutants: NO2, NO; Permitted Allowable Emission Rate = 3.0 grams/hp-hr; Permitted Maximum Operating Rate = 1148 Hp/ 800 Kw; Average Tested Emission Rate = 1.26 grams/hp-hr; Average Tested Operating Rate = 1148 grams/hr-hr; Results = Passed; AFS Date = 2011-10-27 00:00:00.0; AFS ID = legacy)
2011 | 786 | 0664000056 | Waste Management of Ohio (Suburban South Recycling) | 3415 Township Road 447 | Glenford | 43739 |  | Perry | P003 | 1148 HP CAT 3516 Reciprocating LFG Engine | 2011-05-26 | NA | Custom Statck Analysis , LLC |  |  |  |  | 7E | Nitrogen Dioxide | PASS | NA | Y | Tested pollutants: NO2, NO; Permitted Allowable Emission Rate = 3.0 grams/hp-hr; Permitted Maximum Operating Rate = 1148 Hp/ 800 Kw; Average Tested Emission Rate = 1.26 grams/hp-hr; Average Tested Operating Rate = 1148 grams/hr-hr; Results = Passed; AFS Date = 2011-10-27 00:00:00.0; AFS ID = legacy)
2011 | 788 | 0664000056 | Waste Management of Ohio (Suburban South Recycling) | 3415 Township Road 447 | Glenford | 43739 |  | Perry | P007 | 1148 HP CAT 3516 Reciprocating LFG Engine | 2011-05-26 | NA | Custom Statck Analysis , LLC |  |  |  |  | 7E | Nitrogen Dioxide | PASS | NA | Y | Tested pollutants: NO2, NO; Permitted Allowable Emission Rate = 3.0 grams/hp-hr; Permitted Maximum Operating Rate = 1148 Hp/ 800 Kw; Average Tested Emission Rate = 1.19 grams/hp-hr; Average Tested Operating Rate = 1148 grams/hr-hr/811 Kw; Results = Passed; AFS Date = 2011-10-27 00:00:00.0; AFS ID = legacy)
2011 | 791 | 0664000056 | Waste Management of Ohio (Suburban South Recycling) | 3415 Township Road 447 | Glenford | 43739 |  | Perry | P007 | 1148 HP CAT 3516 Reciprocating LFG Engine | 2011-05-26 | NA | Custom Statck Analysis , LLC |  |  |  |  | 7E | Nitrogen Oxide | PASS | NA | Y | Tested pollutants: NO2, NO; Permitted Allowable Emission Rate = 3.0 grams/hp-hr; Permitted Maximum Operating Rate = 1148 Hp/ 800 Kw; Average Tested Emission Rate = 1.19 grams/hp-hr; Average Tested Operating Rate = 1148 grams/hr-hr/811 Kw; Results = Passed; AFS Date = 2011-10-27 00:00:00.0; AFS ID = legacy)
2011 | 794 | 0664000056 | Waste Management of Ohio (Suburban South Recycling) | 3415 Township Road 447 | Glenford | 43739 |  | Perry | P008 | 1148 HP CAT 3516 Reciprocating LFG Engine | 2011-05-26 | NA | Custom Statck Analysis , LLC |  |  |  |  | 7E | Nitrogen Dioxide | PASS | NA | Y | Tested pollutants: NO2, NO; Permitted Allowable Emission Rate = 3.0 grams/hp-hr; Permitted Maximum Operating Rate = 1148 Hp/ 800 Kw; Average Tested Emission Rate = 1.12 grams/hp-hr; Average Tested Operating Rate = 1148 grams/hr-hr/810 Kw; Results = Passed; AFS Date = 2011-10-27 00:00:00.0; AFS ID = legacy)
2011 | 795 | 0664000056 | Waste Management of Ohio (Suburban South Recycling) | 3415 Township Road 447 | Glenford | 43739 |  | Perry | P008 | 1148 HP CAT 3516 Reciprocating LFG Engine | 2011-05-26 | NA | Custom Statck Analysis , LLC |  |  |  |  | 7E | Nitrogen Oxide | PASS | NA | Y | Tested pollutants: NO2, NO; Permitted Allowable Emission Rate = 3.0 grams/hp-hr; Permitted Maximum Operating Rate = 1148 Hp/ 800 Kw; Average Tested Emission Rate = 1.12 grams/hp-hr; Average Tested Operating Rate = 1148 grams/hr-hr/810 Kw; Results = Passed; AFS Date = 2011-10-27 00:00:00.0; AFS ID = legacy)
2011 | 797 | 0664000056 | Waste Management of Ohio (Suburban South Recycling) | 3415 Township Road 447 | Glenford | 43739 |  | Perry | P002 | 1148 HP CAT 3516 Reciprocating LFG Engine | 2011-06-01 | NA | Custom Statck Analysis , LLC |  |  |  |  | 7E | Nitrogen Oxide | PASS | NA | Y | Tested pollutants: NO2, NO; Permitted Allowable Emission Rate = 3.0 grams/hp-hr; Permitted Maximum Operating Rate = 1148 Hp/ 800 Kw; Average Tested Emission Rate = 1.39 grams/hp-hr; Average Tested Operating Rate = 1148 grams/hr-hr; Results = Passed; AFS Date = 2011-10-27 00:00:00.0; AFS ID = legacy)
2011 | 798 | 0664000056 | Waste Management of Ohio (Suburban South Recycling) | 3415 Township Road 447 | Glenford | 43739 |  | Perry | P002 | 1148 HP CAT 3516 Reciprocating LFG Engine | 2011-06-01 | NA | Custom Statck Analysis , LLC |  |  |  |  | 7E | Nitrogen Dioxide | PASS | NA | Y | Tested pollutants: NO2, NO; Permitted Allowable Emission Rate = 3.0 grams/hp-hr; Permitted Maximum Operating Rate = 1148 Hp/ 800 Kw; Average Tested Emission Rate = 1.39 grams/hp-hr; Average Tested Operating Rate = 1148 grams/hr-hr; Results = Passed; AFS Date = 2011-10-27 00:00:00.0; AFS ID = legacy)
2011 | 801 | 0664000056 | Waste Management of Ohio (Suburban South Recycling) | 3415 Township Road 447 | Glenford | 43739 |  | Perry | P005 | 1148 HP CAT 3516 Reciprocating LFG Engine | 2011-06-01 | NA | Custom Statck Analysis , LLC |  |  |  |  | 7E | Nitrogen Dioxide | PASS | NA | Y | Tested pollutants: NO2, NO; Permitted Allowable Emission Rate = 3.0 grams/hp-hr; Permitted Maximum Operating Rate = 1148 Hp/ 800 Kw; Average Tested Emission Rate = 1.0 grams/hp-hr; Average Tested Operating Rate = 1148 grams/hr-hr/807 Kw; Results = Passed; AFS Date = 2011-10-27 00:00:00.0; AFS ID = legacy)
2011 | 802 | 0664000056 | Waste Management of Ohio (Suburban South Recycling) | 3415 Township Road 447 | Glenford | 43739 |  | Perry | P005 | 1148 HP CAT 3516 Reciprocating LFG Engine | 2011-06-01 | NA | Custom Statck Analysis , LLC |  |  |  |  | 7E | Nitrogen Oxide | PASS | NA | Y | Tested pollutants: NO2, NO; Permitted Allowable Emission Rate = 3.0 grams/hp-hr; Permitted Maximum Operating Rate = 1148 Hp/ 800 Kw; Average Tested Emission Rate = 1.0 grams/hp-hr; Average Tested Operating Rate = 1148 grams/hr-hr/807 Kw; Results = Passed; AFS Date = 2011-10-27 00:00:00.0; AFS ID = legacy)
2012 | 736 | 0664000056 | Waste Management of Ohio (Suburban South Recycling) | 3415 Township Road 447 | Glenford | 43739 |  | Perry | P008 | 1148 HP CAT 3516 Reciprocating LFG Engine | 2012-04-02 | NA | RMC Environmental, Inc. |  |  |  |  | 7E | Nitrogen Dioxide | PASS | NA | Y | Tested pollutants: NO2, NO; Permitted Allowable Emission Rate = 3.0 grams/hp-hr; Permitted Maximum Operating Rate = 1148 Hp/ 800 Kw; Average Tested Emission Rate = 1.40 grams/hp-hr; Average Tested Operating Rate = 1148 grams/hr-hr/810 Kw; Results = Passed; AFS Date = 2012-08-01 00:00:00.0; AFS ID = legacy) emissions limit: 3.79 lbs/hr test results: 3.53 lbs/hr
2012 | 739 | 0664000056 | Waste Management of Ohio (Suburban South Recycling) | 3415 Township Road 447 | Glenford | 43739 |  | Perry | P008 | 1148 HP CAT 3516 Reciprocating LFG Engine | 2012-04-02 | NA | RMC Environmental, Inc. |  |  |  |  | 7E | Nitrogen Oxide | PASS | NA | Y | Tested pollutants: NO2, NO; Permitted Allowable Emission Rate = 3.0 grams/hp-hr; Permitted Maximum Operating Rate = 1148 Hp/ 800 Kw; Average Tested Emission Rate = 1.40 grams/hp-hr; Average Tested Operating Rate = 1148 grams/hr-hr/810 Kw; Results = Passed; AFS Date = 2012-08-01 00:00:00.0; AFS ID = legacy) emissions limit: 3.79 lbs/hr test results: 3.53 lbs/hr
2012 | 740 | 0664000056 | Waste Management of Ohio (Suburban South Recycling) | 3415 Township Road 447 | Glenford | 43739 |  | Perry | P005 | 1148 HP CAT 3516 Reciprocating LFG Engine | 2012-04-03 | NA | RMC Environmental, Inc. |  |  |  |  | 7E | Nitrogen Dioxide | PASS | NA | Y | Tested pollutants: NO2, NO; Permitted Allowable Emission Rate = 3.0 grams/hp-hr; Permitted Maximum Operating Rate = 1148 Hp/ 800 Kw; Average Tested Emission Rate = 0.99 grams/hp-hr; Average Tested Operating Rate = 1148 grams/hr-hr/810 Kw; Results = Passed; AFS Date = 2012-08-01 00:00:00.0; AFS ID = legacy) emissions limit: 3.79 lbs/hr test results: 2.52 lbs/hr
2012 | 742 | 0664000056 | Waste Management of Ohio (Suburban South Recycling) | 3415 Township Road 447 | Glenford | 43739 |  | Perry | P005 | 1148 HP CAT 3516 Reciprocating LFG Engine | 2012-04-03 | NA | RMC Environmental, Inc. |  |  |  |  | 7E | Nitrogen Oxide | PASS | NA | Y | Tested pollutants: NO2, NO; Permitted Allowable Emission Rate = 3.0 grams/hp-hr; Permitted Maximum Operating Rate = 1148 Hp/ 800 Kw; Average Tested Emission Rate = 0.99 grams/hp-hr; Average Tested Operating Rate = 1148 grams/hr-hr/810 Kw; Results = Passed; AFS Date = 2012-08-01 00:00:00.0; AFS ID = legacy) emissions limit: 3.79 lbs/hr test results: 2.52 lbs/hr
2012 | 744 | 0664000056 | Waste Management of Ohio (Suburban South Recycling) | 3415 Township Road 447 | Glenford | 43739 |  | Perry | P006 | 1148 HP CAT 3516 Reciprocating LFG Engine | 2012-04-03 | NA | RMC Environmental, Inc. |  |  |  |  | 7E | Nitrogen Dioxide | PASS | NA | Y | Tested pollutants: NO2, NO; Permitted Allowable Emission Rate = 3.0 grams/hp-hr; Permitted Maximum Operating Rate = 1148 Hp/ 800 Kw; Average Tested Emission Rate = 1.10 grams/hp-hr; Average Tested Operating Rate = 1148 grams/hr-hr/810 Kw; Results = Passed; AFS Date = 2012-08-01 00:00:00.0; AFS ID = legacy) emissions limit: 3.79 lbs/hr test results: 2.79 lbs/hr
2012 | 746 | 0664000056 | Waste Management of Ohio (Suburban South Recycling) | 3415 Township Road 447 | Glenford | 43739 |  | Perry | P006 | 1148 HP CAT 3516 Reciprocating LFG Engine | 2012-04-03 | NA | RMC Environmental, Inc. |  |  |  |  | 7E | Nitrogen Oxide | PASS | NA | Y | Tested pollutants: NO2, NO; Permitted Allowable Emission Rate = 3.0 grams/hp-hr; Permitted Maximum Operating Rate = 1148 Hp/ 800 Kw; Average Tested Emission Rate = 1.10 grams/hp-hr; Average Tested Operating Rate = 1148 grams/hr-hr/810 Kw; Results = Passed; AFS Date = 2012-08-01 00:00:00.0; AFS ID = legacy) emissions limit: 3.79 lbs/hr test results: 2.79 lbs/hr
2012 | 750 | 0664000056 | Waste Management of Ohio (Suburban South Recycling) | 3415 Township Road 447 | Glenford | 43739 |  | Perry | P007 | 1148 HP CAT 3516 Reciprocating LFG Engine | 2012-04-03 | NA | RMC Environmental, Inc. |  |  |  |  | 7E | Nitrogen Dioxide | PASS | NA | Y | Tested pollutants: NO2, NO; Permitted Allowable Emission Rate = 3.0 grams/hp-hr; Permitted Maximum Operating Rate = 1148 Hp/ 800 Kw; Average Tested Emission Rate = 1.07 grams/hp-hr; Average Tested Operating Rate = 1148 grams/hr-hr/810 Kw; Results = Passed; AFS Date = 2012-08-01 00:00:00.0; AFS ID = legacy) emissions limit: 3.79 lbs/hr test results: 2.71 lbs/hr
2012 | 751 | 0664000056 | Waste Management of Ohio (Suburban South Recycling) | 3415 Township Road 447 | Glenford | 43739 |  | Perry | P007 | 1148 HP CAT 3516 Reciprocating LFG Engine | 2012-04-03 | NA | RMC Environmental, Inc. |  |  |  |  | 7E | Nitrogen Oxide | PASS | NA | Y | Tested pollutants: NO2, NO; Permitted Allowable Emission Rate = 3.0 grams/hp-hr; Permitted Maximum Operating Rate = 1148 Hp/ 800 Kw; Average Tested Emission Rate = 1.07 grams/hp-hr; Average Tested Operating Rate = 1148 grams/hr-hr/810 Kw; Results = Passed; AFS Date = 2012-08-01 00:00:00.0; AFS ID = legacy) emissions limit: 3.79 lbs/hr test results: 2.71 lbs/hr
2012 | 754 | 0664000056 | Waste Management of Ohio (Suburban South Recycling) | 3415 Township Road 447 | Glenford | 43739 |  | Perry | P003 | 1148 HP CAT 3516 Reciprocating LFG Engine | 2012-04-04 | NA | RMC Environmental, Inc. |  |  |  |  | 7E | Nitrogen Dioxide | PASS | NA | Y | Tested pollutants: NO2, NO; Permitted Allowable Emission Rate = 3.0 grams/hp-hr; Permitted Maximum Operating Rate = 1148 Hp/ 800 Kw; Average Tested Emission Rate = 1.05 grams/hp-hr; Average Tested Operating Rate = 1148 grams/hr-hr/810 Kw; Results = Passed; AFS Date = 2012-08-01 00:00:00.0; AFS ID = legacy) emissions limit: 3.79 lbs/hr test results: 2.67 lbs/hr
2012 | 755 | 0664000056 | Waste Management of Ohio (Suburban South Recycling) | 3415 Township Road 447 | Glenford | 43739 |  | Perry | P003 | 1148 HP CAT 3516 Reciprocating LFG Engine | 2012-04-04 | NA | RMC Environmental, Inc. |  |  |  |  | 7E | Nitrogen Oxide | PASS | NA | Y | Tested pollutants: NO2, NO; Permitted Allowable Emission Rate = 3.0 grams/hp-hr; Permitted Maximum Operating Rate = 1148 Hp/ 800 Kw; Average Tested Emission Rate = 1.05 grams/hp-hr; Average Tested Operating Rate = 1148 grams/hr-hr/810 Kw; Results = Passed; AFS Date = 2012-08-01 00:00:00.0; AFS ID = legacy) emissions limit: 3.79 lbs/hr test results: 2.67 lbs/hr
2012 | 758 | 0664000056 | Waste Management of Ohio (Suburban South Recycling) | 3415 Township Road 447 | Glenford | 43739 |  | Perry | P004 | 1148 HP CAT 3516 Reciprocating LFG Engine | 2012-04-04 | NA | RMC Environmental, Inc. |  |  |  |  | 7E | Nitrogen Oxide | PASS | NA | Y | Tested pollutants: NO2, NO; Permitted Allowable Emission Rate = 3.0 grams/hp-hr; Permitted Maximum Operating Rate = 1148 Hp/ 800 Kw; Average Tested Emission Rate = 1.38 grams/hp-hr; Average Tested Operating Rate = 1148 grams/hr-hr/810 Kw; Results = Passed; AFS Date = 2012-08-01 00:00:00.0; AFS ID = legacy) emissions limit: 3.79 lbs/hr test results: 3.50 lbs/hr
2012 | 759 | 0664000056 | Waste Management of Ohio (Suburban South Recycling) | 3415 Township Road 447 | Glenford | 43739 |  | Perry | P004 | 1148 HP CAT 3516 Reciprocating LFG Engine | 2012-04-04 | NA | RMC Environmental, Inc. |  |  |  |  | 7E | Nitrogen Dioxide | PASS | NA | Y | Tested pollutants: NO2, NO; Permitted Allowable Emission Rate = 3.0 grams/hp-hr; Permitted Maximum Operating Rate = 1148 Hp/ 800 Kw; Average Tested Emission Rate = 1.38 grams/hp-hr; Average Tested Operating Rate = 1148 grams/hr-hr/810 Kw; Results = Passed; AFS Date = 2012-08-01 00:00:00.0; AFS ID = legacy) emissions limit: 3.79 lbs/hr test results: 3.50 lbs/hr
2012 | 762 | 0664000056 | Waste Management of Ohio (Suburban South Recycling) | 3415 Township Road 447 | Glenford | 43739 |  | Perry | P002 | 1148 HP CAT 3516 Reciprocating LFG Engine | 2012-04-05 | NA | RMC Environmental, Inc. |  |  |  |  | 7E | Nitrogen Dioxide | PASS | NA | Y | Tested pollutants: NO2, NO; Permitted Allowable Emission Rate = 3.0 grams/hp-hr; Permitted Maximum Operating Rate = 1148 Hp/ 800 Kw; Average Tested Emission Rate = 1.10 grams/hp-hr; Average Tested Operating Rate = 1148 grams/hr-hr/810 Kw; Results = Passed; AFS Date = 2012-08-01 00:00:00.0; AFS ID = legacy) emissions limit: 3.79 lbs/hr test results: 2.78 lbs/hr
2012 | 763 | 0664000056 | Waste Management of Ohio (Suburban South Recycling) | 3415 Township Road 447 | Glenford | 43739 |  | Perry | P002 | 1148 HP CAT 3516 Reciprocating LFG Engine | 2012-04-05 | NA | RMC Environmental, Inc. |  |  |  |  | 7E | Nitrogen Oxide | PASS | NA | Y | Tested pollutants: NO2, NO; Permitted Allowable Emission Rate = 3.0 grams/hp-hr; Permitted Maximum Operating Rate = 1148 Hp/ 800 Kw; Average Tested Emission Rate = 1.10 grams/hp-hr; Average Tested Operating Rate = 1148 grams/hr-hr/810 Kw; Results = Passed; AFS Date = 2012-08-01 00:00:00.0; AFS ID = legacy) emissions limit: 3.79 lbs/hr test results: 2.78 lbs/hr
2013 | 1255 | 0664000056 | Waste Management of Ohio (Suburban South Recycling) | 3415 Township Road 447 | Glenford | 43739 |  | Perry | P002 | 1148 HP CAT 3516 Reciprocating LFG Engine | 2013-03-26 | oxidative catalyst reduction | RMC Environmental, Inc. | 1148 Hp | 3.0 grams/Hp-hr 3.79 lbs/hr | 1148 Hp | 1.06 grams/Hp-hr 2.68 lbs/hr | 7E | Nitrogen Dioxide | PASS | NA | Y | Testing occurred March 26 - 28, 2013. Lisa witnessed three different tests.
2013 | 1260 | 0664000056 | Waste Management of Ohio (Suburban South Recycling) | 3415 Township Road 447 | Glenford | 43739 |  | Perry | P003 | 1148 HP CAT 3516 Reciprocating LFG Engine | 2013-03-26 | oxidative catalyst reduction | RMC Environmental, Inc. | 1148 Hp | 3.0 grams/Hp-hr 3.79 lbs/hr | 1148 Hp | 0.91 grams/Hp-hr 2.31 lbs/hr | 7E | Nitrogen Dioxide | PASS | NA | Y | Testing occurred March 26 - 28, 2013. Lisa witnessed three different tests.
2013 | 1261 | 0664000056 | Waste Management of Ohio (Suburban South Recycling) | 3415 Township Road 447 | Glenford | 43739 |  | Perry | P004 | 1148 HP CAT 3516 Reciprocating LFG Engine | 2013-03-26 | oxidative catalyst reduction | RMC Environmental, Inc. | 1148 Hp | 3.0 grams/Hp-hr 3.79 lbs/hr | 1148 Hp | 0.91 grams/Hp-hr 2.29 lbs/hr | 7E | Nitrogen Dioxide | PASS | NA | Y | Testing occurred March 26 - 28, 2013. Lisa witnessed three different tests.
2013 | 1265 | 0664000056 | Waste Management of Ohio (Suburban South Recycling) | 3415 Township Road 447 | Glenford | 43739 |  | Perry | P005 | 1148 HP CAT 3516 Reciprocating LFG Engine | 2013-03-26 | oxidative catalyst reduction | RMC Environmental, Inc. | 1148 Hp | 3.0 grams/Hp-hr 3.79 lbs/hr | 1148 Hp | 1.10 grams/Hp-hr 2.79 lbs/hr | 7E | Nitrogen Dioxide | PASS | NA | Y | Testing occurred March 26 - 28, 2013. Lisa witnessed three different tests.
2013 | 1268 | 0664000056 | Waste Management of Ohio (Suburban South Recycling) | 3415 Township Road 447 | Glenford | 43739 |  | Perry | P006 | 1148 HP CAT 3516 Reciprocating LFG Engine | 2013-03-26 | oxidative catalyst reduction | RMC Environmental, Inc. | 1148 Hp | 3.0 grams/Hp-hr 3.79 lbs/hr | 1148 Hp | 1.04 grams/Hp-hr 2.64 lbs/hr | 7E | Nitrogen Dioxide | PASS | NA | Y | Testing occurred March 26 - 28, 2013. Lisa witnessed three different tests.
2013 | 1272 | 0664000056 | Waste Management of Ohio (Suburban South Recycling) | 3415 Township Road 447 | Glenford | 43739 |  | Perry | P007 | 1148 HP CAT 3516 Reciprocating LFG Engine | 2013-03-26 | oxidative catalyst reduction | RMC Environmental, Inc. | 1148 Hp | 3.0 grams/Hp-hr 3.79 lbs/hr | 1148 Hp | 1.05 grams/Hp-hr 2.65 lbs/hr | 7E | Nitrogen Dioxide | PASS | NA | Y | Testing occurred March 26 - 28, 2013. Lisa witnessed three different tests.
2013 | 1275 | 0664000056 | Waste Management of Ohio (Suburban South Recycling) | 3415 Township Road 447 | Glenford | 43739 |  | Perry | P008 | 1148 HP CAT 3516 Reciprocating LFG Engine | 2013-03-26 | oxidative catalyst reduction | RMC Environmental, Inc. | 1148 Hp | 3.0 grams/Hp-hr 3.79 lbs/hr | 1148 Hp | 1.03 grams/Hp-hr 2.61 lbs/hr | 7E | Nitrogen Dioxide | PASS | NA | Y | Testing occurred March 26 - 28, 2013. Lisa witnessed three different tests.
2014 | 2109 | 0664000056 | Waste Management of Ohio (Suburban South Recycling) | 3415 Township Road 447 | Glenford | 43739 |  | Perry | P002 | 1148 HP CAT 3516 Reciprocating LFG Engine | 2014-04-28 | none | RMC Environmental | 800 Kw | 3.0 g/hp-hr | 824 KW | 0.8 gr/hp-hr | 7E | Nitrogen Dioxide | PASS | NA | Y |  | Yes
2014 | 2114 | 0664000056 | Waste Management of Ohio (Suburban South Recycling) | 3415 Township Road 447 | Glenford | 43739 |  | Perry | P004 | 1148 HP CAT 3516 Reciprocating LFG Engine | 2014-04-28 | none | RMC Environmental | 800 MW | 3.0 g/hp-hr | 828 MW | 0.8 g/hp-hr | 7E | Nitrogen Dioxide | PASS | NA | Y |  | Yes
2014 | 2115 | 0664000056 | Waste Management of Ohio (Suburban South Recycling) | 3415 Township Road 447 | Glenford | 43739 |  | Perry | P005 | 1148 HP CAT 3516 Reciprocating LFG Engine | 2014-04-28 | none | RMC Environmental | 800 MW | 3.0 g/hp-hr | 818 MW | 1.3 g/hp-hr | 7E | Nitrogen Dioxide | PASS | NA | Y |  | Yes
2014 | 2119 | 0664000056 | Waste Management of Ohio (Suburban South Recycling) | 3415 Township Road 447 | Glenford | 43739 |  | Perry | P003 | 1148 HP CAT 3516 Reciprocating LFG Engine | 2014-04-29 | none | RMC Environmental | 800 MW | 3.0g/hp-hr | 818 MW | 0.8 g/hp-hr | 7E | Nitrogen Dioxide | PASS | NA | Y |  | Yes
2014 | 2121 | 0664000056 | Waste Management of Ohio (Suburban South Recycling) | 3415 Township Road 447 | Glenford | 43739 |  | Perry | P007 | 1148 HP CAT 3516 Reciprocating LFG Engine | 2014-04-29 | none | RMC Environmental | 800 MW | 3.0 g/hp-hr | 823 MW | 1.0 g/hp-hr | 7E | Nitrogen Dioxide | PASS | NA | Y |  | Yes
2014 | 2126 | 0664000056 | Waste Management of Ohio (Suburban South Recycling) | 3415 Township Road 447 | Glenford | 43739 |  | Perry | P008 | 1148 HP CAT 3516 Reciprocating LFG Engine | 2014-04-29 | none | RMC Environmental | 800 MW | 3.0 g/hp-hr | 824 MW | 0.6 g/hp-hr | 7E | Nitrogen Dioxide | PASS | NA | Y |  | Yes
2014 | 2129 | 0664000056 | Waste Management of Ohio (Suburban South Recycling) | 3415 Township Road 447 | Glenford | 43739 |  | Perry | P006 | 1148 HP CAT 3516 Reciprocating LFG Engine | 2014-04-30 | none | RMC Environmenatl | 800 MW | 3.0 g/hp-hr | 825 MW | 0.9 g/hp-hr | 7E | Nitrogen Dioxide | PASS | NA | Y |  | Yes
2015 | 910 | 0664000056 | Waste Management of Ohio (Suburban South Recycling) | 3415 Township Road 447 | Glenford | 43739 |  | Perry | P003 | 1148 HP CAT 3516 Reciprocating LFG Engine | 2015-03-24 | none | RMC Envirnmental, Inc. | 1,148 hp | 3.0 g/hp-hr | 1,260 hp | 0.9 g/hp-hr | 7E | Nitrogen Dioxide | PP | NA | Y
2015 | 915 | 0664000056 | Waste Management of Ohio (Suburban South Recycling) | 3415 Township Road 447 | Glenford | 43739 |  | Perry | P005 | 1148 HP CAT 3516 Reciprocating LFG Engine | 2015-03-24 | none | RMC Environmental, Inc | 1,148 hp | 3.0 g/hp-hr | 1,252 hp | 1.4 g/hp-hr | 7E | Nitrogen Dioxide | PP | NA | Y
2015 | 916 | 0664000056 | Waste Management of Ohio (Suburban South Recycling) | 3415 Township Road 447 | Glenford | 43739 |  | Perry | P002 | 1148 HP CAT 3516 Reciprocating LFG Engine | 2015-03-25 | none | RMC Envirnmental, Inc. | 1,148 hp | 3.0 g/hp-hr | 1228 hp | 0.8 g/hp-hr | 7E | Nitrogen Dioxide | PP | NA | Y
2015 | 920 | 0664000056 | Waste Management of Ohio (Suburban South Recycling) | 3415 Township Road 447 | Glenford | 43739 |  | Perry | P004 | 1148 HP CAT 3516 Reciprocating LFG Engine | 2015-03-25 | none | RMC Environmental, Inc | 1,148 hp | 3.0 g/hp-hr | 1,231 hp | 0.8 g/hp-hr | 7E | Nitrogen Dioxide | PP | NA | Y
2015 | 923 | 0664000056 | Waste Management of Ohio (Suburban South Recycling) | 3415 Township Road 447 | Glenford | 43739 |  | Perry | P006 | 1148 HP CAT 3516 Reciprocating LFG Engine | 2015-03-25 | none | RMC Environmental, Inc | 1,148 hp | 3.0 g/hp-hr | 1,251 hp | 1.3 g/hp-hr | 7E | Nitrogen Dioxide | PP | NA | Y
2015 | 926 | 0664000056 | Waste Management of Ohio (Suburban South Recycling) | 3415 Township Road 447 | Glenford | 43739 |  | Perry | P007 | 1148 HP CAT 3516 Reciprocating LFG Engine | 2015-03-26 | none | RMC Environmental, Inc | 1,148 hp | 3.0 g/hp-hr | 1,241 hp | 1.0 g/hp-hr | 7E | Nitrogen Dioxide | PP | NA | Y
2015 | 929 | 0664000056 | Waste Management of Ohio (Suburban South Recycling) | 3415 Township Road 447 | Glenford | 43739 |  | Perry | P008 | 1148 HP CAT 3516 Reciprocating LFG Engine | 2015-03-26 | none | RMC Environmental, Inc | 1,148 hp | 3.0 g/hp-hr | 1,268 hp | 0.7 g/hp-hr | 7E | Nitrogen Dioxide | PP | NA | Y
2016 | 905 | 0664000056 | Waste Management of Ohio (Suburban South Recycling) | 3415 Township Road 447 | Glenford | 43739 |  | Perry | P002 | 1148 HP CAT 3516 Reciprocating LFG Engine | 2016-03-31 | none | RMC Environmental, Inc. | 1148 hp | 3.0 g/hp-hr | 1251 hp | 1.1 g/hp-hr | 7E | Nitrogen Dioxide | PP | Y | NA
2016 | 906 | 0664000056 | Waste Management of Ohio (Suburban South Recycling) | 3415 Township Road 447 | Glenford | 43739 |  | Perry | P003 | 1148 HP CAT 3516 Reciprocating LFG Engine | 2016-03-31 | none | RMC Environmental, Inc. | 1148 hp | 3.0 g/hp-hr | 1239 hp | 1.0 g/hp-hr | 7E | Nitrogen Dioxide | PP | Y | NA
2016 | 907 | 0664000056 | Waste Management of Ohio (Suburban South Recycling) | 3415 Township Road 447 | Glenford | 43739 |  | Perry | P004 | 1148 HP CAT 3516 Reciprocating LFG Engine | 2016-03-31 | none | RMC Environmental, Inc. | 1148 hp | 3.0 g/hp-hr | 1240 hp | 1.1 g/hp-hr | 7E | Nitrogen Dioxide | PP | Y | NA
2016 | 908 | 0664000056 | Waste Management of Ohio (Suburban South Recycling) | 3415 Township Road 447 | Glenford | 43739 |  | Perry | P005 | 1148 HP CAT 3516 Reciprocating LFG Engine | 2016-03-31 | none | RMC Environmental, Inc. | 1148 hp | 3.0 g/hp-hr | 1244 hp | 0.6 g/hp-hr | 7E | Nitrogen Dioxide | PP | Y | NA
2016 | 909 | 0664000056 | Waste Management of Ohio (Suburban South Recycling) | 3415 Township Road 447 | Glenford | 43739 |  | Perry | P006 | 1148 HP CAT 3516 Reciprocating LFG Engine | 2016-03-31 | none | RMC Environmental, Inc. | 1148 hp | 3.0 g/hp-hr | 1334 hp | 0.6 b/hp-hr | 7E | Nitrogen Dioxide | PP | Y | NA
2016 | 910 | 0664000056 | Waste Management of Ohio (Suburban South Recycling) | 3415 Township Road 447 | Glenford | 43739 |  | Perry | P007 | 1148 HP CAT 3516 Reciprocating LFG Engine | 2016-03-31 | none | RMC Environmental, Inc. | 1148 hp | 3.0 g/hp-hr | 1288 hp | 0.7 g/hp-hr | 7E | Nitrogen Dioxide | PP | Y | NA
2016 | 911 | 0664000056 | Waste Management of Ohio (Suburban South Recycling) | 3415 Township Road 447 | Glenford | 43739 |  | Perry | P008 | 1148 HP CAT 3516 Reciprocating LFG Engine | 2016-03-31 | none | RMC Environmental, Inc. | 1148 hp | 3.0 g/hp-hr | 1258 hp | 0.8 g/hp-hr | 7E | Nitrogen Dioxide | PP | Y | NA
2015 | 553 | 0285032008 | Wooster Renewable Energy, LLC | 1123 Old Columbus Road | Wooster | 44619 |  | Wayne | B001 | Combined Heat and Process Unit consisting of a 1,475 hp/1,800 rpm/1,100 kw, 4SLB, digester gas engine powering a 1.3 MW generator | 2015-04-21 | Oxygen Sensor that will adjust fuel to air ratios. | Custom Stack Analysis | 1475 Hp | 160 ppm @ 15% O2 2.0 g/hp-hr | 1341 Hp | 116.86 ppm @ 15% O2 1.45 g/hp-hr | 7E | Nitrogen Oxide | PP | NA | Y |  | Yes
2006 | 1397 | 1431070849 | University of Cincinnati | Clifton Campus | Cincinnati | 45221 |  | Hamilton | P007 | 2 MW Diesel fuel-fired internal combustion engine | 2006-07-16 | CATALYTIC OXIDIZER | EQM |  |  |  |  | 7 | Nitrogen Oxide | PASS | NA | Y |  | Yes
2006 | 1398 | 1431070849 | University of Cincinnati | Clifton Campus | Cincinnati | 45221 |  | Hamilton | P007 | 2 MW Diesel fuel-fired internal combustion engine | 2006-07-16 | CATALYTIC OXIDIZER | EQM |  |  |  |  | 7 | Nitrogen Dioxide | PASS | NA | Y |  | Yes
2006 | 1403 | 1431070849 | University of Cincinnati | Clifton Campus | Cincinnati | 45221 |  | Hamilton | P008 | 1.5 MW Diesel fuel-fired internal combustion engine | 2006-08-15 | CATALYTIC OXIDIZER | EQM |  |  |  |  | 7 | Nitrogen Dioxide | PASS | NA | Y |  | Yes
2006 | 1404 | 1431070849 | University of Cincinnati | Clifton Campus | Cincinnati | 45221 |  | Hamilton | P008 | 1.5 MW Diesel fuel-fired internal combustion engine | 2006-08-15 | CATALYTIC OXIDIZER | EQM |  |  |  |  | 7 | Nitrogen Oxide | PASS | NA | Y |  | Yes
2012 | 1323 | 1431070849 | University of Cincinnati | Clifton Campus | Cincinnati | 45221 |  | Hamilton | B108 | 135.6 MMBTU Spreader Stoker Boiler w/ fabric filter, capable of coal, clean cellulosic biomass and/or pelletized fuel (capacity with CCB is 131 MMBtu/hr; capacity with pelletized fuel 90 MMBtu/hr) [This emissions unit was formerly identified as B008 under facility ID 1431070270 and has been incorporated into this facility ID as emissions unit B108 in accordance with Engineering Guide 58.] | 2012-12-13 | Fabric Filter Baghouse and Over-fire Air System | RMC Environmental, Inc. | 135.6 MMBtu/hr (100,000 lb of steam/hr) | 0.70 lb/mmBtu | 76,000 lb of steam/hr | 0.38 lb/mmBtu | 7E | Nitrogen Dioxide | PASS | NA | Y | Testing was conducted to gather new baseline emissions data for NOx and CO after installation of a new Over-fire air system. 100% coal was used to fire the boiler during the test. CO emissions were found to be 59 ppmvd @ 3% O2 and 0.05 lb/mmBtu. Test Report: Report ID# 56838 (attachment ID - 676210) ITT: Report ID# 54681 (attachment ID - 648371)
2012 | 1547 | 1677011251 | Urban Renewables III, LLC | 2460 Akron Peninsula Rd | Akron | 44313 |  | Summit | B001 | Reciprocating internal combustion engine burning landfill gas to drive an electrical generator. | 2012-11-16 | None | Air Compliance Testing Inc | 1000 kW | 220 ppmvd @ 15% O2 | 997.96 kW | 53.9 ppmvd @ 15% O2 | 7E | Nitrogen Dioxide | PASS | NA | Y | Testing to comply with 40 CFR part 60 subpart JJJJ. Emission Standards for Stationary Non-Emergency SI. Stationary SI Landfill/Digester Gas Engines. Table 1 (HP > 500). | Yes
2016 | 2419 | 1677011251 | Urban Renewables III, LLC | 2460 Akron Peninsula Rd | Akron | 44313 |  | Summit | B001 | Reciprocating internal combustion engine burning landfill gas to drive an electrical generator. | 2016-06-01 | n/a | Air Compliance Testing, Inc. | 1137 KW | 3.81 lb/hr | 904KW | 2.67 lb/hr | 7E | Nitrogen Dioxide | PP | Y | Y |  | Yes
2004 | 371 | 0369000025 | PRO-TEC Coating Company | 5500 PRO-TEC Pkwy | Leipsic | 45856 | 9234 | Putnam | P001 | 92.0 MMBtu/hr natural gas-fired continuous annealing furnace, this includes 12 MMBtu/hr auxiliary natural gas-fired burners [the burners are used to maintain the selective catalytic reduction (SCR) control device operating temperature within the recommended range]. With alkaline cleaning, annealing furnace, water quenching and tempering. | 2004-09-16 | selective catalytic reduction unit | AIR COMPLIANCE CONSULTANTS, INC. | 96 mmbtu/hr | 9.6 lbs/hr; 0.10 lbs/mmbtu | 89.2 mmbtu/hr | 1.09 lbs/hr; 0.012 lbs/mmbtu | 7 | Nitrogen Dioxide | PASS | NA | Y
2006 | 536 | 0369000025 | PRO-TEC Coating Company | 5500 PRO-TEC Pkwy | Leipsic | 45856 | 9234 | Putnam | P001 | 92.0 MMBtu/hr natural gas-fired continuous annealing furnace, this includes 12 MMBtu/hr auxiliary natural gas-fired burners [the burners are used to maintain the selective catalytic reduction (SCR) control device operating temperature within the recommended range]. With alkaline cleaning, annealing furnace, water quenching and tempering. | 2006-05-19 | selective catalytic reducing unit (SCR) | Air Compliance Consultants, Inc. |  |  |  |  | 7 | Nitrogen Dioxide | PASS | NA | Y
2006 | 538 | 0369000025 | PRO-TEC Coating Company | 5500 PRO-TEC Pkwy | Leipsic | 45856 | 9234 | Putnam | P001 | 92.0 MMBtu/hr natural gas-fired continuous annealing furnace, this includes 12 MMBtu/hr auxiliary natural gas-fired burners [the burners are used to maintain the selective catalytic reduction (SCR) control device operating temperature within the recommended range]. With alkaline cleaning, annealing furnace, water quenching and tempering. | 2006-05-19 | selective catalytic reducing unit (SCR) | Air Compliance Consultants, Inc. |  |  |  |  | 7 | Nitrogen Oxide | PASS | NA | Y
2013 | 899 | 0369000025 | PRO-TEC Coating Company | 5500 PRO-TEC Pkwy | Leipsic | 45856 | 9234 | Putnam | P001 | 92.0 MMBtu/hr natural gas-fired continuous annealing furnace, this includes 12 MMBtu/hr auxiliary natural gas-fired burners [the burners are used to maintain the selective catalytic reduction (SCR) control device operating temperature within the recommended range]. With alkaline cleaning, annealing furnace, water quenching and tempering. | 2013-04-18 | CGL1-SCR(NOx Reduction Technology): Urea Injection and Selective Catalytic Reduction | Custom Stack Analysis, LLC | 92 MMBtu/hr | 9.2 lbs/hr, 0.10 lb/MMBtu | 83.8 MMBtu/hr | 1.98 lbs/hr, 0.024 lb/MMBtu | 7E | Nitrogen Dioxide | PASS | NA | Y | The average SCR temperature for the test was 635.7 F. The urea injection rate was 7.0 gal/hr.
2013 | 901 | 0369000025 | PRO-TEC Coating Company | 5500 PRO-TEC Pkwy | Leipsic | 45856 | 9234 | Putnam | P001 | 92.0 MMBtu/hr natural gas-fired continuous annealing furnace, this includes 12 MMBtu/hr auxiliary natural gas-fired burners [the burners are used to maintain the selective catalytic reduction (SCR) control device operating temperature within the recommended range]. With alkaline cleaning, annealing furnace, water quenching and tempering. | 2013-05-29 | CGL1-SCR(NOx Reduction Technology): Urea Injection and Selective Catalytic Reduction | Custom Stack Analysis, LLC | 92 MMBtu/hr | 9.2 lbs/hr, 0.10 lb/MMBtu | 85.1 MMBtu/hr | 1.74 lbs/hr, 0.02 lb/MMBtu | 7E | Nitrogen Dioxide | PASS | NA | Y | The SCR temperature averaged 633.7 F for the test. The urea injection rate was 6.9 gal/hr.
2007 | 1492 | 1318538151 | MM Cuyahoga Energy LLC | Cochran and Solon Roads | Solon | 44139 |  | Cuyahoga | P003 | 9.06 MMBtu per hour Caterpillar internal combustion engine for the burning of landfill gas | 2007-09-06 | N/A | CK Environmental |  |  |  |  | 7E | Nitrogen Oxide | PASS | NA | Y
2007 | 1494 | 1318538151 | MM Cuyahoga Energy LLC | Cochran and Solon Roads | Solon | 44139 |  | Cuyahoga | P003 | 9.06 MMBtu per hour Caterpillar internal combustion engine for the burning of landfill gas | 2007-09-06 | N/A | CK Environmental |  |  |  |  | 7E | Nitrogen Dioxide | PASS | NA | Y
2007 | 1497 | 1318538151 | MM Cuyahoga Energy LLC | Cochran and Solon Roads | Solon | 44139 |  | Cuyahoga | P004 | 9.06 MMBtu per hour Caterpillar internal combustion engine for the burning of landfill gas | 2007-09-06 | N/A | CK Environmental |  |  |  |  | 7E | Nitrogen Dioxide | PASS | NA | Y
2007 | 1499 | 1318538151 | MM Cuyahoga Energy LLC | Cochran and Solon Roads | Solon | 44139 |  | Cuyahoga | P004 | 9.06 MMBtu per hour Caterpillar internal combustion engine for the burning of landfill gas | 2007-09-06 | N/A | CK Environmental |  |  |  |  | 7E | Nitrogen Oxide | PASS | NA | Y
2016 | 1464 | 0656005025 | REX Booster Station | Twp Rd 964 | Switzerland Twp. | 43915 |  | Monroe | P004 | Caterpillar 3516C. This is a natural gas fired engine associated with the Generator Unit | 2016-05-04 | C001(Catalytic Converter): Oxidation Catalysts; C002(Catalytic Converter): Oxidation Catalysts; C003(Catalytic Converter): Oxidation Catalysts | Alliance Source Testing | 2175 hp | 0.5 g/hp-hr | 1958 hp | 0.41 g/hp-hr | 7E | Nitrogen Dioxide | PP | Y | NA
2005 | 695 | 0575000174 | Honda of America Mfg., Inc. Anna Engine Plant | 12500 Meranda Road | Anna | 45302 | 9699 | Shelby | P006 | PED Engine Testing dynamometers with nine (9) test stands and two thermal oxidizers | 2005-08-31 | thermal oxidizers | KBD TECHNIC |  |  |  |  | 7 | Nitrogen Oxide | PASS | Y | Y
2005 | 696 | 0575000174 | Honda of America Mfg., Inc. Anna Engine Plant | 12500 Meranda Road | Anna | 45302 | 9699 | Shelby | P006 | PED Engine Testing dynamometers with nine (9) test stands and two thermal oxidizers | 2005-08-31 | thermal oxidizers | KBD TECHNIC |  |  |  |  | 7 | Nitrogen Dioxide | PASS | Y | Y
2007 | 1020 | 0575000174 | Honda of America Mfg., Inc. Anna Engine Plant | 12500 Meranda Road | Anna | 45302 | 9699 | Shelby | P006 | PED Engine Testing dynamometers with nine (9) test stands and two thermal oxidizers | 2007-01-04 | RTO | KBD Technic |  |  |  |  | 7 | Nitrogen Oxide | PASS | NA | Y
2007 | 1021 | 0575000174 | Honda of America Mfg., Inc. Anna Engine Plant | 12500 Meranda Road | Anna | 45302 | 9699 | Shelby | P006 | PED Engine Testing dynamometers with nine (9) test stands and two thermal oxidizers | 2007-01-04 | RTO | KBD Technic |  |  |  |  | 7 | Nitrogen Dioxide | PASS | NA | Y
2016 | 1137 | 0575000174 | Honda of America Mfg., Inc. Anna Engine Plant | 12500 Meranda Road | Anna | 45302 | 9699 | Shelby | P006 | PED Engine Testing dynamometers with nine (9) test stands and two thermal oxidizers | 2016-07-12 | RTO | KBD Technic | 120 liters/hr | 9.27 lb/hr | 120 liters/hr | 1.73 lb/hr | 7E | Nitrogen Oxide | PP | Y | NA
2016 | 1138 | 0575000174 | Honda of America Mfg., Inc. Anna Engine Plant | 12500 Meranda Road | Anna | 45302 | 9699 | Shelby | P006 | PED Engine Testing dynamometers with nine (9) test stands and two thermal oxidizers | 2016-07-13 | RTO | KBD Technic | 120 liters/hr | 9.27 lb/hr | 120 liters/hr | 1.73 lb/hr | 7E | Nitrogen Oxide | PP | Y | NA
2016 | 404 | 0210002039 | Kilgore Compressor Station-Utica Gas Services, LLC | Pontiff Rd | Kilgore | 43988 |  | Carroll | P013 | 605 hp NG-fired generator equipped w/3-way catalyst Baldor IGLC420-2N: engine reconstructed and given new manufacture date 2016-02-23 (see compliance reports) | 2016-04-18 | CC013(Catalytic Converter): Generator #3 - Three-way Catalyst | Alliance Source Testing, Inc. | 605 Hp | 2.0 g/Hp-hr & 160ppm @ 15%O2 & 1.33lb/hr | 555 Hp | 0.014 g/Hp-hr & 3.5 @ 15%O2, & 0.017 lb/hr | 7E | Nitrogen Dioxide | PP | Y | NA
2014 | 1405 | 0370010128 | Jay Plastics-Broscho Fab. Prod. Div. | 1595 W. LONGVIEW AVENUE | Mansfield | 44906 |  | Richland | P006 | 9.361 mmBtu/hr (1531 HP) NG, 4-stroke, LB, SI ICE - Generator #4 | 2014-02-26 | GEN1 cat(Catalytic Converter): 3-way catalytic converter for Generator #1 | Air Compliance Testing, Inc. | 1142 kW | 2.0 grams/bhp-hr | 1089.05 kW | 0.71 grams/bhp-hr | 7E | Nitrogen Dioxide | PASS | NA | Y |  | Yes
2014 | 1408 | 0370010128 | Jay Plastics-Broscho Fab. Prod. Div. | 1595 W. LONGVIEW AVENUE | Mansfield | 44906 |  | Richland | P002 | 11.581 mmBtu/hour (1475 HP), Natural Gas-Fired, 4-Stroke, Rich-Burn, Spark Ignition, Reciprocating Internal Combustion Engine, w/NSCR | 2014-02-28 | GEN1 cat(Catalytic Converter): 3-way catalytic converter for Generator #1 | Air Compliance Testing, Inc. | 1368 kW | 1.30 grams/bhp-hr | 1042.5 kW | 1.10 grams/bhp-hr | 7E | Nitrogen Dioxide | PASS | NA | Y | Low process weight rate determination made by Chad Winebrenner. | Yes
2006 | 411 | 0302020143 | Ford Motor Co.-Lima | 1155 Bible Road | Lima | 45801 |  | Allen | P051 | 4 Cell Engine Testing Dynamometer - East | 2006-05-04 | afterburner | KBD Technic, Inc. |  |  |  |  | 7 | Nitrogen Oxide | PASS | NA | Y
2006 | 412 | 0302020143 | Ford Motor Co.-Lima | 1155 Bible Road | Lima | 45801 |  | Allen | P051 | 4 Cell Engine Testing Dynamometer - East | 2006-05-04 | afterburner | KBD Technic, Inc. |  |  |  |  | 7 | Nitrogen Dioxide | PASS | NA | Y
2006 | 414 | 0302020143 | Ford Motor Co.-Lima | 1155 Bible Road | Lima | 45801 |  | Allen | P050 | 4 Cell Engine Testing Dynamometer - West Block | 2006-05-05 | afterburner | KBD Technic, Inc. |  |  |  |  | 7 | Nitrogen Dioxide | PASS | NA | Y
2006 | 415 | 0302020143 | Ford Motor Co.-Lima | 1155 Bible Road | Lima | 45801 |  | Allen | P050 | 4 Cell Engine Testing Dynamometer - West Block | 2006-05-05 | afterburner | KBD Technic, Inc. |  |  |  |  | 7 | Nitrogen Oxide | PASS | NA | Y
2014 | 1183 | 0302020143 | Ford Motor Co.-Lima | 1155 Bible Road | Lima | 45801 |  | Allen | P051 | 4 Cell Engine Testing Dynamometer - East | 2014-02-13 | RTO #1/P051 (east bank)(Thermal Incinerator): Control eff. based on manufacturer specifications. | KBD Technic | 80 gallons/hr | 40.8 lbs/hr | 32.3 gallons/hr | 5.6 lbs/hr | 7E | Nitrogen Dioxide | PASS | NA | Y | The incinerator combustion temperature averaged 1,299 F during the test. The tested operating rate was less than 90% of the maximum operating rate; however, the test was performed under the worst-case scenario for generation of NOx.
2005 | 1134 | 1409040243 | City of Hamilton Department of Public Utilities | 960 North Third Street | Hamilton | 45011 |  | Butler | B009 | 729 mmBtu/hour Pulverized Coal and Natural Gas-Fired Boiler, equipped with a lime injection dry scrubber system and baghouse, as well as an electrostatic precipitator (ESP) to be used as a back-up control device if the baghouse is not in service | 2005-12-29 | ESP | GE ENERGY |  |  |  |  | 7 | Nitrogen Dioxide | PASS | NA | Y
2005 | 1136 | 1409040243 | City of Hamilton Department of Public Utilities | 960 North Third Street | Hamilton | 45011 |  | Butler | B009 | 729 mmBtu/hour Pulverized Coal and Natural Gas-Fired Boiler, equipped with a lime injection dry scrubber system and baghouse, as well as an electrostatic precipitator (ESP) to be used as a back-up control device if the baghouse is not in service | 2005-12-29 | ESP | GE ENERGY |  |  |  |  | 7 | Nitrogen Oxide | PASS | NA | Y
2015 | 585 | 0322000295 | Bio-Gas Technologies, LTD | 10215 Hoover Road | Milan | 44846 |  | Erie | P001 | 13.9 mmBtu/hr LFG fired IC engine/generator #1 | 2015-01-21 | None | Air Compliance Testing, Inc. | 1600 kW | 5.90 lbs/hr | 1512 kW | 3.28 lbs/hr | 7E | Nitrogen Dioxide | PP | NA | Y |  | Yes
2015 | 588 | 0322000295 | Bio-Gas Technologies, LTD | 10215 Hoover Road | Milan | 44846 |  | Erie | P001 | 13.9 mmBtu/hr LFG fired IC engine/generator #1 | 2015-01-22 | None | Air Compliance Testing, Inc. | 800 kW | 5.06 lbs/hr | 779 kW | 3.66 lbs/hr | 7E | Nitrogen Dioxide | PP | NA | Y |  | Yes
2016 | 509 | 0210012004 | Augusta Compressor Facility- Utica Gas Services, L.L.C. | 8034 Bane Rd NE | East Twp. | 44427 |  | Carroll | P014 | 605-hp Baldor IGLC420-2N Engine Driven Emergency Generator | 2016-09-08 | Oxid. Cat. 3(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 4(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 5(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 6(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 7(Catalytic Converter): | EcoTest Energy Services | 605 Hp | 1.33 lbs/hr, 2.0 g/hp/hr, 160ppmvd@15%O2 | 560 Hp or 92.6% of Max | .17 lb/hr, .14 g/hp/hr, 10 ppmvd@15%O2 | 7E | Nitrogen Dioxide | PP | Y | NA
2016 | 510 | 0210012004 | Augusta Compressor Facility- Utica Gas Services, L.L.C. | 8034 Bane Rd NE | East Twp. | 44427 |  | Carroll | P015 | 605-hp Baldor IGLC420-2N Engine Driven Emergency Generator | 2016-09-08 | Oxid. Cat. 3(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 4(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 5(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 6(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 7(Catalytic Converter): | EcoTest Energy Services | 605 Hp | 1.33 lbs/hr, 2.0 g/hp/hr, 160ppmvd@15%O2 | 560 Hp or 92.6% of Max | .15 lb/hr, .12 g/hp/hr, 9 ppmvd@15%O2 | 7E | Nitrogen Dioxide | PP | Y | NA
2004 | 606 | 0374010117 | Autolite | 1600 N. Union Street | Fostoria | 44830 |  | Seneca | P074 | dynamometer spark plug testing engines. | 2004-11-16 | none | CUSTOM STACK ANALYSIS | 41.98 gallons gasoline/hr | 4.62 lbs/hr | 48.43 gallons gasoline/hr | 3.56 lbs/hr | 7 | Nitrogen Dioxide | PASS | NA | Y
2013 | 962 | 0374010117 | Autolite | 1600 N. Union Street | Fostoria | 44830 |  | Seneca | P074 | dynamometer spark plug testing engines. | 2013-01-10 | None | Air Compliance Testing, Inc. | 51.0 gallons gasoline/hr | 4.08 lbs/hr | 46.2 gallons gasoline/hr | 5.74 lbs/hr | 7E | Nitrogen Dioxide | FAIL | NA | Y | Failure determination made by Andrea Odendahl.
2016 | 535 | 0238000191 | H W CHAIR, LTD | 6291 COUNTY ROAD 77 | MILLERSBURG | 44654 |  | Holmes | B002 | 738 hp (550 kW) 4SRB natural gas engine controlled by a NSCR and AFR to power facility: Waukesha F3521GSI | 2016-06-01 | CCWEG2(Catalytic Converter): catalyst | Custom Stack Analysis | 550 KW | 82 ppm @ 15% O2 or 1.0 g/hp-hr | 354.83 KW | 36.1 ppm @ 15% O2 or 0.46 g/hp-hr | 7E | Nitrogen Dioxide | PP | Y | NA |  | Yes

## Engine CO
REPORTING YEAR | RECORD_NUMBER | FACILITY ID | FACILITY NAME | ADDRESS | CITY | ZIP5 | ZIP4 | COUNTY | EUID | EUID DESCRIPTION | EVALUATION DATE | CONTROL EQUPMENT | COMPANY PERFORMING TEST | MAX RATE | ALLOWABLE RATE | TESTED OPERATING RATE | TESTED EMISSION RATE | METHOD NUMBER | POLLUTANTS | RESULTS | CONFORM | AUDIT | NOTES | COULD_BE_GENERATOR
2008 | 399 | 0125102034 | Dominion - Groveport Compressor Station | 5509 Berger Road | Groveport | 43125 |  | Franklin | B002 | 4200 HP Engine-spark ignition, 2-stroke, lean burn | 2008-11-05 | none | DOMINION TRANSMISSION | 4200 hp | 25.93 lbs/hr | 4066 hp | 17.09 lbs/hr | 10 | CO - Carbon Monoxide | PASS | NA | Y
2008 | 401 | 0125102034 | Dominion - Groveport Compressor Station | 5509 Berger Road | Groveport | 43125 |  | Franklin | B001 | 4200 HP Engine-spark ignition, 2-stroke, lean burn | 2008-11-06 | none | DOMINION TRANSMISSION | 4200 hp | 25.93 lbs/hr | 4072 hp | 20.74 lbs/hr | 10 | CO - Carbon Monoxide | PASS | NA | Y
2008 | 404 | 0125102034 | Dominion - Groveport Compressor Station | 5509 Berger Road | Groveport | 43125 |  | Franklin | B003 | 3200 HP Engine-spark ignition, 2-stroke, lean burn | 2008-11-06 | none | DOMINION TRANSMISSION | 3200 hp | 18.33 lbs/hr | 3149.6 | 13.22 lbs/hr | 10 | CO - Carbon Monoxide | PASS | NA | Y
2011 | 322 | 0250000911 | East Ohio Gas Company - Austintown | 9686 NEW ROAD | Austintown Twp. | 44451 | 9708 | Mahoning | B003 | Natural gas-fired, 4-stroke, lean burn, reciprocating internal combustion engine (Caterpillar G3516TALE) rated at 1,340 HP, 11.9 mmBtu/hr equipped with a selective catalytic reduction system to control carbon monoxide (CO), volatile organic compounds (VOC) and formaldehyde. | 2011-04-28 | Selective catalytic reduction | Environmental Quality Management, Inc. | 1340 HP | 540 ppmvd @ 15% O2, 4.0 g/HP-hr | 1270 HP | 15.4 ppmvd @ 15% O2, 0.13 g/HPhr | 10 | CO - Carbon Monoxide | PASS | NA | Y
2011 | 360 | 0285000366 | East Ohio Gas - Chippewa Station | 17045 Galehouse Road | Doylestown | 44230 |  | Wayne | B009 | 2,370 hp SI ICE pipeline compressor w/catalyst: CAT G3608-LE-TA | 2011-06-28 | oxidation catalyst | Environmental Quality Management, Inc. | 100% ¿10% | 0.91 lb/hr | 93% | 0.06 lb/hr | 10 | CO - Carbon Monoxide | PASS | NA | Y | Permit also requires 93% CO removal, by weight. Testing demonstrated 99% CO removal, by weight. CMS audit was also conducted. Average temperature was 900¿F. MACT requires temp be maintained between 750¿F and 1250¿F. MACT also requires maintain catalyst so that the pressure drop across the catalyst does not change by more than 2 inches of water at 100 percent load plus or minus 10 percent from the pressure drop across the catalyst measured during the initial performance test. The pressure drop across catalyst during the initial test was 1.8 inches water. The pressure drop during this test was 2.0 inches water.
2011 | 361 | 0285000366 | East Ohio Gas - Chippewa Station | 17045 Galehouse Road | Doylestown | 44230 |  | Wayne | B010 | 2,370 hp 4SLB SI ICE; CAT G3608 | 2011-06-28 | oxidation catalyst | Environmental Quality Management, Inc. | 100% ¿10% load | 1.00 lb/hr | 100% +/- 10% load rating | 0.27 lb/hr | 10 | CO - Carbon Monoxide | PASS | NA | Y
2011 | 770 | 0661005002 | Summerfield Compressor Station | between CR-45 and HWY 233 | Caldwell | 43724 |  | Noble | P001 | Natural Gas Engine(1) 1,380 hp engine | 2011-03-29 | Catalytic Silencer | BCMJ Controls | 1,380 Hp | 2.0 g/Hp-hr, 270 -15% O2 ppmvd | 1,104 Hp | 0.01 g/Hp-hr, 1.1 - 15% O2 ppmvd | 10 | CO - Carbon Monoxide | PASS | NA | Y
2011 | 773 | 0661005002 | Summerfield Compressor Station | between CR-45 and HWY 233 | Caldwell | 43724 |  | Noble | P002 | Natural Gas Engine (2) 1,380 hp | 2011-03-29 | Catalytic Silencer | BCMJ Controls | 1,380 Hp | 2.0 g/Hp-hr, 270 -15% O2 ppmvd | 1,104 Hp | 0.08 g/Hp-hr, 6.8 - 15% O2 ppmvd | 10 | CO - Carbon Monoxide | PASS | NA | Y
2011 | 967 | 0857103154 | PINNACLE GAS PRODUCERS LLC | 4220 PINNACLE RD | MORAINE | 45439 |  | Montgomery | B001 | 12 MMBtu/hour (1,626 bhp) pipeline quality gas/natural gas-fired compressor engine | 2011-03-10 | N/A | DTE ENERGY | 1200 RPM | 9.85 LB/HR CO | 1017 RPM | 7.55 LB/HR CO | 10 | CO - Carbon Monoxide | PASS | NA | Y
2011 | 1179 | 1576002033 | East Ohio Gas - Pike Compressor Station | 6024 Kieffer Ave., SW | Canton | 44706 |  | Stark | P001 | Caterpillar G3516-LE-AFR, 1340 hp, 9.9 mmbtu/hr capacity, natural gas fired engine. | 2011-07-08 | CAT-OX | Environmental Quality Management Inc. | 1340 bhp | 1.0 bhp | 80.1, 93.3, 92.0% max load | 0.01 lb CO/hr | 10 | CO - Carbon Monoxide | PASS | NA | Y | Observed 98.8% CO reduction
2011 | 1182 | 1576002033 | East Ohio Gas - Pike Compressor Station | 6024 Kieffer Ave., SW | Canton | 44706 |  | Stark | P002 | Caterpillar G3516-LE-AFR, 1,340 hp, 9.9 mmbtu/hr capacity natural gas fired engine. | 2011-07-08 | CAT-OX | Environmental Quality Management Inc. | 1340 bhp | 1.0 bhp | 94.5, 97.5 & 85.5% max load | 0.01 lb CO/hr | 10 | CO - Carbon Monoxide | PASS | NA | Y | Observed 99.7% CO reduction
2012 | 274 | 0210012015 | Chesapeake Exploration LLC - Snoddy 11-13-5 Pad | Sorrel Road (TWP HWY 620) | Carrollton | 44615 |  | Carroll | P002 | Flash gas compressor with catalyst, 211 hp SI ICE | 2012-10-03 | Catalyst | Alliance Source Testing. | 211 Hp | 540 ppmvd@ 15% O2 | 116 hp | 26.2 ppmvd@15%O2 | 10 | CO - Carbon Monoxide | PASS | NA | Y
2012 | 295 | 0238000050 | MILEY COMPRESSOR STATION | 7531 State Rte 514 | Ripley Twp. | 44611 |  | Holmes | B003 | White Superior 8G-825, 4-cycle, rich burn, natural gas-fired reciprocating pipeline compressor engine, having a maximum capacity of 780hp, controlled by a Non-Selectivie Catalytic Reduction. (Compressor #07701 - B003) | 2012-05-10 | TWC | Windrock Environmental | 780 hp | 23 tpy rolling | >702 hp | 2.19 tpy | 10 | CO - Carbon Monoxide | PASS | NA | Y
2012 | 298 | 0238000050 | MILEY COMPRESSOR STATION | 7531 State Rte 514 | Ripley Twp. | 44611 |  | Holmes | B004 | White Superior 8G-825, 4-cycle, rich burn, natural gas-fired reciprocating pipeline compressor engine, having a maximum capacity of 780hp, controlled by a Non-Selective Catalytic Reduction. (Compressor #07702 - B004) | 2012-05-10 | TWC | Windrock Environmental | 780 hp | 23 tpy rolling | >702 hp | 1.05 tpy | 10 | CO - Carbon Monoxide | PASS | NA | Y
2012 | 323 | 0250000911 | East Ohio Gas Company - Austintown | 9686 NEW ROAD | Austintown Twp. | 44451 | 9708 | Mahoning | B003 | Natural gas-fired, 4-stroke, lean burn, reciprocating internal combustion engine (Caterpillar G3516TALE) rated at 1,340 HP, 11.9 mmBtu/hr equipped with a selective catalytic reduction system to control carbon monoxide (CO), volatile organic compounds (VOC) and formaldehyde. | 2012-03-19 | Selective catalytic reduction | Environmental Quality Management, Inc. | 1340 HP | 540 ppmvd @ 15% O2, 4.0 g/HP-hr | 1264 HP | 9.7 ppmvd @ 15% O2, 0.09 g/HPhr | 10 | CO - Carbon Monoxide | PASS | NA | Y
2012 | 363 | 0285000366 | East Ohio Gas - Chippewa Station | 17045 Galehouse Road | Doylestown | 44230 |  | Wayne | B009 | 2,370 hp SI ICE pipeline compressor w/catalyst: CAT G3608-LE-TA | 2012-06-12 | oxidation catalyst | Environmental Quality Management, Inc. | 100% ¿10% load | 1.0lb/hr | 100% +/- 10% load rating | 0.22lb/hr | 10 | CO - Carbon Monoxide | PASS | NA | Y
2012 | 367 | 0285000366 | East Ohio Gas - Chippewa Station | 17045 Galehouse Road | Doylestown | 44230 |  | Wayne | B010 | 2,370 hp 4SLB SI ICE; CAT G3608 | 2012-06-12 | oxidation catalyst | Environmental Quality Management, Inc. | 100% ¿10% load | 4.0 grams/hp-hr | 100% +/- 10% load rating | .066 grams hp/hr | 10 | CO - Carbon Monoxide | PASS | NA | Y
2012 | 370 | 0285000388 | East Ohio Gas Company - Paint | STATE RTE 250 | Wooster | 44624 |  | Wayne | B002 | Natural gas fired Internal Combustion Engine with max input capacity of 11.9 MMBtu/hr - Caterpillar G3516TALE with 1340 HP, 4-stroke, selective catalytic reduction (SCR) | 2012-08-29 | Three way Catalyst | Environmental Quality Management | 1340 HP | 540 ppm @ 15% O2 and 4.0 g/hp-hr | 1233 HP-hr | 12.97 ppm @ 15% O2 and 0.11 g/hp-hr | 10 | CO - Carbon Monoxide | PASS | NA | Y
2012 | 730 | 0661005002 | Summerfield Compressor Station | between CR-45 and HWY 233 | Caldwell | 43724 |  | Noble | P001 | Natural Gas Engine(1) 1,380 hp engine | 2012-03-12 | Catalytic Silencer | BCMJ Controls | 1,380 Hp | 2.0 g/Hp-hr, 270 -15% O2 ppmvd | 1,104 Hp | 0.03/Hp-hr, 2.4 15% O2 ppmvd | 10 | CO - Carbon Monoxide | PASS | NA | Y
2012 | 734 | 0661005002 | Summerfield Compressor Station | between CR-45 and HWY 233 | Caldwell | 43724 |  | Noble | P002 | Natural Gas Engine (2) 1,380 hp | 2012-03-12 | Catalytic Silencer | BCMJ Controls | 1,380 Hp | 2.0 g/Hp-hr, 270 -15% O2 ppmvd | 1,104 Hp | 0.03/Hp-hr, 3.1 15% O2 ppmvd | 10 | CO - Carbon Monoxide | PASS | NA | Y
2013 | 148 | 0210012004 | Augusta Compressor Facility- Utica Gas Services, L.L.C. | 8034 Bane Rd NE | East Twp. | 44427 |  | Carroll | P012 | 1,775-hp Caterpillar G3606 Compressor Engine w/ Oxidation Catalyst | 2013-10-08 | Oxid. Cat. 3(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 4(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 5(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 6(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 7(Catalytic Converter): | Alliance Source Testing | 1775 Hp | 1.18 lbs/hr, 2.0 g/hp/hr, 270ppmvd@15%O2 | 1703 Hp or 96% of Max | 0.25 lbs/hr, 0.1 g/hp/hr, 9.5 ppmvd@15%O2 | 10 | CO - Carbon Monoxide | PASS | NA | Y
2013 | 150 | 0210012004 | Augusta Compressor Facility- Utica Gas Services, L.L.C. | 8034 Bane Rd NE | East Twp. | 44427 |  | Carroll | P013 | 1,775-hp Caterpillar G3606 Compressor Engine w/ Oxidation Catalyst | 2013-10-08 | Oxid. Cat. 3(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 4(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 5(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 6(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 7(Catalytic Converter): | Alliance Source Testing | 1775 Hp | 1.18 lbs/hr, 2.0 g/hp/hr, 270ppmvd@15%O2 | 1680 Hp or 95% of Max | 0.24 lbs/hr, 0.07 g/hp/hr, 9.7 ppmvd@15%O2 | 10 | CO - Carbon Monoxide | PASS | NA | Y
2013 | 159 | 0210012004 | Augusta Compressor Facility- Utica Gas Services, L.L.C. | 8034 Bane Rd NE | East Twp. | 44427 |  | Carroll | P006 | 1,775-hp Caterpillar G3606 Compressor Engine w/ Oxidation Catalyst | 2013-10-09 | Oxid. Cat. 3(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 4(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 5(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 6(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 7(Catalytic Converter): | Alliance Source Testing | 1775 Hp | 1.18 lbs/hr, 2.0 g/hp/hr, 270ppmvd@15%O2 | 1651 Hp or 93% of Max | 0.11 lbs/hr, 0.03 g/hp/hr, 4.5 ppmvd@15%O2 | 10 | CO - Carbon Monoxide | PASS | NA | Y
2013 | 163 | 0210012004 | Augusta Compressor Facility- Utica Gas Services, L.L.C. | 8034 Bane Rd NE | East Twp. | 44427 |  | Carroll | P007 | 1,775-hp Caterpillar G3606 Compressor Engine w/ Oxidation Catalyst | 2013-10-09 | Oxid. Cat. 3(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 4(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 5(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 6(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 7(Catalytic Converter): | Alliance Source Testing | 1775 Hp | 1.18 lbs/hr, 2.0 g/hp/hr, 270ppmvd@15%O2 | 1624 Hp or 91% of Max | 0.10 lbs/hr, 0.03 g/hp/hr, 4.0 ppmvd@15%O2 | 10 | CO - Carbon Monoxide | PASS | NA | Y
2013 | 167 | 0210012004 | Augusta Compressor Facility- Utica Gas Services, L.L.C. | 8034 Bane Rd NE | East Twp. | 44427 |  | Carroll | P008 | 1,775-hp Caterpillar G3606 Compressor Engine w/ Oxidation Catalyst | 2013-10-09 | Oxid. Cat. 3(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 4(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 5(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 6(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 7(Catalytic Converter): | Alliance Source Testing | 1775 Hp | 1.18 lbs/hr, 2.0 g/hp/hr, 270ppmvd@15%O2 | 1610 Hp or 91% of Max | 0.27 lbs/hr, 0.1 g/hp/hr, 10.8 ppmvd@15%O2 | 10 | CO - Carbon Monoxide | PASS | NA | Y
2013 | 187 | 0210002013 | Chesapeake Exploration LLC - Slates 16-12-5 | County Highway 59 | Kilgore | 43903 |  | Carroll | P002 | 211 hp CAT G3306TA Flash Gas Compressor equipped with catalyst. For this EU, GP12.1 covers one or multiple stationary natural gas-fired spark ignition (SI) internal combustion engines (ICE) with a combined total horsepower (HP) of no more than 1,800 HP for the site. Includes 2007 and later model year engines manufactured after the applicable effective date identified in 40 CFR 60.4230(a)(3) and engines manufactured before the effective date of the NSPS, where compliance with the Part 60 Subpart JJJJ emissions standards for the same size engine can be met by retrofitting the engine with a control device and demonstrated through stack testing. | 2013-08-08 | N/A | Alliance Source Testing, Inc. | 211 bhp | 270 ppmvd@15%O2 | 96% or 202 bHp | 66.0 ppmvd@15%O2 | 10 | CO - Carbon Monoxide | PASS | NA | Y | Caterpillar 215 bhp Natural Gas Engine G6X08478
2013 | 190 | 0210002014 | Chesapeake Exploration LLC - Scott 24-12-5 Pad | Ponder Rd | Kilgore | 44615 |  | Carroll | P002 | 211 hp CAT G3306TA flash gas compressor equipped with catalyst. For this EU, GP12.1 covers one or multiple stationary natural gas-fired spark ignition (SI) internal combustion engines (ICE) with a combined total horsepower (HP) of no more than 1,800 HP for the site. Includes 2007 and later model year engines manufactured after the applicable effective date identified in 40 CFR 60.4230(a)(3) and engines manufactured before the effective date of the NSPS, where compliance with the Part 60 Subpart JJJJ emissions standards for the same size engine can be met by retrofitting the engine with a control device and demonstrated through stack testing. | 2013-05-22 | Catalyst | Alliance Source Testing, Inc. | 215Hp | 11.5 lb/hr or 4.0 g/hp-hr | 162 hp=75% | 0.1 lb/hr and 0.4 g/hp-hr | 10 | CO - Carbon Monoxide | PASS | NA | Y | Testing was accepted a the rate of 75% of max given that the facility is aware if they increase above this rate by more than 10% of the tested rate they will have to test again.
2013 | 192 | 0210012002 | Utica Gas Services, LLC-Carrollton Compressor Facility | 2098 Panda Road SE | Carrollton | 44615 |  | Carroll | P009 | 1,775 HP natural gas-fired Caterpillar G3606 engine #6 equipped with an oxidation catalyst | 2013-03-06 | Oxid. Cat.(Catalytic Converter): Oxidative Catalyst | Air Hygiene Inc. | 1775 Hp | CO<270 ppmvd @ 15% O2 and 2.0 g/hp-hr | 1652 Hp | 7.11ppmvd @ 15 % O2 and 0.04 g/hp-hr | 10 | CO - Carbon Monoxide | PASS | NA | Y
2013 | 196 | 0210012002 | Utica Gas Services, LLC-Carrollton Compressor Facility | 2098 Panda Road SE | Carrollton | 44615 |  | Carroll | P010 | 1,775 HP natural gas-fired Caterpillar G3606 engine #7 equipped with an oxidation catalyst | 2013-03-06 | Oxid. Cat.(Catalytic Converter): Oxidative Catalyst | Air Hygiene, Inc. | 1775 Hp | CO<270 ppmvd @ 15% O2 and 2.0 g/hp-hr | 1608 Hp | 5.85ppmvd @ 15 % O2 and 0.04 g/hp-hr | 10 | CO - Carbon Monoxide | PASS | NA | Y
2013 | 200 | 0210012002 | Utica Gas Services, LLC-Carrollton Compressor Facility | 2098 Panda Road SE | Carrollton | 44615 |  | Carroll | P006 | 1,775 HP natural gas-fired Caterpillar G3606 engine #3 equipped with an oxidation catalyst | 2013-03-07 | Oxid. Cat.(Catalytic Converter): Oxidative Catalyst | Alliance Source Testing | 1775 Hp | CO<270 ppmvd @ 15% O2 and 2.0 g/hp-hr | 1666 hp | 4.1ppmvd @ 15 % O2 and 0.02 g/hp-hr | 10 | CO - Carbon Monoxide | PASS | NA | Y
2013 | 202 | 0210012002 | Utica Gas Services, LLC-Carrollton Compressor Facility | 2098 Panda Road SE | Carrollton | 44615 |  | Carroll | P007 | 1,775 HP natural gas-fired Caterpillar G3606 engine #4 equipped with an oxidation catalyst | 2013-03-07 | Oxid. Cat.(Catalytic Converter): Oxidative Catalyst | Alliance Source Testing | 1775 Hp | CO<270 ppmvd @ 15% O2 and 2.0 g/hp-hr | 1690 | 8.1ppmvd @ 15 % O2 and 0.1 g/hp-hr | 10 | CO - Carbon Monoxide | PASS | NA | Y
2013 | 205 | 0210012002 | Utica Gas Services, LLC-Carrollton Compressor Facility | 2098 Panda Road SE | Carrollton | 44615 |  | Carroll | P008 | 1,775 HP natural gas-fired Caterpillar G3606 engine #5 equipped with an oxidation catalyst | 2013-03-07 | Oxid. Cat.(Catalytic Converter): Oxidative Catalyst | Air Hygiene Inc. | 1775 Hp | CO<270 ppmvd @ 15% O2 and 2.0 g/hp-hr | 1657 | 8.6 ppmvd @ 15 % O2 and 0.05 g/hp-hr | 10 | CO - Carbon Monoxide | PASS | NA | Y
2013 | 209 | 0210012002 | Utica Gas Services, LLC-Carrollton Compressor Facility | 2098 Panda Road SE | Carrollton | 44615 |  | Carroll | P011 | 1,775 HP natural gas-fired Caterpillar G3606 engine #8 equipped with an oxidation catalyst | 2013-03-07 | Oxid. Cat.(Catalytic Converter): Oxidative Catalyst | Air Hygiene, Inc. | 1775 hp | CO<270 ppmvd @ 15% O2 and 2.0 g/hp-hr | 1654 hp | 3.96ppmvd @ 15 % O2 and 0.02 g/hp-hr | 10 | CO - Carbon Monoxide | PASS | NA | Y
2013 | 211 | 0210012002 | Utica Gas Services, LLC-Carrollton Compressor Facility | 2098 Panda Road SE | Carrollton | 44615 |  | Carroll | P012 | 1,775 HP natural gas-fired Caterpillar G3606 engine #9 equipped with an oxidation catalyst | 2013-03-08 | Oxid. Cat.(Catalytic Converter): Oxidative Catalyst | Air Hygiene, Inc | 1775 hp | CO<270 ppmvd @ 15% O2 and 2.0 g/hp-hr | 1661 Hp | 4.77ppmvd @ 15 % O2 and 0.03 g/hp-hr | 10 | CO - Carbon Monoxide | PASS | NA | Y
2013 | 215 | 0210012002 | Utica Gas Services, LLC-Carrollton Compressor Facility | 2098 Panda Road SE | Carrollton | 44615 |  | Carroll | P004 | 1,775 HP natural gas-fired Caterpillar G3606 engine #1 equipped with an oxidation catalyst. | 2013-05-01 | Oxid. Cat.(Catalytic Converter): Oxidative Catalyst | Air Hygiene Inc. | 1775 HP | 540 ppmvd @ 15% O2 or 4g/hp-hr | 1678 HP | 9.58 ppmvd @ 15% O2 and .01 g/hp-hr | 10 | CO - Carbon Monoxide | PASS | NA | Y
2013 | 217 | 0210012002 | Utica Gas Services, LLC-Carrollton Compressor Facility | 2098 Panda Road SE | Carrollton | 44615 |  | Carroll | P005 | 1,775 HP natural gas-fired Caterpillar G3606 engine #2 equipped with an oxidation catalyst | 2013-05-01 | Oxid. Cat.(Catalytic Converter): Oxidative Catalyst | Air Hygiene Inc. | 1775 HP | 540 ppmvd @ 15% O2 or 4g/hp-hr | 1620 HP | 2.95 ppmvd @ 15% O2 and .01 g/hp-hr | 10 | CO - Carbon Monoxide | PASS | NA | Y
2013 | 221 | 0210012002 | Utica Gas Services, LLC-Carrollton Compressor Facility | 2098 Panda Road SE | Carrollton | 44615 |  | Carroll | P013 | 1,775 HP natural gas-fired Caterpillar G3606 engine #10equipped with an oxidation catalyst | 2013-05-01 | Oxid. Cat.(Catalytic Converter): Oxidative Catalyst | Air Hygiene Inc. | 1775 HP | 540 ppmvd @ 15% O2 or 4g/hp-hr | 1625 HP | 4.8 ppmvd @ 15% and 0 g/hp-hr | 10 | CO - Carbon Monoxide | PASS | NA | Y
2013 | 227 | 0210012004 | Augusta Compressor Facility- Utica Gas Services, L.L.C. | 8034 Bane Rd NE | East Twp. | 44427 |  | Carroll | P006 | 1,775-hp Caterpillar G3606 Compressor Engine w/ Oxidation Catalyst | 2013-10-08 | Oxid. Cat. 3(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 4(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 5(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 6(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 7(Catalytic Converter): | Alliance Source Testing | 1775 Hp | 1.18 lbs/hr, 2.0 g/hp/hr, 270ppmvd@15%O2 | 1651 Hp or 93% of Max | 0.11 lbs/hr, 0.03 g/hp/hr, 4.5 ppmvd@15%O2 | 10 | CO - Carbon Monoxide | PASS | NA | Y
2013 | 228 | 0210012004 | Augusta Compressor Facility- Utica Gas Services, L.L.C. | 8034 Bane Rd NE | East Twp. | 44427 |  | Carroll | P007 | 1,775-hp Caterpillar G3606 Compressor Engine w/ Oxidation Catalyst | 2013-10-08 | Oxid. Cat. 3(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 4(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 5(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 6(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 7(Catalytic Converter): | Alliance Source Testing | 1775 Hp | 1.18 lbs/hr, 2.0 g/hp/hr, 270ppmvd@15%O2 | 1624 Hp or 91% of Max | 0.10 lbs/hr, 0.03 g/hp/hr, 4.0 ppmvd@15%O2 | 10 | CO - Carbon Monoxide | PASS | NA | Y
2013 | 231 | 0210012004 | Augusta Compressor Facility- Utica Gas Services, L.L.C. | 8034 Bane Rd NE | East Twp. | 44427 |  | Carroll | P008 | 1,775-hp Caterpillar G3606 Compressor Engine w/ Oxidation Catalyst | 2013-10-08 | Oxid. Cat. 3(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 4(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 5(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 6(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 7(Catalytic Converter): | Alliance Source Testing | 1775 Hp | 1.18 lbs/hr, 2.0 g/hp/hr, 270ppmvd@15%O2 | 1610 Hp or 91% of Max | 0.27 lbs/hr, 0.1 g/hp/hr, 10.8 ppmvd@15%O2 | 10 | CO - Carbon Monoxide | PASS | NA | Y
2013 | 234 | 0210012004 | Augusta Compressor Facility- Utica Gas Services, L.L.C. | 8034 Bane Rd NE | East Twp. | 44427 |  | Carroll | P009 | 1,775-hp Caterpillar G3606 Compressor Engine w/ Oxidation Catalyst | 2013-10-08 | Oxid. Cat. 3(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 4(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 5(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 6(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 7(Catalytic Converter): | Alliance Source Testing | 1775 Hp | 1.18 lbs/hr, 2.0 g/hp/hr, 270ppmvd@15%O2 | 1724 Hp or 97% of Max | 0.06 lbs/hr, 0.02 g/hp/hr, 2.4 ppmvd@15%O2 | 10 | CO - Carbon Monoxide | PASS | NA | Y
2013 | 237 | 0210012004 | Augusta Compressor Facility- Utica Gas Services, L.L.C. | 8034 Bane Rd NE | East Twp. | 44427 |  | Carroll | P010 | 1,775-hp Caterpillar G3606 Compressor Engine w/ Oxidation Catalyst | 2013-10-08 | Oxid. Cat. 3(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 4(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 5(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 6(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 7(Catalytic Converter): | Alliance Source Testing | 1775 Hp | 1.18 lbs/hr, 2.0 g/hp/hr, 270ppmvd@15%O2 | 1621 Hp or 91% of Max | 0.16 lbs/hr, 0.05g/hp/hr, 6.6 ppmvd@15%O2 | 10 | CO - Carbon Monoxide | PASS | NA | Y
2013 | 241 | 0210012004 | Augusta Compressor Facility- Utica Gas Services, L.L.C. | 8034 Bane Rd NE | East Twp. | 44427 |  | Carroll | P011 | 1,775-hp Caterpillar G3606 Compressor Engine w/ Oxidation Catalyst | 2013-10-08 | Oxid. Cat. 3(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 4(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 5(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 6(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 7(Catalytic Converter): | Alliance Source Testing | 1775 Hp | 1.18 lbs/hr, 2.0 g/hp/hr, 270ppmvd@15%O2 | 1632 Hp or 92% of Max | 0.07 lbs/hr, 0.02 g/hp/hr, 2.8 ppmvd@15%O2 | 10 | CO - Carbon Monoxide | PASS | NA | Y
2013 | 245 | 0210012004 | Augusta Compressor Facility- Utica Gas Services, L.L.C. | 8034 Bane Rd NE | East Twp. | 44427 |  | Carroll | P009 | 1,775-hp Caterpillar G3606 Compressor Engine w/ Oxidation Catalyst | 2013-10-09 | Oxid. Cat. 3(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 4(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 5(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 6(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 7(Catalytic Converter): | Alliance Source Testing | 1775 Hp | 1.18 lbs/hr, 2.0 g/hp/hr, 270ppmvd@15%O2 | 1724 Hp or 97% of Max | 0.06 lbs/hr, 0.02 g/hp/hr, 2.4 ppmvd@15%O2 | 10 | CO - Carbon Monoxide | PASS | NA | Y
2013 | 279 | 0210012004 | Augusta Compressor Facility- Utica Gas Services, L.L.C. | 8034 Bane Rd NE | East Twp. | 44427 |  | Carroll | P010 | 1,775-hp Caterpillar G3606 Compressor Engine w/ Oxidation Catalyst | 2013-10-09 | Oxid. Cat. 3(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 4(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 5(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 6(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 7(Catalytic Converter): | Alliance Source Testing | 1775 Hp | 1.18 lbs/hr, 2.0 g/hp/hr, 270ppmvd@15%O2 | 1621 Hp or 91% of Max | 0.16 lbs/hr, 0.05g/hp/hr, 6.6 ppmvd@15%O2 | 10 | CO - Carbon Monoxide | PASS | NA | Y
2013 | 282 | 0210012004 | Augusta Compressor Facility- Utica Gas Services, L.L.C. | 8034 Bane Rd NE | East Twp. | 44427 |  | Carroll | P011 | 1,775-hp Caterpillar G3606 Compressor Engine w/ Oxidation Catalyst | 2013-10-09 | Oxid. Cat. 3(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 4(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 5(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 6(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 7(Catalytic Converter): | Alliance Source Testing | 1775 Hp | 1.18 lbs/hr, 2.0 g/hp/hr, 270ppmvd@15%O2 | 1632 Hp or 92% of Max | 0.07 lbs/hr, 0.02 g/hp/hr, 2.8 ppmvd@15%O2 | 10 | CO - Carbon Monoxide | PASS | NA | Y
2013 | 284 | 0210012004 | Augusta Compressor Facility- Utica Gas Services, L.L.C. | 8034 Bane Rd NE | East Twp. | 44427 |  | Carroll | P012 | 1,775-hp Caterpillar G3606 Compressor Engine w/ Oxidation Catalyst | 2013-10-09 | Oxid. Cat. 3(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 4(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 5(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 6(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 7(Catalytic Converter): | Alliance Source Testing | 1775 Hp | 1.18 lbs/hr, 2.0 g/hp/hr, 270ppmvd@15%O2 | 1703 Hp or 96% of Max | 0.25 lbs/hr, 0.1 g/hp/hr, 9.5 ppmvd@15%O2 | 10 | CO - Carbon Monoxide | PASS | NA | Y
2013 | 288 | 0210012004 | Augusta Compressor Facility- Utica Gas Services, L.L.C. | 8034 Bane Rd NE | East Twp. | 44427 |  | Carroll | P013 | 1,775-hp Caterpillar G3606 Compressor Engine w/ Oxidation Catalyst | 2013-10-09 | Oxid. Cat. 3(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 4(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 5(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 6(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 7(Catalytic Converter): | Alliance Source Testing | 1775 Hp | 1.18 lbs/hr, 2.0 g/hp/hr, 270ppmvd@15%O2 | 1680 Hp or 95% of Max | 0.24 lbs/hr, 0.07 g/hp/hr, 9.7 ppmvd@15%O2 | 10 | CO - Carbon Monoxide | PASS | NA | Y
2013 | 296 | 0210012004 | Augusta Compressor Facility- Utica Gas Services, L.L.C. | 8034 Bane Rd NE | East Twp. | 44427 |  | Carroll | P006 | 1,775-hp Caterpillar G3606 Compressor Engine w/ Oxidation Catalyst | 2013-10-10 | Oxid. Cat. 3(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 4(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 5(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 6(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 7(Catalytic Converter): | Alliance Source Testing | 1775 Hp | 1.18 lbs/hr, 2.0 g/hp/hr, 270ppmvd@15%O2 | 1651 Hp or 93% of Max | 0.11 lbs/hr, 0.03 g/hp/hr, 4.5 ppmvd@15%O2 | 10 | CO - Carbon Monoxide | PASS | NA | Y
2013 | 300 | 0210012004 | Augusta Compressor Facility- Utica Gas Services, L.L.C. | 8034 Bane Rd NE | East Twp. | 44427 |  | Carroll | P007 | 1,775-hp Caterpillar G3606 Compressor Engine w/ Oxidation Catalyst | 2013-10-10 | Oxid. Cat. 3(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 4(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 5(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 6(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 7(Catalytic Converter): | Alliance Source Testing | 1775 Hp | 1.18 lbs/hr, 2.0 g/hp/hr, 270ppmvd@15%O2 | 1624 Hp or 91% of Max | 0.10 lbs/hr, 0.03 g/hp/hr, 4.0 ppmvd@15%O2 | 10 | CO - Carbon Monoxide | PASS | NA | Y
2013 | 301 | 0210012004 | Augusta Compressor Facility- Utica Gas Services, L.L.C. | 8034 Bane Rd NE | East Twp. | 44427 |  | Carroll | P008 | 1,775-hp Caterpillar G3606 Compressor Engine w/ Oxidation Catalyst | 2013-10-10 | Oxid. Cat. 3(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 4(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 5(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 6(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 7(Catalytic Converter): | Alliance Source Testing | 1775 Hp | 1.18 lbs/hr, 2.0 g/hp/hr, 270ppmvd@15%O2 | 1610 Hp or 91% of Max | 0.27 lbs/hr, 0.1 g/hp/hr, 10.8 ppmvd@15%O2 | 10 | CO - Carbon Monoxide | PASS | NA | Y
2013 | 305 | 0210012004 | Augusta Compressor Facility- Utica Gas Services, L.L.C. | 8034 Bane Rd NE | East Twp. | 44427 |  | Carroll | P009 | 1,775-hp Caterpillar G3606 Compressor Engine w/ Oxidation Catalyst | 2013-10-10 | Oxid. Cat. 3(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 4(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 5(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 6(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 7(Catalytic Converter): | Alliance Source Testing | 1775 Hp | 1.18 lbs/hr, 2.0 g/hp/hr, 270ppmvd@15%O2 | 1724 Hp or 97% of Max | 0.06 lbs/hr, 0.02 g/hp/hr, 2.4 ppmvd@15%O2 | 10 | CO - Carbon Monoxide | PASS | NA | Y
2013 | 309 | 0210012004 | Augusta Compressor Facility- Utica Gas Services, L.L.C. | 8034 Bane Rd NE | East Twp. | 44427 |  | Carroll | P010 | 1,775-hp Caterpillar G3606 Compressor Engine w/ Oxidation Catalyst | 2013-10-10 | Oxid. Cat. 3(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 4(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 5(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 6(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 7(Catalytic Converter): | Alliance Source Testing | 1775 Hp | 1.18 lbs/hr, 2.0 g/hp/hr, 270ppmvd@15%O2 | 1621 Hp or 91% of Max | 0.16 lbs/hr, 0.05g/hp/hr, 6.6 ppmvd@15%O2 | 10 | CO - Carbon Monoxide | PASS | NA | Y
2013 | 310 | 0210012004 | Augusta Compressor Facility- Utica Gas Services, L.L.C. | 8034 Bane Rd NE | East Twp. | 44427 |  | Carroll | P011 | 1,775-hp Caterpillar G3606 Compressor Engine w/ Oxidation Catalyst | 2013-10-10 | Oxid. Cat. 3(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 4(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 5(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 6(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 7(Catalytic Converter): | Alliance Source Testing | 1775 Hp | 1.18 lbs/hr, 2.0 g/hp/hr, 270ppmvd@15%O2 | 1632 Hp or 92% of Max | 0.07 lbs/hr, 0.02 g/hp/hr, 2.8 ppmvd@15%O2 | 10 | CO - Carbon Monoxide | PASS | NA | Y
2013 | 313 | 0210012004 | Augusta Compressor Facility- Utica Gas Services, L.L.C. | 8034 Bane Rd NE | East Twp. | 44427 |  | Carroll | P012 | 1,775-hp Caterpillar G3606 Compressor Engine w/ Oxidation Catalyst | 2013-10-10 | Oxid. Cat. 3(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 4(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 5(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 6(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 7(Catalytic Converter): | Alliance Source Testing | 1775 Hp | 1.18 lbs/hr, 2.0 g/hp/hr, 270ppmvd@15%O2 | 1703 Hp or 96% of Max | 0.25 lbs/hr, 0.1 g/hp/hr, 9.5 ppmvd@15%O2 | 10 | CO - Carbon Monoxide | PASS | NA | Y
2013 | 317 | 0210012004 | Augusta Compressor Facility- Utica Gas Services, L.L.C. | 8034 Bane Rd NE | East Twp. | 44427 |  | Carroll | P013 | 1,775-hp Caterpillar G3606 Compressor Engine w/ Oxidation Catalyst | 2013-10-10 | Oxid. Cat. 3(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 4(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 5(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 6(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 7(Catalytic Converter): | Alliance Source Testing | 1775 Hp | 1.18 lbs/hr, 2.0 g/hp/hr, 270ppmvd@15%O2 | 1680 Hp or 95% of Max | 0.24 lbs/hr, 0.07 g/hp/hr, 9.7 ppmvd@15%O2 | 10 | CO - Carbon Monoxide | PASS | NA | Y
2013 | 328 | 0210012008 | Chesapeake Exploration LLC - Mangun 22-15-5 Pad | Lustre Rd NE | Carrollton | 44607 |  | Carroll | P002 | 145 hp Spark Ignition Internal Combustion Engine | 2013-03-06 | Catalyst | Alliance Source Testing | 145 hp | 270 ppmvd @15% O2 | 130 | 24.9 ppmvd @ 15% O2 | 10 | CO - Carbon Monoxide | PASS | NA | Y
2013 | 337 | 0210012020 | Chesapeake Exploration LLC - Rutledge 10-14-6 Pad | Canyon Rd SW | Carrollton | 44615 |  | Carroll | P002 | Natural Gas Engines | 2013-05-22 | Catalyst | Alliance Source Testing, Inc. | 215 Hp | 11.5 lb/hr or 4.0 g-hp/hr | 195 hp = 90% | 0.3 lb/hr and 0.7 g-hp/hr | 10 | CO - Carbon Monoxide | PASS | NA | Y
2013 | 343 | 0210012024 | Chesapeake Exploration LLC - Brunk 32-13-5 Pad | Pinto Rd SE | Carrollton | 44615 |  | Carroll | P002 | Natural Gas Engines | 2013-08-09 | N/A | Alliance Source Testing | 215 bhp | 270 ppmvd @ 15% O@ | 91% or 196 bhp | 67.7 ppmvd@15%O2 | 10 | CO - Carbon Monoxide | PASS | NA | Y | Caterpillar 215 hp Natural Gas engine serial# 4FD04197
2013 | 348 | 0210012025 | Chesapeake Exploration LLC - Davis Farms 2-14-6 Pad | Pillar Rd SW | Carrollton | 44615 |  | Carroll | P002 | Natural Gas Engines | 2013-08-08 | N/A | Alliance Source Testing, Inc. | 215 bhp | 270 ppmvd@15%O2 | 91% or 197 bhp | 19.4 ppmvd@15%O2 | 10 | CO - Carbon Monoxide | PASS | NA | Y | Caterpillar 215 hp Natural Gas Engine serial# 4FD04263
2013 | 349 | 0215050202 | BRINKER COMPRESSOR STATION | 5213 Leetonia Rd | Leetonia | 44431 |  | Columbiana | B001 | Ingersoll-Rand 38 KVG, serial no. 83NL844, 4-stroke rich burn, natural gas fired reciprocating internal combustion engine (RICE) having a maximum capacity of 10.3 mmBTU/hr (880 BHP). Compressor no.15501. | 2013-12-04 | CAT1(Catalytic Converter): COMPR #15501 CATLAYTIC CONVERTER; CAT2(Catalytic Converter): COMPR 315502 CATALYTIC CONVERTER; CAT3(Catalytic Converter): COMPR #15503 CATALYTIC CONVERTER | Alliance Source Testing, Inc. | 880 Hp | 270 ppmvd @ 15% O2 | 815 Hp | 17.4 ppmvd @ 15% O2 | 10 | CO - Carbon Monoxide | PASS | NA | Y | B001 Tested on 1/31/14 because of span selection error and B002/B003 tested on 12/2/13.
2013 | 350 | 0215050202 | BRINKER COMPRESSOR STATION | 5213 Leetonia Rd | Leetonia | 44431 |  | Columbiana | B002 | Ingersoll-Rand 38 KVG, serial no. 83NL845, 4-stroke rich burn, natural gas fired reciprocating internal combustion engine (RICE) having a maximum capacity of 10.3 mmBTU/hr (880 BHP). Compressor no.15502. | 2013-12-04 | CAT1(Catalytic Converter): COMPR #15501 CATLAYTIC CONVERTER; CAT2(Catalytic Converter): COMPR 315502 CATALYTIC CONVERTER; CAT3(Catalytic Converter): COMPR #15503 CATALYTIC CONVERTER | Alliance Source Testing, Inc. | 880 Hp | 270 ppmvd @ 15% O2 | 833 Hp | 2.3 ppmvd @ 15% O2 | 10 | CO - Carbon Monoxide | PASS | NA | Y | B001 Tested on 1/31/14 because of span selection error and B002/B003 tested on 12/2/13.
2013 | 351 | 0215050202 | BRINKER COMPRESSOR STATION | 5213 Leetonia Rd | Leetonia | 44431 |  | Columbiana | B003 | Ingersoll-Rand 48 KVSFT 563, serial no. 48FT563, 4-stroke lean burn, natural gas fired reciprocating internal combustion engine (RICE) having a maximum capacity of 13.7 mmBTU/hr (1,320 BHP). Compressor no.15503. | 2013-12-04 | CAT1(Catalytic Converter): COMPR #15501 CATLAYTIC CONVERTER; CAT2(Catalytic Converter): COMPR 315502 CATALYTIC CONVERTER; CAT3(Catalytic Converter): COMPR #15503 CATALYTIC CONVERTER | Alliance Source Testing, Inc. | 1320 Hp | 47 ppmvd @ 15% O2 | 1251 Hp | 4.9 ppmvd @ 15% O2 | 10 | CO - Carbon Monoxide | PASS | NA | Y | B001 Tested on 1/31/14 because of span selection error and B002/B003 tested on 12/2/13.
2013 | 668 | 0285000366 | East Ohio Gas - Chippewa Station | 17045 Galehouse Road | Doylestown | 44230 |  | Wayne | B009 | 2,370 hp SI ICE pipeline compressor w/catalyst: CAT G3608-LE-TA | 2013-06-11 | Engine 5 Converter(Catalytic Converter): Engine #5; Cat B010(Catalytic Converter): Catalytic Converter for B010, engine #6 | Environmental Quality Management, Inc. | 2370 HP | 1.0 lb/hr and 93% Removal efficiency | 93% of max | 0.13 lb/hr and 98.5% removal | 10 | CO - Carbon Monoxide | PASS | NA | Y
2013 | 669 | 0285000366 | East Ohio Gas - Chippewa Station | 17045 Galehouse Road | Doylestown | 44230 |  | Wayne | B010 | 2,370 hp 4SLB SI ICE; CAT G3608 | 2013-06-11 | Engine 5 Converter(Catalytic Converter): Engine #5; Cat B010(Catalytic Converter): Catalytic Converter for B010, engine #6 | Environmental Quality Management, Inc. | 2370 | 540 ppmvd@15%O2 or 4.0 g/hp-hr and 93% removal | 98% of max | 11.0 ppmvd and 0.094 g/hp-hr and 95.3% removal | 10 | CO - Carbon Monoxide | PASS | NA | Y
2013 | 682 | 0285012009 | Aspire Energy of Ohio LLC - AEO-C06 | County Rd 40 | Penn Twp. | 43758 |  | Morgan | P001 | Portable 276 bhp (@1,800 RPM), 2.05 MMBtu/hr Caterpillar Model G3406 TA, 4-stroke rich burn (4SRB), spark ignition (SI), natural gas-fired internal combustion engine, driving a pump or compressor, manufactured April 2012 and installed in October 2012. | 2013-10-10 | Converter(Catalytic Converter): Catalytic Converter | Custom Stack Analysis, LLC. | 276 hp | 2.0 g/hp-hr 270 ppm @ 15% O2 | 179 | 0.245 g/hp-hr 44.49 ppm @ 15%O2 | 10 | CO - Carbon Monoxide | PASS | NA | Y | Averages: 160.77 ppm 0.1546 lbs/hr 44.49 ppm @ 15% O2 0.245 g/hp-hr
2013 | 1049 | 0607015001 | Tri-County Compressor Station (MarkWest / Ohio Oil Gath | North of intersection of Hwy 379 and Town | Barnesville | 43713 |  | Belmont | P004 | Compressor Engine #4 - 1980 HP (15.43 MMBtu/hr) Waukesha P9390 - natural gas-fired four-stroke rich burn internal combustion engine equipped with a three-way oxidation catalyst controlling CH2O, CO, NOx, & VOCs by 80, 97, 98.5 & 66 percent respectively | 2013-11-15 | CC002(Catalytic Converter): Compressor Engine #2 - 3-way Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - 3-way Catalyst; CC004(Catalytic Converter): Compressor Engine #4 - 3-way Catalyst; CC005(Catalytic Converter): Compressor Engine #5 - 3-w | Air Hygiene International | 1980 Hp | 270 ppm | 1881 | 0.77 ppm | 10 | CO - Carbon Monoxide | PASS | NA | Y | testing November 15th and 16th, 2013
2013 | 1052 | 0607015001 | Tri-County Compressor Station (MarkWest / Ohio Oil Gath | North of intersection of Hwy 379 and Town | Barnesville | 43713 |  | Belmont | P005 | Compressor Engine #5 - 1980 HP (15.43 MMBtu/hr) Waukesha P9390 - natural gas-fired four-stroke rich burn internal combustion engine equipped with a three-way oxidation catalyst controlling CH2O, CO, NOx, & VOCs by 80, 97, 98.5 & 66 percent respectively | 2013-11-15 | CC002(Catalytic Converter): Compressor Engine #2 - 3-way Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - 3-way Catalyst; CC004(Catalytic Converter): Compressor Engine #4 - 3-way Catalyst; CC005(Catalytic Converter): Compressor Engine #5 - 3-w | Air Hygiene International | 1980 Hp | 270 ppm | 1881 | 0.89 ppm | 10 | CO - Carbon Monoxide | PASS | NA | Y | testing November 15th and 16th, 2013
2013 | 1074 | 0679000330 | East Ohio Gas Jefferson Compressor Sta. | 4378 Williams Lake Rd SW | New Philadelphia | 44663 |  | Tuscarawas | P001 | 1340 HP 4 stroke lean burn natural gas fired reciprocating engine with catalytic oxidation | 2013-09-25 | S001(Catalytic Converter): Catalytic Converter for P001 | Environmental Quality Management, Inc. | 1340 HP | 4.0 g/HP-hr; 540 ppmvd @ 15% O2 | 1134 HP | 0.036 g/HP-hr; 11.2 ppmvd @ 15% O2 | 10 | CO - Carbon Monoxide | PASS | NA | Y | PTIO P0110413 and NSPS JJJJ testing requirements
2013 | 1153 | 0607015001 | Tri-County Compressor Station (MarkWest / Ohio Oil Gath | North of intersection of Hwy 379 and Town | Barnesville | 43713 |  | Belmont | P003 | Compressor Engine #3 - 1980 HP (15.43 MMBtu/hr) Waukesha P9390 - natural gas-fired four-stroke rich burn internal combustion engine equipped with a three-way oxidation catalyst controlling CH2O, CO, NOx, & VOCs by 80, 97, 98.5 & 66 percent respectively | 2013-11-15 | CC002(Catalytic Converter): Compressor Engine #2 - 3-way Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - 3-way Catalyst; CC004(Catalytic Converter): Compressor Engine #4 - 3-way Catalyst; CC005(Catalytic Converter): Compressor Engine #5 - 3-w | Air Hygiene International | 1980 Hp | 270 ppm | 1861 | 12.47 ppm | 10 | CO - Carbon Monoxide | PASS | NA | Y | testing November 15th and 16th, 2013
2013 | 1156 | 0607015001 | Tri-County Compressor Station (MarkWest / Ohio Oil Gath | North of intersection of Hwy 379 and Town | Barnesville | 43713 |  | Belmont | P006 | Compressor Engine #6 - 1980 HP (15.43 MMBtu/hr) Waukesha P9390 - natural gas-fired four-stroke rich burn internal combustion engine equipped with a three-way oxidation catalyst controlling CH2O, CO, NOx, & VOCs by 80, 97, 98.5 & 66 percent respectively | 2013-11-15 | CC002(Catalytic Converter): Compressor Engine #2 - 3-way Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - 3-way Catalyst; CC004(Catalytic Converter): Compressor Engine #4 - 3-way Catalyst; CC005(Catalytic Converter): Compressor Engine #5 - 3-w | Air Hygiene International | 1980 Hp | 270 ppm | 1881 | 7.9 ppm | 10 | CO - Carbon Monoxide | PASS | NA | Y | testing November 15th and 16th, 2013
2013 | 1175 | 0634005029 | Cadiz Gas Plant | 43071 Industrial Park Rd | Cadiz | 43907 |  | Harrison | P007 | Compressor Engine #7 - 4735 HP Caterpillar G3616 engine (CM-1206-7) - natural gas-fired four-stroke lean burn internal combustion engine equipped with an oxidation catalyst controlling CO, VOC and formaldehyde 95, 75, and 90 percent respectively. | 2013-11-14 | CC007(Catalytic Converter): oxidation catalyst | Air Hygiene International | 4,735 hp | 270.0 ppm | 4,715 hp | 7.8 ppm | 10 | CO - Carbon Monoxide | PASS | NA | Y
2013 | 1178 | 0634005029 | Cadiz Gas Plant | 43071 Industrial Park Rd | Cadiz | 43907 |  | Harrison | P008 | Compressor Engine #8 - 4735 HP Caterpillar G3616 engine (CM-1206-8) - natural gas-fired four-stroke lean burn internal combustion engine equipped with an oxidation catalyst controlling CO, VOC and formaldehyde 95, 75, and 90 percent respectively. | 2013-11-14 | CC008(Catalytic Converter): oxidation catalyst | Air Hygiene International | 4,735 hp | 270.0 ppm | 4,725 ppm | 8.4 ppm | 10 | CO - Carbon Monoxide | PASS | NA | Y
2013 | 1183 | 0634005035 | Chesapeake Exploration LLC- Henderson South 10-12-6 Pad | Township Highway 225 | Scio | 43988 |  | Harrison | P002 | Flash Gas Compressor equipped with catalyst, 145 hp, Cat G3306 NA (Spark Ignition Internal Combustion Engine, P002) Flash Gas Compressor equipped with catalyst, 211 hp, CAT G3306 TA (Spark Ignition Internal Combustion Engine, P002) | 2013-08-23 | none | Alliance Source Testing | 211 Hp | 270 ppm | 185 Hp | 36.6 ppm | 10 | CO - Carbon Monoxide | PASS | NA | Y
2013 | 1191 | 0634005040 | Archer Compressor Facility | County Highway 45 | Cadiz | 43907 |  | Harrison | P002 | Compressor Engine #2 - 1775 HP Caterpillar G3606 (4S-LB) - natural gas-fired four-cycle lean burn internal combustion engine rated equipped with an oxidation catalyst controlling CO and VOC emissions. | 2013-12-12 | OxidCat-102(Catalytic Converter): Oxidative Catalyst; OxidCat-102(Catalytic Converter): Oxidative Catalyst | Alliance Source Testing, LLC | 1775 HP | 1.78 lbs/hr | 1621 | 0.2 g/HP-hr | 10 | CO - Carbon Monoxide | PASS | NA | Y
2013 | 1194 | 0634005040 | Archer Compressor Facility | County Highway 45 | Cadiz | 43907 |  | Harrison | P003 | Compressor Engine #3 - 1775 HP Caterpillar G3606 (4S-LB) - natural gas-fired four-cycle lean burn internal combustion engine rated equipped with an oxidation catalyst controlling CO and VOC emissions. | 2013-12-12 | OxidCat-102(Catalytic Converter): Oxidative Catalyst; OxidCat-102(Catalytic Converter): Oxidative Catalyst | Alliance Source Testing, LLC | 1775 HP | 1.78 lbs/hr | 1598 | 0.02 | 10 | CO - Carbon Monoxide | PASS | NA | Y
2013 | 1196 | 0634005040 | Archer Compressor Facility | County Highway 45 | Cadiz | 43907 |  | Harrison | P004 | Compressor Engine #4 - 1775 HP Caterpillar G3606 (4S-LB) - natural gas-fired four-cycle lean burn internal combustion engine rated equipped with an oxidation catalyst controlling CO and VOC emissions. | 2013-12-12 | OxidCat-102(Catalytic Converter): Oxidative Catalyst; OxidCat-102(Catalytic Converter): Oxidative Catalyst | Alliance Source Testing, LLC | 1775 HP | 1.78 lbs/hr | 1609 | 0.13 | 10 | CO - Carbon Monoxide | PASS | NA | Y
2013 | 1200 | 0634005040 | Archer Compressor Facility | County Highway 45 | Cadiz | 43907 |  | Harrison | P005 | Compressor Engine #5 - 1775 HP Caterpillar G3606 (4S-LB) - natural gas-fired four-cycle lean burn internal combustion engine rated equipped with an oxidation catalyst controlling CO and VOC emissions. | 2013-12-12 | OxidCat-102(Catalytic Converter): Oxidative Catalyst; OxidCat-102(Catalytic Converter): Oxidative Catalyst | Alliance Source Testing, LLC | 1775 HP | 1.78 lbs/hr | 1615 | 0.22 | 10 | CO - Carbon Monoxide | PASS | NA | Y
2013 | 1204 | 0634005040 | Archer Compressor Facility | County Highway 45 | Cadiz | 43907 |  | Harrison | P001 | Compressor Engine #1 - 1775 HP Caterpillar G3606 (4S-LB) - natural gas-fired four-cycle lean burn internal combustion engine rated equipped with an oxidation catalyst controlling CO and VOC emissions. | 2013-12-13 | OxidCat-101(Catalytic Converter): Oxidative Catalyst | Alliance Source Testing, LLC | 1775 | 1.78 lb/hr | 1632 | 0.29 lb/hr | 10 | CO - Carbon Monoxide | PASS | NA | Y | PTIO P0113393 and NSPS JJJJ testing requirements.
2013 | 1238 | 0656035002 | Statoil - Eisenbarth Pad | 42240 Long Ridge Road | Clarington | 43931 |  | Monroe | P002 | (1) - 860 Hp, 6.5 mmBTU/hr, 4 stroke, lean burn, catalytic oxidation, Caterpillar G 3512 LE natural gas-fired internal combustion engine. | 2013-04-11 | Oxidative catalyst | Air Hygiene international, Inc. | 860 | 4.0 g/hp-hr 540 ppmvd @ 15% O2 | 860 | 0.03 g/hp-hr 3.90 ppmvd @ 15% O2 | 10 | CO - Carbon Monoxide | PASS | NA | Y
2013 | 1250 | 0661005002 | Summerfield Compressor Station | between CR-45 and HWY 233 | Caldwell | 43724 |  | Noble | P001 | Natural Gas Engine(1) 1,380 hp engine | 2013-03-12 | Catalyst 1(Catalytic Converter): Oxidation Catalyst 1 | BCMJ Controls | 1380 Hp | 2.0 g/Hp-hr | 1178 Hp | 0.02 g/Hp-hr | 10 | CO - Carbon Monoxide | PASS | NA | Y
2013 | 1253 | 0661005002 | Summerfield Compressor Station | between CR-45 and HWY 233 | Caldwell | 43724 |  | Noble | P002 | Natural Gas Engine (2) 1,380 hp | 2013-03-12 | Catalyst 1(Catalytic Converter): Oxidation Catalyst 1 | BCMJ Controls | 1380 Hp | 2.0 g/Hp-hr | 1178 Hp | 0.03 g/Hp-hr | 10 | CO - Carbon Monoxide | PASS | NA | Y
2014 | 50 | 0634005040 | Archer Compressor Facility | County Highway 45 | Cadiz | 43907 |  | Harrison | P004 | Compressor Engine #4 - 1775 HP Caterpillar G3606 (4S-LB) - natural gas-fired four-cycle lean burn internal combustion engine rated equipped with an oxidation catalyst controlling CO and VOC emissions. | 2014-11-10 | OxidCat-104(Catalytic Converter): Oxidative Catalyst | EcoTest Energy Services | 1775 Hp | 2.00 g/Hp-hr | 1642 Hp | 0.0 g/Hp-hr | 10 | CO - Carbon Monoxide | PASS | NA | Y | Method 10 not used. Methods 205, 320 and ASTM 6348-3 FTIR
2014 | 53 | 0210002039 | Kilgore Compressor Station-Utica Gas Services, LLC | Pontiff Rd | Kilgore | 43988 |  | Carroll | P010 | 1,775 hp NG-fired 4SLB Stationary ICE equipped w/catalyst Caterpillar G3606: Serial Number: 4ZS01814 | 2014-12-15 | CC001(Catalytic Converter): Compressor Engine #1 - Oxidation Catalyst; CC002(Catalytic Converter): Compressor Engine #2 - Oxidation Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - Oxidation Catalyst; CC004(Catalytic Converter): Compressor Eng | Alliance Source Testing, Inc. | 1775 HP | 2.0g/hp-hr & 1.18lbs/hr | 1616 HP | 0.003g/hp-hr & 0.01lb/hr | 10 | CO - Carbon Monoxide | PASS | NA | Y
2014 | 55 | 0210002039 | Kilgore Compressor Station-Utica Gas Services, LLC | Pontiff Rd | Kilgore | 43988 |  | Carroll | P010 | 1,775 hp NG-fired 4SLB Stationary ICE equipped w/catalyst Caterpillar G3606: Serial Number: 4ZS01814 | 2014-12-16 | CC001(Catalytic Converter): Compressor Engine #1 - Oxidation Catalyst; CC002(Catalytic Converter): Compressor Engine #2 - Oxidation Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - Oxidation Catalyst; CC004(Catalytic Converter): Compressor Eng | Alliance Source Testing, Inc. | 1775 HP | 2.0g/hp-hr & 1.18lbs/hr | 1616 HP | 0.003g/hp-hr & 0.01lb/hr | 10 | CO - Carbon Monoxide | PASS | NA | Y
2014 | 58 | 0210002039 | Kilgore Compressor Station-Utica Gas Services, LLC | Pontiff Rd | Kilgore | 43988 |  | Carroll | P010 | 1,775 hp NG-fired 4SLB Stationary ICE equipped w/catalyst Caterpillar G3606: Serial Number: 4ZS01814 | 2014-12-17 | CC001(Catalytic Converter): Compressor Engine #1 - Oxidation Catalyst; CC002(Catalytic Converter): Compressor Engine #2 - Oxidation Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - Oxidation Catalyst; CC004(Catalytic Converter): Compressor Eng | Alliance Source Testing, Inc. | 1775 HP | 2.0g/hp-hr & 1.18lbs/hr | 1616 HP | 0.003g/hp-hr & 0.01lb/hr | 10 | CO - Carbon Monoxide | PASS | NA | Y
2014 | 62 | 0210002039 | Kilgore Compressor Station-Utica Gas Services, LLC | Pontiff Rd | Kilgore | 43988 |  | Carroll | P006 | 1,775 hp NG-fired 4SLB Stationary ICE equipped w/catalyst Caterpillar G3606: Serial Number: 4ZS01805 | 2014-12-15 | CC001(Catalytic Converter): Compressor Engine #1 - Oxidation Catalyst; CC002(Catalytic Converter): Compressor Engine #2 - Oxidation Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - Oxidation Catalyst; CC004(Catalytic Converter): Compressor Eng | Alliance Source Testing, Inc. | 1775 HP | 2.0g/hp-hr & 1.18lbs/hr | 1604 HP | 0.005g/hp-hr & 0.02lb/hr | 10 | CO - Carbon Monoxide | PASS | NA | Y
2014 | 65 | 0210002039 | Kilgore Compressor Station-Utica Gas Services, LLC | Pontiff Rd | Kilgore | 43988 |  | Carroll | P006 | 1,775 hp NG-fired 4SLB Stationary ICE equipped w/catalyst Caterpillar G3606: Serial Number: 4ZS01805 | 2014-12-16 | CC001(Catalytic Converter): Compressor Engine #1 - Oxidation Catalyst; CC002(Catalytic Converter): Compressor Engine #2 - Oxidation Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - Oxidation Catalyst; CC004(Catalytic Converter): Compressor Eng | Alliance Source Testing, Inc. | 1775 HP | 2.0g/hp-hr & 1.18lbs/hr | 1604 HP | 0.005g/hp-hr & 0.02lb/hr | 10 | CO - Carbon Monoxide | PASS | NA | Y
2014 | 156 | 0210002039 | Kilgore Compressor Station-Utica Gas Services, LLC | Pontiff Rd | Kilgore | 43988 |  | Carroll | P006 | 1,775 hp NG-fired 4SLB Stationary ICE equipped w/catalyst Caterpillar G3606: Serial Number: 4ZS01805 | 2014-12-17 | CC001(Catalytic Converter): Compressor Engine #1 - Oxidation Catalyst; CC002(Catalytic Converter): Compressor Engine #2 - Oxidation Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - Oxidation Catalyst; CC004(Catalytic Converter): Compressor Eng | Alliance Source Testing, Inc. | 1775 HP | 2.0g/hp-hr & 1.18lbs/hr | 1604 HP | 0.005g/hp-hr & 0.02lb/hr | 10 | CO - Carbon Monoxide | PASS | NA | Y
2014 | 157 | 0634005056 | Scio Compressor Station | 37650 Bower Rd | Scio | 43988 |  | Harrison | P005 | Compressor Engine #5 - 1,775 HP Caterpillar G3606 (4S-LB) - natural gas-fired four-cycle lean burn internal combustion engine equipped with an oxidation catalyst controlling CO & VOC emissions | 2014-06-23 | CC005(Catalytic Converter): Compressor Engine #5 - Oxidation Catalyst | Alliance Source Testing | 1,775 Hp | 0.30 g/Hp-hr 270 ppm | 1,627 Hp | 0.01 g/Hp-hr 0.8 ppm | 10 | CO - Carbon Monoxide | PASS | NA | Y
2014 | 161 | 0210002039 | Kilgore Compressor Station-Utica Gas Services, LLC | Pontiff Rd | Kilgore | 43988 |  | Carroll | P003 | 1,775 hp NG-fired 4SLB Stationary ICE equipped w/catalyst Caterpillar G3606: Serial Number: 4ZS01797 | 2014-12-15 | CC001(Catalytic Converter): Compressor Engine #1 - Oxidation Catalyst; CC002(Catalytic Converter): Compressor Engine #2 - Oxidation Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - Oxidation Catalyst; CC004(Catalytic Converter): Compressor Eng | Alliance Source Testing, Inc. | 1775 HP | 2.0g/hp-hr & 1.18lbs/hr | 1598 HP | 0.01g/hp-hr & 0.02lb/hr | 10 | CO - Carbon Monoxide | PASS | NA | Y
2014 | 183 | 0210002039 | Kilgore Compressor Station-Utica Gas Services, LLC | Pontiff Rd | Kilgore | 43988 |  | Carroll | P009 | 1,775 hp NG-fired 4SLB Stationary ICE equipped w/catalyst Caterpillar G3606: Serial Number: 4ZS01776 | 2014-12-17 | CC001(Catalytic Converter): Compressor Engine #1 - Oxidation Catalyst; CC002(Catalytic Converter): Compressor Engine #2 - Oxidation Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - Oxidation Catalyst; CC004(Catalytic Converter): Compressor Eng | Alliance Source Testing, Inc. | 1775 HP | 2.0g/hp-hr & 1.18lbs/hr | 1616 HP | 0.01g/hp-hr & 0.03lb/hr | 10 | CO - Carbon Monoxide | PASS | NA | Y
2014 | 185 | 0210002039 | Kilgore Compressor Station-Utica Gas Services, LLC | Pontiff Rd | Kilgore | 43988 |  | Carroll | P004 | 1,775 hp NG-fired 4SLB Stationary ICE equipped w/catalyst Caterpillar G3606: Serial Number: 4ZS01800 | 2014-12-15 | CC001(Catalytic Converter): Compressor Engine #1 - Oxidation Catalyst; CC002(Catalytic Converter): Compressor Engine #2 - Oxidation Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - Oxidation Catalyst; CC004(Catalytic Converter): Compressor Eng | Alliance Source Testing, Inc. | 1775 HP | 2.0g/hp-hr & 1.18lbs/hr | 1651 HP | 0.01g/hp-hr & 0.04lb/hr | 10 | CO - Carbon Monoxide | PASS | NA | Y
2014 | 190 | 0210012004 | Augusta Compressor Facility- Utica Gas Services, L.L.C. | 8034 Bane Rd NE | East Twp. | 44427 |  | Carroll | P010 | 1,775-hp Caterpillar G3606 Compressor Engine w/ Oxidation Catalyst | 2014-09-17 | Oxid. Cat. 3(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 4(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 5(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 6(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 7(Catalytic Converter): | Great Plains Analytical | 1775 Hp | 1.18 lbs/hr, 2.0 g/hp/hr, 270ppmvd@15%O2 | 1819 | 0.28 lbs/hr, 0.07g/hp/hr, 10.94 ppmvd@15%O2 | 10 | CO - Carbon Monoxide | PASS | NA | Y
2014 | 191 | 0210012004 | Augusta Compressor Facility- Utica Gas Services, L.L.C. | 8034 Bane Rd NE | East Twp. | 44427 |  | Carroll | P010 | 1,775-hp Caterpillar G3606 Compressor Engine w/ Oxidation Catalyst | 2014-09-18 | Oxid. Cat. 3(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 4(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 5(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 6(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 7(Catalytic Converter): | Great Plains Analytical | 1775 Hp | 1.18 lbs/hr, 2.0 g/hp/hr, 270ppmvd@15%O2 | 1819 | 0.28 lbs/hr, 0.07g/hp/hr, 10.94 ppmvd@15%O2 | 10 | CO - Carbon Monoxide | PASS | NA | Y
2014 | 194 | 0210012004 | Augusta Compressor Facility- Utica Gas Services, L.L.C. | 8034 Bane Rd NE | East Twp. | 44427 |  | Carroll | P013 | 1,775-hp Caterpillar G3606 Compressor Engine w/ Oxidation Catalyst | 2014-09-16 | Oxid. Cat. 3(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 4(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 5(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 6(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 7(Catalytic Converter): | Great Plains Analytical | 1775 Hp | 1.18 lbs/hr, 2.0 g/hp/hr, 270ppmvd@15%O2 | 1780 | 0.30 lbs/hr, 0.07 g/hp/hr, 11.62 ppmvd@15%O2 | 10 | CO - Carbon Monoxide | PASS | NA | Y
2014 | 199 | 0210012004 | Augusta Compressor Facility- Utica Gas Services, L.L.C. | 8034 Bane Rd NE | East Twp. | 44427 |  | Carroll | P013 | 1,775-hp Caterpillar G3606 Compressor Engine w/ Oxidation Catalyst | 2014-09-17 | Oxid. Cat. 3(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 4(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 5(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 6(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 7(Catalytic Converter): | Great Plains Analytical | 1775 Hp | 1.18 lbs/hr, 2.0 g/hp/hr, 270ppmvd@15%O2 | 1780 | 0.30 lbs/hr, 0.07 g/hp/hr, 11.62 ppmvd@15%O2 | 10 | CO - Carbon Monoxide | PASS | NA | Y
2014 | 202 | 0656105005 | E2 Appalachian Compression LLC - Reusser | Twp Hwy 68 and Twp Hwy 66 | Woodsfield | 43793 |  | Monroe | P005 | 1680 Hp. natural gas rich burn compressor engine - Waukesha L7044GSI | 2014-12-10 | C-3(Catalytic Converter): Engine #3 Catalyst; C-4(Catalytic Converter): Engine #4 Catalyst; C-5(Catalytic Converter): Engine #5 Catalyst; C-6(Catalytic Converter): Engine #6Catalyst; C-8(Catalytic Converter): Engine #8 Catalyst | E2 Energy Services | 1,680 hp | 0.94 lb/hr | 1,557 hp | 0.61 lb/hr | 6348 03 | CO - Carbon Monoxide | PASS | NA | Y
2014 | 205 | 0656105005 | E2 Appalachian Compression LLC - Reusser | Twp Hwy 68 and Twp Hwy 66 | Woodsfield | 43793 |  | Monroe | P005 | 1680 Hp. natural gas rich burn compressor engine - Waukesha L7044GSI | 2014-12-11 | C-3(Catalytic Converter): Engine #3 Catalyst; C-4(Catalytic Converter): Engine #4 Catalyst; C-5(Catalytic Converter): Engine #5 Catalyst; C-6(Catalytic Converter): Engine #6Catalyst; C-8(Catalytic Converter): Engine #8 Catalyst | E2 Energy Services | 1,680 hp | 0.94 lb/hr | 1,557 hp | 0.61 lb/hr | 6348 03 | CO - Carbon Monoxide | PASS | NA | Y
2014 | 224 | 0210002039 | Kilgore Compressor Station-Utica Gas Services, LLC | Pontiff Rd | Kilgore | 43988 |  | Carroll | P003 | 1,775 hp NG-fired 4SLB Stationary ICE equipped w/catalyst Caterpillar G3606: Serial Number: 4ZS01797 | 2014-12-16 | CC001(Catalytic Converter): Compressor Engine #1 - Oxidation Catalyst; CC002(Catalytic Converter): Compressor Engine #2 - Oxidation Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - Oxidation Catalyst; CC004(Catalytic Converter): Compressor Eng | Alliance Source Testing, Inc. | 1775 HP | 2.0g/hp-hr & 1.18lbs/hr | 1598 HP | 0.01g/hp-hr & 0.02lb/hr | 10 | CO - Carbon Monoxide | PASS | NA | Y
2014 | 228 | 0210002039 | Kilgore Compressor Station-Utica Gas Services, LLC | Pontiff Rd | Kilgore | 43988 |  | Carroll | P003 | 1,775 hp NG-fired 4SLB Stationary ICE equipped w/catalyst Caterpillar G3606: Serial Number: 4ZS01797 | 2014-12-17 | CC001(Catalytic Converter): Compressor Engine #1 - Oxidation Catalyst; CC002(Catalytic Converter): Compressor Engine #2 - Oxidation Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - Oxidation Catalyst; CC004(Catalytic Converter): Compressor Eng | Alliance Source Testing, Inc. | 1775 HP | 2.0g/hp-hr & 1.18lbs/hr | 1598 HP | 0.01g/hp-hr & 0.02lb/hr | 10 | CO - Carbon Monoxide | PASS | NA | Y
2014 | 236 | 0210002039 | Kilgore Compressor Station-Utica Gas Services, LLC | Pontiff Rd | Kilgore | 43988 |  | Carroll | P007 | 1,775 hp NG-fired 4SLB Stationary ICE equipped w/catalyst Caterpillar G3606: Serial Number: 4ZS01807 | 2014-12-15 | CC001(Catalytic Converter): Compressor Engine #1 - Oxidation Catalyst; CC002(Catalytic Converter): Compressor Engine #2 - Oxidation Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - Oxidation Catalyst; CC004(Catalytic Converter): Compressor Eng | Alliance Source Testing, Inc. | 1775 HP | 2.0g/hp-hr & 1.18lbs/hr | 1610 HP | 0.01g/hp-hr & 0.03b/hr | 10 | CO - Carbon Monoxide | PASS | NA | Y
2014 | 238 | 0210002039 | Kilgore Compressor Station-Utica Gas Services, LLC | Pontiff Rd | Kilgore | 43988 |  | Carroll | P007 | 1,775 hp NG-fired 4SLB Stationary ICE equipped w/catalyst Caterpillar G3606: Serial Number: 4ZS01807 | 2014-12-16 | CC001(Catalytic Converter): Compressor Engine #1 - Oxidation Catalyst; CC002(Catalytic Converter): Compressor Engine #2 - Oxidation Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - Oxidation Catalyst; CC004(Catalytic Converter): Compressor Eng | Alliance Source Testing, Inc. | 1775 HP | 2.0g/hp-hr & 1.18lbs/hr | 1610 HP | 0.01g/hp-hr & 0.03b/hr | 10 | CO - Carbon Monoxide | PASS | NA | Y
2014 | 241 | 0210002039 | Kilgore Compressor Station-Utica Gas Services, LLC | Pontiff Rd | Kilgore | 43988 |  | Carroll | P007 | 1,775 hp NG-fired 4SLB Stationary ICE equipped w/catalyst Caterpillar G3606: Serial Number: 4ZS01807 | 2014-12-17 | CC001(Catalytic Converter): Compressor Engine #1 - Oxidation Catalyst; CC002(Catalytic Converter): Compressor Engine #2 - Oxidation Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - Oxidation Catalyst; CC004(Catalytic Converter): Compressor Eng | Alliance Source Testing, Inc. | 1775 HP | 2.0g/hp-hr & 1.18lbs/hr | 1610 HP | 0.01g/hp-hr & 0.03b/hr | 10 | CO - Carbon Monoxide | PASS | NA | Y
2014 | 245 | 0210002039 | Kilgore Compressor Station-Utica Gas Services, LLC | Pontiff Rd | Kilgore | 43988 |  | Carroll | P005 | 1,775 hp NG-fired 4SLB Stationary ICE equipped w/catalyst Caterpillar G3606: Serial Number: 4ZS01804 | 2014-12-15 | CC001(Catalytic Converter): Compressor Engine #1 - Oxidation Catalyst; CC002(Catalytic Converter): Compressor Engine #2 - Oxidation Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - Oxidation Catalyst; CC004(Catalytic Converter): Compressor Eng | Alliance Source Testing, Inc. | 1775 HP | 2.0g/hp-hr & 1.18lbs/hr | 1604 HP | 0.01g/hp-hr & 0.03lb/hr | 10 | CO - Carbon Monoxide | PASS | NA | Y
2014 | 248 | 0210002039 | Kilgore Compressor Station-Utica Gas Services, LLC | Pontiff Rd | Kilgore | 43988 |  | Carroll | P009 | 1,775 hp NG-fired 4SLB Stationary ICE equipped w/catalyst Caterpillar G3606: Serial Number: 4ZS01776 | 2014-12-15 | CC001(Catalytic Converter): Compressor Engine #1 - Oxidation Catalyst; CC002(Catalytic Converter): Compressor Engine #2 - Oxidation Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - Oxidation Catalyst; CC004(Catalytic Converter): Compressor Eng | Alliance Source Testing, Inc. | 1775 HP | 2.0g/hp-hr & 1.18lbs/hr | 1616 HP | 0.01g/hp-hr & 0.03lb/hr | 10 | CO - Carbon Monoxide | PASS | NA | Y
2014 | 250 | 0210002039 | Kilgore Compressor Station-Utica Gas Services, LLC | Pontiff Rd | Kilgore | 43988 |  | Carroll | P005 | 1,775 hp NG-fired 4SLB Stationary ICE equipped w/catalyst Caterpillar G3606: Serial Number: 4ZS01804 | 2014-12-16 | CC001(Catalytic Converter): Compressor Engine #1 - Oxidation Catalyst; CC002(Catalytic Converter): Compressor Engine #2 - Oxidation Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - Oxidation Catalyst; CC004(Catalytic Converter): Compressor Eng | Alliance Source Testing, Inc. | 1775 HP | 2.0g/hp-hr & 1.18lbs/hr | 1604 HP | 0.01g/hp-hr & 0.03lb/hr | 10 | CO - Carbon Monoxide | PASS | NA | Y
2014 | 254 | 0210002039 | Kilgore Compressor Station-Utica Gas Services, LLC | Pontiff Rd | Kilgore | 43988 |  | Carroll | P009 | 1,775 hp NG-fired 4SLB Stationary ICE equipped w/catalyst Caterpillar G3606: Serial Number: 4ZS01776 | 2014-12-16 | CC001(Catalytic Converter): Compressor Engine #1 - Oxidation Catalyst; CC002(Catalytic Converter): Compressor Engine #2 - Oxidation Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - Oxidation Catalyst; CC004(Catalytic Converter): Compressor Eng | Alliance Source Testing, Inc. | 1775 HP | 2.0g/hp-hr & 1.18lbs/hr | 1616 HP | 0.01g/hp-hr & 0.03lb/hr | 10 | CO - Carbon Monoxide | PASS | NA | Y
2014 | 257 | 0210002039 | Kilgore Compressor Station-Utica Gas Services, LLC | Pontiff Rd | Kilgore | 43988 |  | Carroll | P005 | 1,775 hp NG-fired 4SLB Stationary ICE equipped w/catalyst Caterpillar G3606: Serial Number: 4ZS01804 | 2014-12-17 | CC001(Catalytic Converter): Compressor Engine #1 - Oxidation Catalyst; CC002(Catalytic Converter): Compressor Engine #2 - Oxidation Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - Oxidation Catalyst; CC004(Catalytic Converter): Compressor Eng | Alliance Source Testing, Inc. | 1775 HP | 2.0g/hp-hr & 1.18lbs/hr | 1604 HP | 0.01g/hp-hr & 0.03lb/hr | 10 | CO - Carbon Monoxide | PASS | NA | Y
2014 | 269 | 0210002039 | Kilgore Compressor Station-Utica Gas Services, LLC | Pontiff Rd | Kilgore | 43988 |  | Carroll | P004 | 1,775 hp NG-fired 4SLB Stationary ICE equipped w/catalyst Caterpillar G3606: Serial Number: 4ZS01800 | 2014-12-16 | CC001(Catalytic Converter): Compressor Engine #1 - Oxidation Catalyst; CC002(Catalytic Converter): Compressor Engine #2 - Oxidation Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - Oxidation Catalyst; CC004(Catalytic Converter): Compressor Eng | Alliance Source Testing, Inc. | 1775 HP | 2.0g/hp-hr & 1.18lbs/hr | 1651 HP | 0.01g/hp-hr & 0.04lb/hr | 10 | CO - Carbon Monoxide | PASS | NA | Y
2014 | 271 | 0210002039 | Kilgore Compressor Station-Utica Gas Services, LLC | Pontiff Rd | Kilgore | 43988 |  | Carroll | P004 | 1,775 hp NG-fired 4SLB Stationary ICE equipped w/catalyst Caterpillar G3606: Serial Number: 4ZS01800 | 2014-12-17 | CC001(Catalytic Converter): Compressor Engine #1 - Oxidation Catalyst; CC002(Catalytic Converter): Compressor Engine #2 - Oxidation Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - Oxidation Catalyst; CC004(Catalytic Converter): Compressor Eng | Alliance Source Testing, Inc. | 1775 HP | 2.0g/hp-hr & 1.18lbs/hr | 1651 HP | 0.01g/hp-hr & 0.04lb/hr | 10 | CO - Carbon Monoxide | PASS | NA | Y
2014 | 276 | 0607005015 | Morristown Compressor Station | Between Hwys 100 and 203 | Union Twp. | 43713 |  | Belmont | P003 | compressor engine | 2014-11-20 | CC001(Catalytic Converter): Compressor Engine #1 Catalytic Converter; CC002(Catalytic Converter): Compressor Engine #2 Catalytic Converter; CC003(Catalytic Converter): Compressor Engine #3 Catalytic Converter; CC004(Catalytic Converter): Compressor Engine | Air Hygiene, Inc. | 2,370 hp | 2.0 g/hp-hr | 2,236 hp | 0.02 g/hp-hr | 10 | CO - Carbon Monoxide | PASS | NA | Y
2014 | 279 | 0607005015 | Morristown Compressor Station | Between Hwys 100 and 203 | Union Twp. | 43713 |  | Belmont | P004 | compressor engine | 2014-11-20 | CC001(Catalytic Converter): Compressor Engine #1 Catalytic Converter; CC002(Catalytic Converter): Compressor Engine #2 Catalytic Converter; CC003(Catalytic Converter): Compressor Engine #3 Catalytic Converter; CC004(Catalytic Converter): Compressor Engine | Air Hygiene, Inc. | 2,370 hp | 2.0 g/hp-hr | 2,283 hp | 0.02 g/hp-hr | 10 | CO - Carbon Monoxide | PASS | NA | Y
2014 | 280 | 0607005015 | Morristown Compressor Station | Between Hwys 100 and 203 | Union Twp. | 43713 |  | Belmont | P003 | compressor engine | 2014-11-21 | CC001(Catalytic Converter): Compressor Engine #1 Catalytic Converter; CC002(Catalytic Converter): Compressor Engine #2 Catalytic Converter; CC003(Catalytic Converter): Compressor Engine #3 Catalytic Converter; CC004(Catalytic Converter): Compressor Engine | Air Hygiene, Inc. | 2,370 hp | 2.0 g/hp-hr | 2,236 hp | 0.02 g/hp-hr | 10 | CO - Carbon Monoxide | PASS | NA | Y
2014 | 284 | 0607005015 | Morristown Compressor Station | Between Hwys 100 and 203 | Union Twp. | 43713 |  | Belmont | P004 | compressor engine | 2014-11-21 | CC001(Catalytic Converter): Compressor Engine #1 Catalytic Converter; CC002(Catalytic Converter): Compressor Engine #2 Catalytic Converter; CC003(Catalytic Converter): Compressor Engine #3 Catalytic Converter; CC004(Catalytic Converter): Compressor Engine | Air Hygiene, Inc. | 2,370 hp | 2.0 g/hp-hr | 2,283 hp | 0.02 g/hp-hr | 10 | CO - Carbon Monoxide | PASS | NA | Y
2014 | 287 | 0634005027 | Arrowhead Compressor Station | E of Clements Rd and S of Jockey Hollow | Athens Twp. | 43977 |  | Harrison | P011 | Compressor Engine #8 - Caterpillar G3608 - natural gas fired four-stroke, lean burn internal combustion engine rated at an operating capacity of 2,370 horsepower equipped with a catalytic convertor | 2014-11-20 | CC006(Catalytic Converter): Compressor Engine #6 Catalytic Convertor; CC07(Catalytic Converter): Compressor Engine #7 Catalytic Convertor; CC008(Catalytic Converter): Compressor Engine #8 Catalytic Convertor | Air Hygiene Inc. | 2370 Hp | 2.0 g/Hp-hr | 2197 Hp | 0.02 g/Hp-hr | 10 | CO - Carbon Monoxide | PASS | NA | Y
2014 | 290 | 0656005011 | Ormet Production Facility | 43879 St Rte 7 | Hannibal | 43931 |  | Monroe | P001 | CAT 3516BLE SI combustion engine 1380 bhp | 2014-10-30 | none | EcoTest Energy Services | 1,380 Hp | 2.98 g/Hp-hr | 1,250 Hp | 0.02 g/Hp-hr | 10 | CO - Carbon Monoxide | PASS | NA | Y | Method 10 not used. Method 320 used
2014 | 292 | 0656005011 | Ormet Production Facility | 43879 St Rte 7 | Hannibal | 43931 |  | Monroe | P001 | CAT 3516BLE SI combustion engine 1380 bhp | 2014-10-30 | none in facility profile | EcoTest Energy Services | 1,380 Hp | 2.98 g/Hp-hr | 1,250 Hp | 0.02 g/Hp-hr | 6348 03 | CO - Carbon Monoxide | PASS | NA | Y | Method 320 used-not ASTM 6348-03
2014 | 296 | 0656005010 | Dominion East Ohio - Switzerland Compressor Station | German Ridge Road | Switzerland Twp. | 43942 |  | Monroe | P001 | 3550 Hp Natural gas-fired (4SLB) Caterpillar model 3612 LE DM5309-06 compressor engines equipped with catalytic reduction (three-way). | 2014-11-11 | catalytic reduction | Air Compliance Consultants | 3550 Hp | 0.22 g/Hp-hr | 3408 | 0.024 g/Hp-hr | 10 | CO - Carbon Monoxide | PASS | NA | Y
2014 | 309 | 0656005010 | Dominion East Ohio - Switzerland Compressor Station | German Ridge Road | Switzerland Twp. | 43942 |  | Monroe | P003 | 3550 Hp Natural gas-fired (4SLB) Caterpillar model 3612 LE DM5309-06 compressor engines equipped with catalytic reduction (three-way). | 2014-11-11 | catalytic reduction | Air Compliance Consultants | 3550 Hp | 0.22 g/Hp-hr | 3242 Hp | 0.024 g/Hp-hr | 10 | CO - Carbon Monoxide | PASS | NA | Y
2014 | 312 | 0656005010 | Dominion East Ohio - Switzerland Compressor Station | German Ridge Road | Switzerland Twp. | 43942 |  | Monroe | P001 | 3550 Hp Natural gas-fired (4SLB) Caterpillar model 3612 LE DM5309-06 compressor engines equipped with catalytic reduction (three-way). | 2014-11-12 | catalytic reduction | Air Compliance Consultants | 3550 Hp | 0.22 g/Hp-hr | 3408 | 0.024 g/Hp-hr | 10 | CO - Carbon Monoxide | PASS | NA | Y
2014 | 313 | 0656005010 | Dominion East Ohio - Switzerland Compressor Station | German Ridge Road | Switzerland Twp. | 43942 |  | Monroe | P003 | 3550 Hp Natural gas-fired (4SLB) Caterpillar model 3612 LE DM5309-06 compressor engines equipped with catalytic reduction (three-way). | 2014-11-12 | catalytic reduction | Air Compliance Consultants | 3550 Hp | 0.22 g/Hp-hr | 3242 Hp | 0.024 g/Hp-hr | 10 | CO - Carbon Monoxide | PASS | NA | Y
2014 | 316 | 0210002039 | Kilgore Compressor Station-Utica Gas Services, LLC | Pontiff Rd | Kilgore | 43988 |  | Carroll | P008 | 1,775 hp NG-fired 4SLB Stationary ICE equipped w/catalyst Caterpillar G3606: Serial Number: 4ZS01808 | 2014-12-15 | CC001(Catalytic Converter): Compressor Engine #1 - Oxidation Catalyst; CC002(Catalytic Converter): Compressor Engine #2 - Oxidation Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - Oxidation Catalyst; CC004(Catalytic Converter): Compressor Eng | Alliance Source Testing, Inc. | 1775 HP | 2.0g/hp-hr & 1.18lbs/hr | 1687 HP | 0.02g/hp-hr & 0.07lb/hr | 10 | CO - Carbon Monoxide | PASS | NA | Y
2014 | 321 | 0210002039 | Kilgore Compressor Station-Utica Gas Services, LLC | Pontiff Rd | Kilgore | 43988 |  | Carroll | P008 | 1,775 hp NG-fired 4SLB Stationary ICE equipped w/catalyst Caterpillar G3606: Serial Number: 4ZS01808 | 2014-12-16 | CC001(Catalytic Converter): Compressor Engine #1 - Oxidation Catalyst; CC002(Catalytic Converter): Compressor Engine #2 - Oxidation Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - Oxidation Catalyst; CC004(Catalytic Converter): Compressor Eng | Alliance Source Testing, Inc. | 1775 HP | 2.0g/hp-hr & 1.18lbs/hr | 1687 HP | 0.02g/hp-hr & 0.07lb/hr | 10 | CO - Carbon Monoxide | PASS | NA | Y
2014 | 323 | 0210002039 | Kilgore Compressor Station-Utica Gas Services, LLC | Pontiff Rd | Kilgore | 43988 |  | Carroll | P008 | 1,775 hp NG-fired 4SLB Stationary ICE equipped w/catalyst Caterpillar G3606: Serial Number: 4ZS01808 | 2014-12-17 | CC001(Catalytic Converter): Compressor Engine #1 - Oxidation Catalyst; CC002(Catalytic Converter): Compressor Engine #2 - Oxidation Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - Oxidation Catalyst; CC004(Catalytic Converter): Compressor Eng | Alliance Source Testing, Inc. | 1775 HP | 2.0g/hp-hr & 1.18lbs/hr | 1687 HP | 0.02g/hp-hr & 0.07lb/hr | 10 | CO - Carbon Monoxide | PASS | NA | Y
2014 | 325 | 0607005015 | Morristown Compressor Station | Between Hwys 100 and 203 | Union Twp. | 43713 |  | Belmont | P001 | compressor engine | 2014-11-20 | CC001(Catalytic Converter): Compressor Engine #1 Catalytic Converter; CC002(Catalytic Converter): Compressor Engine #2 Catalytic Converter; CC003(Catalytic Converter): Compressor Engine #3 Catalytic Converter; CC004(Catalytic Converter): Compressor Engine | Air Hygiene, Inc. | 2,370 hp | 2.0 g/hp--hr | 2,236 hp | 0.03 g/hp-hr | 10 | CO - Carbon Monoxide | PASS | NA | Y
2014 | 329 | 0607005015 | Morristown Compressor Station | Between Hwys 100 and 203 | Union Twp. | 43713 |  | Belmont | P002 | compressor engine | 2014-11-20 | CC001(Catalytic Converter): Compressor Engine #1 Catalytic Converter; CC002(Catalytic Converter): Compressor Engine #2 Catalytic Converter; CC003(Catalytic Converter): Compressor Engine #3 Catalytic Converter; CC004(Catalytic Converter): Compressor Engine | Air Hygiene, Inc. | 2,370 hp | 2.0 g/hp-hr | 2,299 hp | 0.03 g/hp-hr | 10 | CO - Carbon Monoxide | PASS | NA | Y
2014 | 332 | 0607005015 | Morristown Compressor Station | Between Hwys 100 and 203 | Union Twp. | 43713 |  | Belmont | P005 | compressor engine | 2014-11-20 | CC001(Catalytic Converter): Compressor Engine #1 Catalytic Converter; CC002(Catalytic Converter): Compressor Engine #2 Catalytic Converter; CC003(Catalytic Converter): Compressor Engine #3 Catalytic Converter; CC004(Catalytic Converter): Compressor Engine | Air Hygiene, Inc. | 2,370 hp | 2.0 g/hp-hr | 2,212 hp | 0.03 g/hp-hr | 10 | CO - Carbon Monoxide | PASS | NA | Y
2014 | 336 | 0607005015 | Morristown Compressor Station | Between Hwys 100 and 203 | Union Twp. | 43713 |  | Belmont | P006 | compressor engine | 2014-11-20 | CC001(Catalytic Converter): Compressor Engine #1 Catalytic Converter; CC002(Catalytic Converter): Compressor Engine #2 Catalytic Converter; CC003(Catalytic Converter): Compressor Engine #3 Catalytic Converter; CC004(Catalytic Converter): Compressor Engine | Air Hygiene, Inc. | 2,370 hp | 2.0 g/hp-hr | 2,140 hp | 0.03 g/hp-hr | 10 | CO - Carbon Monoxide | PASS | NA | Y
2014 | 347 | 0607005015 | Morristown Compressor Station | Between Hwys 100 and 203 | Union Twp. | 43713 |  | Belmont | P001 | compressor engine | 2014-11-21 | CC001(Catalytic Converter): Compressor Engine #1 Catalytic Converter; CC002(Catalytic Converter): Compressor Engine #2 Catalytic Converter; CC003(Catalytic Converter): Compressor Engine #3 Catalytic Converter; CC004(Catalytic Converter): Compressor Engine | Air Hygiene, Inc. | 2,370 hp | 2.0 g/hp--hr | 2,236 hp | 0.03 g/hp-hr | 10 | CO - Carbon Monoxide | PASS | NA | Y
2014 | 349 | 0607005015 | Morristown Compressor Station | Between Hwys 100 and 203 | Union Twp. | 43713 |  | Belmont | P002 | compressor engine | 2014-11-21 | CC001(Catalytic Converter): Compressor Engine #1 Catalytic Converter; CC002(Catalytic Converter): Compressor Engine #2 Catalytic Converter; CC003(Catalytic Converter): Compressor Engine #3 Catalytic Converter; CC004(Catalytic Converter): Compressor Engine | Air Hygiene, Inc. | 2,370 hp | 2.0 g/hp-hr | 2,299 hp | 0.03 g/hp-hr | 10 | CO - Carbon Monoxide | PASS | NA | Y
2014 | 352 | 0607005015 | Morristown Compressor Station | Between Hwys 100 and 203 | Union Twp. | 43713 |  | Belmont | P005 | compressor engine | 2014-11-21 | CC001(Catalytic Converter): Compressor Engine #1 Catalytic Converter; CC002(Catalytic Converter): Compressor Engine #2 Catalytic Converter; CC003(Catalytic Converter): Compressor Engine #3 Catalytic Converter; CC004(Catalytic Converter): Compressor Engine | Air Hygiene, Inc. | 2,370 hp | 2.0 g/hp-hr | 2,212 hp | 0.03 g/hp-hr | 10 | CO - Carbon Monoxide | PASS | NA | Y
2014 | 355 | 0607005015 | Morristown Compressor Station | Between Hwys 100 and 203 | Union Twp. | 43713 |  | Belmont | P006 | compressor engine | 2014-11-21 | CC001(Catalytic Converter): Compressor Engine #1 Catalytic Converter; CC002(Catalytic Converter): Compressor Engine #2 Catalytic Converter; CC003(Catalytic Converter): Compressor Engine #3 Catalytic Converter; CC004(Catalytic Converter): Compressor Engine | Air Hygiene, Inc. | 2,370 hp | 2.0 g/hp-hr | 2,140 hp | 0.03 g/hp-hr | 10 | CO - Carbon Monoxide | PASS | NA | Y
2014 | 360 | 0634005027 | Arrowhead Compressor Station | E of Clements Rd and S of Jockey Hollow | Athens Twp. | 43977 |  | Harrison | P010 | Compressor Engine #7 - Caterpillar G3608 - natural gas fired four-stroke, lean burn internal combustion engine rated at an operating capacity of 2,370 horsepower equipped with a catalytic convertor | 2014-11-20 | CC006(Catalytic Converter): Compressor Engine #6 Catalytic Convertor; CC07(Catalytic Converter): Compressor Engine #7 Catalytic Convertor; CC008(Catalytic Converter): Compressor Engine #8 Catalytic Convertor | Air Hygiene Inc. | 2370 Hp | 2.0 g/Hp-hr | 2252 Hp | 0.03 g/Hp-hr | 10 | CO - Carbon Monoxide | PASS | NA | Y
2014 | 361 | 0661005002 | Summerfield Compressor Station | between CR-45 and HWY 233 | Caldwell | 43724 |  | Noble | P001 | Natural Gas Engine(1) 1,380 hp engine | 2014-05-01 | Catalyst 1(Catalytic Converter): Oxidation Catalyst 1;; Flare(Flare): FL-1 | Environmental Quality Management | 1,380 hp | 2.0 g/hp-hr | 889 hp | 0.03 g/hp-hr | 10 | CO - Carbon Monoxide | PASS | NA | Y
2014 | 366 | 0634005056 | Scio Compressor Station | 37650 Bower Rd | Scio | 43988 |  | Harrison | P010 | Compressor Engine #10 - 1,775 HP Caterpillar G3606 (4S-LB) - natural gas-fired four-cycle lean burn internal combustion engine equipped with an oxidation catalyst controlling CO & VOC emissions | 2014-06-25 | CC010(Catalytic Converter): Compressor Engine #10 - Oxidation Catalyst | Alliance Source Testing | 1,775 Hp | 0.30 g/Hp-hr 270 ppm | 1,602 Hp | 0.03 g/Hp-hr 4.6 ppm | 10 | CO - Carbon Monoxide | PASS | NA | Y
2014 | 367 | 0634005056 | Scio Compressor Station | 37650 Bower Rd | Scio | 43988 |  | Harrison | P008 | Compressor Engine #8 - 1,775 HP Caterpillar G3606 (4S-LB) - natural gas-fired four-cycle lean burn internal combustion engine equipped with an oxidation catalyst controlling CO & VOC emissions | 2014-06-25 | CC008(Catalytic Converter): Compressor Engine #8 - Oxidation Catalyst | Alliance Source Testing | 1,775 Hp | 0.3 g/Hp-hr 270 ppm | 1,615 Hp | 0.03 g/Hp-hr 5.1 ppm | 10 | CO - Carbon Monoxide | PASS | NA | Y
2014 | 372 | 0210002039 | Kilgore Compressor Station-Utica Gas Services, LLC | Pontiff Rd | Kilgore | 43988 |  | Carroll | P001 | 1,775 hp NG-fired 4SLB Stationary ICE equipped w/catalyst Caterpillar G3606 Serial Number: 4ZS01713 | 2014-12-15 | CC001(Catalytic Converter): Compressor Engine #1 - Oxidation Catalyst; CC002(Catalytic Converter): Compressor Engine #2 - Oxidation Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - Oxidation Catalyst; CC004(Catalytic Converter): Compressor Eng | Alliance Source Testing, Inc. | 1775 HP | 2.0g/hp-hr & 1.18lbs/hr | 1651 HP | 0.03g/hp-hr & .11lb/hr | 10 | CO - Carbon Monoxide | PASS | NA | Y
2014 | 374 | 0210002039 | Kilgore Compressor Station-Utica Gas Services, LLC | Pontiff Rd | Kilgore | 43988 |  | Carroll | P001 | 1,775 hp NG-fired 4SLB Stationary ICE equipped w/catalyst Caterpillar G3606 Serial Number: 4ZS01713 | 2014-12-16 | CC001(Catalytic Converter): Compressor Engine #1 - Oxidation Catalyst; CC002(Catalytic Converter): Compressor Engine #2 - Oxidation Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - Oxidation Catalyst; CC004(Catalytic Converter): Compressor Eng | Alliance Source Testing, Inc. | 1775 HP | 2.0g/hp-hr & 1.18lbs/hr | 1651 HP | 0.03g/hp-hr & .11lb/hr | 10 | CO - Carbon Monoxide | PASS | NA | Y
2014 | 386 | 0210002039 | Kilgore Compressor Station-Utica Gas Services, LLC | Pontiff Rd | Kilgore | 43988 |  | Carroll | P001 | 1,775 hp NG-fired 4SLB Stationary ICE equipped w/catalyst Caterpillar G3606 Serial Number: 4ZS01713 | 2014-12-17 | CC001(Catalytic Converter): Compressor Engine #1 - Oxidation Catalyst; CC002(Catalytic Converter): Compressor Engine #2 - Oxidation Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - Oxidation Catalyst; CC004(Catalytic Converter): Compressor Eng | Alliance Source Testing, Inc. | 1775 HP | 2.0g/hp-hr & 1.18lbs/hr | 1651 HP | 0.03g/hp-hr & .11lb/hr | 10 | CO - Carbon Monoxide | PASS | NA | Y
2014 | 389 | 0634005027 | Arrowhead Compressor Station | E of Clements Rd and S of Jockey Hollow | Athens Twp. | 43977 |  | Harrison | P009 | Compressor Engine #6 - Caterpillar G3608 - natural gas fired four-stroke, lean burn internal combustion engine rated at an operating capacity of 2,370 horsepower equipped with a catalytic convertor | 2014-11-20 | CC006(Catalytic Converter): Compressor Engine #6 Catalytic Convertor; CC07(Catalytic Converter): Compressor Engine #7 Catalytic Convertor; CC008(Catalytic Converter): Compressor Engine #8 Catalytic Convertor | Air Hygiene Inc. | 2370 Hp | 2.0 g/Hp-hr | 2207 Hp | 0.04 g/Hp-hr | 10 | CO - Carbon Monoxide | PASS | NA | Y
2014 | 391 | 0634005056 | Scio Compressor Station | 37650 Bower Rd | Scio | 43988 |  | Harrison | P007 | Compressor Engine #7 - 1,775 HP Caterpillar G3606 (4S-LB) - natural gas-fired four-cycle lean burn internal combustion engine equipped with an oxidation catalyst controlling CO & VOC emissions | 2014-06-25 | CC007(Catalytic Converter): Compressor Engine #7 - Oxidation Catalyst | Alliance Source Testing | 1,775 Hp | 0.30 g/Hp-hr 270 ppm | 1,605 Hp | 0.04 g/Hp-hr 6.3 ppm | 10 | CO - Carbon Monoxide | PASS | NA | Y
2014 | 395 | 0661005008 | Seneca Gas Plant | Zep Road | Summerfield | 43788 |  | Noble | P001 | Compressor Engine #1 - Natural gas-fired four-stroke lean burn (4SLB) internal combustion engine rated at an operating capacity of 4,735 horsepower (hp) and equipped with an oxidation catalyst. | 2014-04-07 | CC001(Catalytic Converter): Compressor Engine #1 - Catalyic Convertor | Air Hygiene International | 4,735 hp | 2.0 g/hp-hr | 4,356 hp | 0.041 g/hp-hr | 10 | CO - Carbon Monoxide | PASS | NA | Y
2014 | 398 | 0634005027 | Arrowhead Compressor Station | E of Clements Rd and S of Jockey Hollow | Athens Twp. | 43977 |  | Harrison | P006 | Compressor Engine #3 - Caterpillar G3608 - natural gas fired four-stroke, lean burn internal combustion engine rated at an operating capacity of 2,370 horsepower equipped with a catalytic convertor. | 2014-05-01 | CC003(Catalytic Converter): Compressor Engine #3 Catalytic Convertor | Air Hygiene | 2,370 hp | 0.14 g/hp-hr | 2,212 hp | 0.05 g/hp-hr | 10 | CO - Carbon Monoxide | PASS | NA | Y
2014 | 401 | 0634005027 | Arrowhead Compressor Station | E of Clements Rd and S of Jockey Hollow | Athens Twp. | 43977 |  | Harrison | P006 | Compressor Engine #3 - Caterpillar G3608 - natural gas fired four-stroke, lean burn internal combustion engine rated at an operating capacity of 2,370 horsepower equipped with a catalytic convertor. | 2014-09-12 | CC003(Catalytic Converter): Compressor Engine #3 Catalytic Convertor; CC004(Catalytic Converter): Compressor Engine #4 Catalytic Convertor | Air Hygeine International | 2370 Hp | 0.14 g/Hp-hr | 2243 Hp | 0.05 g/Hp-hr | 10 | CO - Carbon Monoxide | PASS | NA | Y
2014 | 405 | 0634005027 | Arrowhead Compressor Station | E of Clements Rd and S of Jockey Hollow | Athens Twp. | 43977 |  | Harrison | P008 | Compressor Engine #5 - Caterpillar G3608 - natural gas fired four-stroke, lean burn internal combustion engine rated at an operating capacity of 2,370 horsepower equipped with a catalytic convertor | 2014-11-20 | CC005(Catalytic Converter): Compressor Engine #5 Catalytic Convertor | Air Hygiene, Inc. | 2370 Hp | 2.0 g/Hp-hr | 2209 Hp | 0.05 g/Hp-hr | 10 | CO - Carbon Monoxide | PASS | NA | Y
2014 | 406 | 0634005034 | Lake Compressor Station | County Highway 21 | Freeport | 43973 |  | Harrison | P001 | Compressor Engine #1 - 1480 HP (11.39 MMBtu/hr) Waukesha L7042 - natural gas-fired four-stroke rich burn internal combustion engine equipped with a three-way oxidation catalyst controlling CH2O, CO, NOx, & VOCs by 80, 97, 98.5 & 66 percent respectively | 2014-04-11 | CC001(Catalytic Converter): Compressor Engine #1 - 3-way Catalyst | Air Hygiene International | 1,480 hp | 2.0 g/hp-hr | 1,480 hp | 0.05 g/hp-hr | 10 | CO - Carbon Monoxide | PASS | NA | Y
2014 | 411 | 0634005040 | Archer Compressor Facility | County Highway 45 | Cadiz | 43907 |  | Harrison | P002 | Compressor Engine #2 - 1775 HP Caterpillar G3606 (4S-LB) - natural gas-fired four-cycle lean burn internal combustion engine rated equipped with an oxidation catalyst controlling CO and VOC emissions. | 2014-11-10 | OxidCat-102(Catalytic Converter): Oxidative Catalyst | EcoTest Energy Services | 1775 Hp | 2.0 g/Hp-hr | 1600 Hp | 0.05 g/Hp-hr | 10 | CO - Carbon Monoxide | PASS | NA | Y | Method 10 not used. Method 205, 320 and ASTM 6348-3 FTIR
2014 | 414 | 0634005056 | Scio Compressor Station | 37650 Bower Rd | Scio | 43988 |  | Harrison | P006 | Compressor Engine #6 - 1,775 HP Caterpillar G3606 (4S-LB) - natural gas-fired four-cycle lean burn internal combustion engine equipped with an oxidation catalyst controlling CO & VOC emissions | 2014-06-23 | CC006(Catalytic Converter): Compressor Engine #6 - Oxidation Catalyst | Alliance Source Testing | 1,775 Hp | 0.30 g/Hp-hr 270 ppm | 1,630 Hp | 0.05 g/Hp-hr 6.9 ppm | 10 | CO - Carbon Monoxide | PASS | NA | Y
2014 | 424 | 0634005056 | Scio Compressor Station | 37650 Bower Rd | Scio | 43988 |  | Harrison | P003 | Compressor Engine #3 - 1,775 HP Caterpillar G3606 (4S-LB) - natural gas-fired four-cycle lean burn internal combustion engine equipped with an oxidation catalyst controlling CO & VOC emissions | 2014-06-24 | CC003(Catalytic Converter): Compressor Engine #3 - Oxidation Catalyst | Alliance Source Testing | 1,775 Hp | 0.3 g/Hp-hr 270 ppm | 1,616 Hp | 0.05 g/Hp-hr 7.1 ppm | 10 | CO - Carbon Monoxide | PASS | NA | Y
2014 | 427 | 0634005077 | Gulfport Energy - Michael Well Pad | 75096 Tyson Rd | Flushing | 43977 |  | Harrison | P002 | One or multiple stationary natural gas-fired spark ignition (SI) internal combustion engines (ICE) wiht a combined total horsepower (HP) of no more than 1,800 HP for the site. | 2014-12-03 | none | Great Plains Analytical Services | 118 Hp | 4.0 g/Hp-hr | 53 Hp | 0.055 g/Hp-hr | 10 | CO - Carbon Monoxide | PASS | NA | Y | method 10 not used. Method 1-3A and ASTM 6348-03 used
2014 | 430 | 0607015001 | Tri-County Compressor Station (MarkWest / Ohio Oil Gath | North of intersection of Hwy 379 and Town | Barnesville | 43713 |  | Belmont | P006 | Compressor Engine #6 - 1980 HP (15.43 MMBtu/hr) Waukesha P9390 - natural gas-fired four-stroke rich burn internal combustion engine equipped with a three-way oxidation catalyst controlling CH2O, CO, NOx, & VOCs by 80, 97, 98.5 & 66 percent respectively | 2014-11-11 | CC002(Catalytic Converter): Compressor Engine #2 - 3-way Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - 3-way Catalyst; CC004(Catalytic Converter): Compressor Engine #4 - 3-way Catalyst; CC005(Catalytic Converter): Compressor Engine #5 - 3-w | Air Hygiene, Inc | 1,980 hp | 2.0 g/hp-hr | 1,794 hp | 0.06 g/hp-hr | 10 | CO - Carbon Monoxide | PASS | NA | Y
2014 | 433 | 0607015001 | Tri-County Compressor Station (MarkWest / Ohio Oil Gath | North of intersection of Hwy 379 and Town | Barnesville | 43713 |  | Belmont | P006 | Compressor Engine #6 - 1980 HP (15.43 MMBtu/hr) Waukesha P9390 - natural gas-fired four-stroke rich burn internal combustion engine equipped with a three-way oxidation catalyst controlling CH2O, CO, NOx, & VOCs by 80, 97, 98.5 & 66 percent respectively | 2014-11-12 | CC002(Catalytic Converter): Compressor Engine #2 - 3-way Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - 3-way Catalyst; CC004(Catalytic Converter): Compressor Engine #4 - 3-way Catalyst; CC005(Catalytic Converter): Compressor Engine #5 - 3-w | Air Hygiene, Inc | 1,980 hp | 2.0 g/hp-hr | 1,794 hp | 0.06 g/hp-hr | 10 | CO - Carbon Monoxide | PASS | NA | Y
2014 | 438 | 0607015001 | Tri-County Compressor Station (MarkWest / Ohio Oil Gath | North of intersection of Hwy 379 and Town | Barnesville | 43713 |  | Belmont | P006 | Compressor Engine #6 - 1980 HP (15.43 MMBtu/hr) Waukesha P9390 - natural gas-fired four-stroke rich burn internal combustion engine equipped with a three-way oxidation catalyst controlling CH2O, CO, NOx, & VOCs by 80, 97, 98.5 & 66 percent respectively | 2014-11-29 | CC002(Catalytic Converter): Compressor Engine #2 - 3-way Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - 3-way Catalyst; CC004(Catalytic Converter): Compressor Engine #4 - 3-way Catalyst; CC005(Catalytic Converter): Compressor Engine #5 - 3-w | Air Hygiene, Inc | 1,980 hp | 2.0 g/hp-hr | 1,794 hp | 0.06 g/hp-hr | 10 | CO - Carbon Monoxide | PASS | NA | Y
2014 | 439 | 0634005033 | Harrison West Compressor Station | Possum Hollow Road | Freeport | 43973 |  | Harrison | P007 | Compressor Engine #7 - 1980 HP (15.43 MMBtu/hr) Waukesha P9390 - natural gas-fired four-stroke rich burn internal combustion engine equipped with a three-way oxidation catalyst controlling CH2O, CO, NOx, & VOCs by 80, 97, 98.5 & 66 percent respectively | 2014-12-11 | CC001(Catalytic Converter): Compressor Engine #1 - 3-way Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - 3-way Catalyst; CC004(Catalytic Converter): Compressor Engine #4 - 3-way Catalyst; CC007(Catalytic Converter): Compressor Engine #7 - 3-w | Air Hygiene, Inc. | 1,980 hp | 0.25 g/hp-hr | 1,799 hp | 0.06 g/hp-hr | 10 | CO - Carbon Monoxide | PASS | NA | Y
2014 | 443 | 0634005033 | Harrison West Compressor Station | Possum Hollow Road | Freeport | 43973 |  | Harrison | P007 | Compressor Engine #7 - 1980 HP (15.43 MMBtu/hr) Waukesha P9390 - natural gas-fired four-stroke rich burn internal combustion engine equipped with a three-way oxidation catalyst controlling CH2O, CO, NOx, & VOCs by 80, 97, 98.5 & 66 percent respectively | 2014-12-12 | CC001(Catalytic Converter): Compressor Engine #1 - 3-way Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - 3-way Catalyst; CC004(Catalytic Converter): Compressor Engine #4 - 3-way Catalyst; CC007(Catalytic Converter): Compressor Engine #7 - 3-w | Air Hygiene, Inc. | 1,980 hp | 0.25 g/hp-hr | 1,799 hp | 0.06 g/hp-hr | 10 | CO - Carbon Monoxide | PASS | NA | Y
2014 | 447 | 0634005034 | Lake Compressor Station | County Highway 21 | Freeport | 43973 |  | Harrison | P004 | Compressor Engine #4 - 1980 HP (15.43 MMBtu/hr) Waukesha P9390 - natural gas-fired four-stroke rich burn internal combustion engine equipped with a three-way oxidation catalyst controlling CH2O, CO, NOx, & VOCs by 80, 97, 98.5 & 66 percent respectively | 2014-12-15 | CC002(Catalytic Converter): Compressor Engine #2 - 3-way Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - 3-way Catalyst; CC004(Catalytic Converter): Compressor Engine #4 - 3-way Catalyst; CC005(Catalytic Converter):; CC011(Catalytic Converter | Air Hygiene, Inc | 1,980 hp | 0.25 g/hp-hr | 1,677 hp | 0.06 g/hp-hr | 10 | CO - Carbon Monoxide | PASS | NA | Y
2014 | 449 | 0634005034 | Lake Compressor Station | County Highway 21 | Freeport | 43973 |  | Harrison | P004 | Compressor Engine #4 - 1980 HP (15.43 MMBtu/hr) Waukesha P9390 - natural gas-fired four-stroke rich burn internal combustion engine equipped with a three-way oxidation catalyst controlling CH2O, CO, NOx, & VOCs by 80, 97, 98.5 & 66 percent respectively | 2014-12-16 | CC002(Catalytic Converter): Compressor Engine #2 - 3-way Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - 3-way Catalyst; CC004(Catalytic Converter): Compressor Engine #4 - 3-way Catalyst; CC005(Catalytic Converter):; CC011(Catalytic Converter | Air Hygiene, Inc | 1,980 hp | 0.25 g/hp-hr | 1,677 hp | 0.06 g/hp-hr | 10 | CO - Carbon Monoxide | PASS | NA | Y
2014 | 453 | 0634005027 | Arrowhead Compressor Station | E of Clements Rd and S of Jockey Hollow | Athens Twp. | 43977 |  | Harrison | P007 | Compressor Engine #4 - Caterpillar G3608 - natural gas fired four-stroke, lean burn internal combustion engine rated at an operating capacity of 2,370 horsepower equipped with a catalytic convertor | 2014-06-18 | CC004(Catalytic Converter): Compressor Engine #4 Catalytic Convertor | Air Hygiene | 2,370 hp | 0.14 g/hp-hr | 2,165 hp | 0.061 g/ph-hr | 10 | CO - Carbon Monoxide | PASS | NA | Y
2014 | 454 | 0634005027 | Arrowhead Compressor Station | E of Clements Rd and S of Jockey Hollow | Athens Twp. | 43977 |  | Harrison | P007 | Compressor Engine #4 - Caterpillar G3608 - natural gas fired four-stroke, lean burn internal combustion engine rated at an operating capacity of 2,370 horsepower equipped with a catalytic convertor | 2014-09-12 | CC003(Catalytic Converter): Compressor Engine #3 Catalytic Convertor; CC004(Catalytic Converter): Compressor Engine #4 Catalytic Convertor | Air Hygeine International | 2370 Hp | 0.14 g/Hp-hr | 2185 Hp | 0.07 g/Hp-hr | 10 | CO - Carbon Monoxide | PASS | NA | Y
2014 | 458 | 0634005029 | Cadiz Gas Plant | 43071 Industrial Park Rd | Cadiz | 43907 |  | Harrison | P008 | Compressor Engine #8 - 4735 HP Caterpillar G3616 engine (CM-1206-8) - natural gas-fired four-stroke lean burn internal combustion engine equipped with an oxidation catalyst controlling CO, VOC and formaldehyde 95, 75, and 90 percent respectively. | 2014-12-19 | CC007(Catalytic Converter): oxidation catalyst; CC008(Catalytic Converter): oxidation catalyst | Air Hygiene | 4,735 hp | 0.14 g/hp-hr | 4,378 hp | 0.08 g/hp-hr | 10 | CO - Carbon Monoxide | PASS | NA | Y
2014 | 462 | 0634005040 | Archer Compressor Facility | County Highway 45 | Cadiz | 43907 |  | Harrison | P001 | Compressor Engine #1 - 1775 HP Caterpillar G3606 (4S-LB) - natural gas-fired four-cycle lean burn internal combustion engine rated equipped with an oxidation catalyst controlling CO and VOC emissions. | 2014-11-10 | OxidCat-101(Catalytic Converter): Oxidative Catalyst | EcoTest Energy Inc. | 1775 Hp | 2.00 g/Hp-hr | 1608 Hp | 0.08 g/Hp-hr | 10 | CO - Carbon Monoxide | PASS | NA | Y | Method 10 not used. Method 205, 320 and ASTM 6348-3 used. FTIR
2014 | 465 | 0661005008 | Seneca Gas Plant | Zep Road | Summerfield | 43788 |  | Noble | P002 | Compressor Engine #2 - Natural gas-fired four-stroke lean burn (4SLB) internal combustion engine rated at an operating capacity of 4,735 horsepower (hp) and equipped with an oxidation catalyst. | 2014-04-07 | CC002(Catalytic Converter): Compressor Engine #2 - Catalytic Convertor | Air Hygiene International | 4,735 hp | 2.0 g/hp-hr | 4,404 hp | 0.087 g/hp-hr | 10 | CO - Carbon Monoxide | PASS | NA | Y
2014 | 467 | 0634005033 | Harrison West Compressor Station | Possum Hollow Road | Freeport | 43973 |  | Harrison | P006 | Compressor Engine #6 - 1980 HP (15.43 MMBtu/hr) Waukesha P9390 - natural gas-fired four-stroke rich burn internal combustion engine equipped with a three-way oxidation catalyst controlling CH2O, CO, NOx, & VOCs by 80, 97, 98.5 & 66 percent respectively | 2014-04-08 | CC006(Catalytic Converter): Compressor Engine #6 - 3-way Catalyst | Air Hygiene International | 1,980 hp | 2.0 g/hp-hr | 1,840 hp | 0.09 g/hp-hr | 10 | CO - Carbon Monoxide | PASS | NA | Y
2014 | 469 | 0634005040 | Archer Compressor Facility | County Highway 45 | Cadiz | 43907 |  | Harrison | P003 | Compressor Engine #3 - 1775 HP Caterpillar G3606 (4S-LB) - natural gas-fired four-cycle lean burn internal combustion engine rated equipped with an oxidation catalyst controlling CO and VOC emissions. | 2014-11-10 | OxidCat-103(Catalytic Converter): Oxidative Catalyst | EcoTest Energy Services | 1775 Hp | 2.00 g/Hp-hr | 1627 Hp | 0.09 g/Hp-hr | 10 | CO - Carbon Monoxide | PASS | NA | Y | Method 10 not used. Method 205, 320 and ASTM 6348-3 used. FTIR
2014 | 473 | 0210002039 | Kilgore Compressor Station-Utica Gas Services, LLC | Pontiff Rd | Kilgore | 43988 |  | Carroll | P002 | 1,775 hp NG-fired 4SLB Stationary ICE equipped w/catalyst Caterpillar G3606: Serial Number: 4ZS01796 | 2014-12-15 | CC001(Catalytic Converter): Compressor Engine #1 - Oxidation Catalyst; CC002(Catalytic Converter): Compressor Engine #2 - Oxidation Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - Oxidation Catalyst; CC004(Catalytic Converter): Compressor Eng | Alliance Source Testing, Inc. | 1775 HP | 2.0g/hp-hr & 1.18lbs/hr | 1633 HP | 0.0g/hp-hr & 0.0lb/hr Non-Detect | 10 | CO - Carbon Monoxide | PASS | NA | Y
2014 | 475 | 0210002039 | Kilgore Compressor Station-Utica Gas Services, LLC | Pontiff Rd | Kilgore | 43988 |  | Carroll | P002 | 1,775 hp NG-fired 4SLB Stationary ICE equipped w/catalyst Caterpillar G3606: Serial Number: 4ZS01796 | 2014-12-16 | CC001(Catalytic Converter): Compressor Engine #1 - Oxidation Catalyst; CC002(Catalytic Converter): Compressor Engine #2 - Oxidation Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - Oxidation Catalyst; CC004(Catalytic Converter): Compressor Eng | Alliance Source Testing, Inc. | 1775 HP | 2.0g/hp-hr & 1.18lbs/hr | 1633 HP | 0.0g/hp-hr & 0.0lb/hr Non-Detect | 10 | CO - Carbon Monoxide | PASS | NA | Y
2014 | 478 | 0210002039 | Kilgore Compressor Station-Utica Gas Services, LLC | Pontiff Rd | Kilgore | 43988 |  | Carroll | P002 | 1,775 hp NG-fired 4SLB Stationary ICE equipped w/catalyst Caterpillar G3606: Serial Number: 4ZS01796 | 2014-12-17 | CC001(Catalytic Converter): Compressor Engine #1 - Oxidation Catalyst; CC002(Catalytic Converter): Compressor Engine #2 - Oxidation Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - Oxidation Catalyst; CC004(Catalytic Converter): Compressor Eng | Alliance Source Testing, Inc. | 1775 HP | 2.0g/hp-hr & 1.18lbs/hr | 1633 HP | 0.0g/hp-hr & 0.0lb/hr Non-Detect | 10 | CO - Carbon Monoxide | PASS | NA | Y
2014 | 481 | 0634005040 | Archer Compressor Facility | County Highway 45 | Cadiz | 43907 |  | Harrison | P005 | Compressor Engine #5 - 1775 HP Caterpillar G3606 (4S-LB) - natural gas-fired four-cycle lean burn internal combustion engine rated equipped with an oxidation catalyst controlling CO and VOC emissions. | 2014-11-11 | OxidCat-105(Catalytic Converter): Oxidative Catalyst | EcoTest Energy Services | 1775 Hp | 2.00 g/Hp-hr | 1638 Hp | 0.1 g/Hp-hr | 10 | CO - Carbon Monoxide | PASS | NA | Y | Method 10 not used. Methods 205, 320 and ASTM 6348-3 FTIR
2014 | 484 | 0634005040 | Archer Compressor Facility | County Highway 45 | Cadiz | 43907 |  | Harrison | P006 | Compressor Engine #6 - 1775 HP Caterpillar G3606 (4S-LB) - natural gas-fired four-cycle lean burn internal combustion engine rated equipped with an oxidation catalyst controlling CO and VOC emissions. | 2014-11-11 | OxidCat-106(Catalytic Converter): Oxidative Catalyst | EcoTest Services | 1775 Hp | 2.00 g/Hp-hr | 1683 Hp | 0.1 g/Hp-hr | 10 | CO - Carbon Monoxide | PASS | NA | Y | Method 10 not used. Method 205, 320 and ASTM 6348-3 FTIR
2014 | 489 | 0634005040 | Archer Compressor Facility | County Highway 45 | Cadiz | 43907 |  | Harrison | P007 | Compressor Engine #7 - 1775 HP Caterpillar G3606 (4S-LB) - natural gas-fired four-cycle lean burn internal combustion engine rated equipped with an oxidation catalyst controlling CO and VOC emissions. | 2014-11-12 | OxidCat-107(Catalytic Converter): Oxidative Catalyst | EcoTest Services | 1775 Hp | 2.00 g/Hp-hr | 1703 Hp | 0.1 g/Hp-hr | 10 | CO - Carbon Monoxide | PASS | NA | Y | Method 10 not used. Method 205, 320 and ASSTM 6348-3 FTIR
2014 | 492 | 0634005056 | Scio Compressor Station | 37650 Bower Rd | Scio | 43988 |  | Harrison | P001 | Compressor Engine #1 - 1,775 HP Caterpillar G3606 (4S-LB) - natural gas-fired four-cycle lean burn internal combustion engine equipped with an oxidation catalyst controlling CO & VOC emissions. | 2014-06-24 | CC001(Catalytic Converter): Compressor Engine #1 - Oxidation Catalyst | Alliance Source Testing | 1,775 Hp | 0.30 g/Hp-hr | 1,650 Hp | 0.1 g/Hp-hr | 10 | CO - Carbon Monoxide | PASS | NA | Y
2014 | 494 | 0634005056 | Scio Compressor Station | 37650 Bower Rd | Scio | 43988 |  | Harrison | P002 | Compressor Engine #2 - 1,775 HP Caterpillar G3606 (4S-LB) - natural gas-fired four-cycle lean burn internal combustion engine equipped with an oxidation catalyst controlling CO & VOC emissions | 2014-06-24 | CC002(Catalytic Converter): Compressor Engine #2 - Oxidation Catalyst | Alliance Source Testing | 1,775 Hp | 0.30 g/Hp-hr | 1,659 Hp | 0.1 g/Hp-hr | 10 | CO - Carbon Monoxide | PASS | NA | Y
2014 | 496 | 0634005056 | Scio Compressor Station | 37650 Bower Rd | Scio | 43988 |  | Harrison | P009 | Compressor Engine #9 - 1,775 HP Caterpillar G3606 (4S-LB) - natural gas-fired four-cycle lean burn internal combustion engine equipped with an oxidation catalyst controlling CO & VOC emissions | 2014-06-25 | CC009(Catalytic Converter): Compressor Engine #9 - Oxidation Catalyst | Alliance Source Testing | 1,775 Hp | 0.3 g/Hp-hr 270 ppm | 1,613 Hp | 0.1 g/Hp-hr 7 ppm | 10 | CO - Carbon Monoxide | PASS | Y | Y
2014 | 499 | 0634005056 | Scio Compressor Station | 37650 Bower Rd | Scio | 43988 |  | Harrison | P004 | Compressor Engine #4 - 1,775 HP Caterpillar G3606 (4S-LB) - natural gas-fired four-cycle lean burn internal combustion engine equipped with an oxidation catalyst controlling CO & VOC emissions | 2014-06-24 | CC004(Catalytic Converter): Compressor Engine #4 - Oxidation Catalyst | Alliance Source Testing | 1,775 Hp | 0.30 g/Hp-hr 270 ppm | 1,651 Hp | 0.1 g/Hp-hr 8.8 ppm | 10 | CO - Carbon Monoxide | PASS | NA | Y
2014 | 504 | 0634005033 | Harrison West Compressor Station | Possum Hollow Road | Freeport | 43973 |  | Harrison | P003 | Compressor Engine #3 - 1980 HP (15.43 MMBtu/hr) Waukesha P9390 - natural gas-fired four-stroke rich burn internal combustion engine equipped with a three-way oxidation catalyst controlling CH2O, CO, NOx, & VOCs by 80, 97, 98.5 & 66 percent respectively | 2014-12-11 | CC001(Catalytic Converter): Compressor Engine #1 - 3-way Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - 3-way Catalyst; CC004(Catalytic Converter): Compressor Engine #4 - 3-way Catalyst; CC007(Catalytic Converter): Compressor Engine #7 - 3-w | Air Hygiene, Inc. | 1,980 hp | 0.25 g/hp-hr | 1,820 hp | 0.10 g/hp-hr | 10 | CO - Carbon Monoxide | PASS | NA | Y
2014 | 505 | 0634005033 | Harrison West Compressor Station | Possum Hollow Road | Freeport | 43973 |  | Harrison | P003 | Compressor Engine #3 - 1980 HP (15.43 MMBtu/hr) Waukesha P9390 - natural gas-fired four-stroke rich burn internal combustion engine equipped with a three-way oxidation catalyst controlling CH2O, CO, NOx, & VOCs by 80, 97, 98.5 & 66 percent respectively | 2014-12-12 | CC001(Catalytic Converter): Compressor Engine #1 - 3-way Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - 3-way Catalyst; CC004(Catalytic Converter): Compressor Engine #4 - 3-way Catalyst; CC007(Catalytic Converter): Compressor Engine #7 - 3-w | Air Hygiene, Inc. | 1,980 hp | 0.25 g/hp-hr | 1,820 hp | 0.10 g/hp-hr | 10 | CO - Carbon Monoxide | PASS | NA | Y
2014 | 509 | 0634005034 | Lake Compressor Station | County Highway 21 | Freeport | 43973 |  | Harrison | P003 | Compressor Engine #3 - 1980 HP (15.43 MMBtu/hr) Waukesha P9390 - natural gas-fired four-stroke rich burn internal combustion engine equipped with a three-way oxidation catalyst controlling CH2O, CO, NOx, & VOCs by 80, 97, 98.5 & 66 percent respectively | 2014-12-15 | CC002(Catalytic Converter): Compressor Engine #2 - 3-way Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - 3-way Catalyst; CC004(Catalytic Converter): Compressor Engine #4 - 3-way Catalyst; CC005(Catalytic Converter):; CC011(Catalytic Converter | Air Hygiene, Inc | 1,980 hp | 0.25 g/hp-hr | 1,571 hp | 0.10 g/hp-hr | 10 | CO - Carbon Monoxide | PASS | NA | Y
2014 | 513 | 0634005034 | Lake Compressor Station | County Highway 21 | Freeport | 43973 |  | Harrison | P003 | Compressor Engine #3 - 1980 HP (15.43 MMBtu/hr) Waukesha P9390 - natural gas-fired four-stroke rich burn internal combustion engine equipped with a three-way oxidation catalyst controlling CH2O, CO, NOx, & VOCs by 80, 97, 98.5 & 66 percent respectively | 2014-12-16 | CC002(Catalytic Converter): Compressor Engine #2 - 3-way Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - 3-way Catalyst; CC004(Catalytic Converter): Compressor Engine #4 - 3-way Catalyst; CC005(Catalytic Converter):; CC011(Catalytic Converter | Air Hygiene, Inc | 1,980 hp | 0.25 g/hp-hr | 1,571 hp | 0.10 g/hp-hr | 10 | CO - Carbon Monoxide | PASS | NA | Y
2014 | 514 | 0661005002 | Summerfield Compressor Station | between CR-45 and HWY 233 | Caldwell | 43724 |  | Noble | P002 | Natural Gas Engine (2) 1,380 hp | 2014-05-01 | Catalyst 2(Catalytic Converter): Oxidation Catalyst; Flare(Flare): FL-1 | Environmental Quality Management | 1,380 hp | 2.0 g/hp-hr | 911 hp | 0.106 g/hp-hr | 10 | CO - Carbon Monoxide | PASS | NA | Y
2014 | 517 | 0607015001 | Tri-County Compressor Station (MarkWest / Ohio Oil Gath | North of intersection of Hwy 379 and Town | Barnesville | 43713 |  | Belmont | P004 | Compressor Engine #4 - 1980 HP (15.43 MMBtu/hr) Waukesha P9390 - natural gas-fired four-stroke rich burn internal combustion engine equipped with a three-way oxidation catalyst controlling CH2O, CO, NOx, & VOCs by 80, 97, 98.5 & 66 percent respectively | 2014-11-11 | CC002(Catalytic Converter): Compressor Engine #2 - 3-way Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - 3-way Catalyst; CC004(Catalytic Converter): Compressor Engine #4 - 3-way Catalyst; CC005(Catalytic Converter): Compressor Engine #5 - 3-w | Air Hygiene, Inc | 1,980 hp | 2.0 g/hp-hr | 1,525 hp | 0.11 g/hp-hr | 10 | CO - Carbon Monoxide | PASS | NA | Y
2014 | 522 | 0607015001 | Tri-County Compressor Station (MarkWest / Ohio Oil Gath | North of intersection of Hwy 379 and Town | Barnesville | 43713 |  | Belmont | P004 | Compressor Engine #4 - 1980 HP (15.43 MMBtu/hr) Waukesha P9390 - natural gas-fired four-stroke rich burn internal combustion engine equipped with a three-way oxidation catalyst controlling CH2O, CO, NOx, & VOCs by 80, 97, 98.5 & 66 percent respectively | 2014-11-12 | CC002(Catalytic Converter): Compressor Engine #2 - 3-way Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - 3-way Catalyst; CC004(Catalytic Converter): Compressor Engine #4 - 3-way Catalyst; CC005(Catalytic Converter): Compressor Engine #5 - 3-w | Air Hygiene, Inc | 1,980 hp | 2.0 g/hp-hr | 1,525 hp | 0.11 g/hp-hr | 10 | CO - Carbon Monoxide | PASS | NA | Y
2014 | 524 | 0607015001 | Tri-County Compressor Station (MarkWest / Ohio Oil Gath | North of intersection of Hwy 379 and Town | Barnesville | 43713 |  | Belmont | P004 | Compressor Engine #4 - 1980 HP (15.43 MMBtu/hr) Waukesha P9390 - natural gas-fired four-stroke rich burn internal combustion engine equipped with a three-way oxidation catalyst controlling CH2O, CO, NOx, & VOCs by 80, 97, 98.5 & 66 percent respectively | 2014-11-29 | CC002(Catalytic Converter): Compressor Engine #2 - 3-way Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - 3-way Catalyst; CC004(Catalytic Converter): Compressor Engine #4 - 3-way Catalyst; CC005(Catalytic Converter): Compressor Engine #5 - 3-w | Air Hygiene, Inc | 1,980 hp | 2.0 g/hp-hr | 1,525 hp | 0.11 g/hp-hr | 10 | CO - Carbon Monoxide | PASS | NA | Y
2014 | 527 | 0634005033 | Harrison West Compressor Station | Possum Hollow Road | Freeport | 43973 |  | Harrison | P004 | Compressor Engine #4 - 1980 HP (15.43 MMBtu/hr) Waukesha P9390 - natural gas-fired four-stroke rich burn internal combustion engine equipped with a three-way oxidation catalyst controlling CH2O, CO, NOx, & VOCs by 80, 97, 98.5 & 66 percent respectively | 2014-12-11 | CC001(Catalytic Converter): Compressor Engine #1 - 3-way Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - 3-way Catalyst; CC004(Catalytic Converter): Compressor Engine #4 - 3-way Catalyst; CC007(Catalytic Converter): Compressor Engine #7 - 3-w | Air Hygiene, Inc. | 1,980 hp | 0.25 g/hp-hr | 1,824 hp | 0.11 g/hp-hr | 10 | CO - Carbon Monoxide | PASS | NA | Y
2014 | 531 | 0634005033 | Harrison West Compressor Station | Possum Hollow Road | Freeport | 43973 |  | Harrison | P004 | Compressor Engine #4 - 1980 HP (15.43 MMBtu/hr) Waukesha P9390 - natural gas-fired four-stroke rich burn internal combustion engine equipped with a three-way oxidation catalyst controlling CH2O, CO, NOx, & VOCs by 80, 97, 98.5 & 66 percent respectively | 2014-12-12 | CC001(Catalytic Converter): Compressor Engine #1 - 3-way Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - 3-way Catalyst; CC004(Catalytic Converter): Compressor Engine #4 - 3-way Catalyst; CC007(Catalytic Converter): Compressor Engine #7 - 3-w | Air Hygiene, Inc. | 1,980 hp | 0.25 g/hp-hr | 1,824 hp | 0.11 g/hp-hr | 10 | CO - Carbon Monoxide | PASS | NA | Y
2014 | 534 | 0634005029 | Cadiz Gas Plant | 43071 Industrial Park Rd | Cadiz | 43907 |  | Harrison | P007 | Compressor Engine #7 - 4735 HP Caterpillar G3616 engine (CM-1206-7) - natural gas-fired four-stroke lean burn internal combustion engine equipped with an oxidation catalyst controlling CO, VOC and formaldehyde 95, 75, and 90 percent respectively. | 2014-12-19 | CC007(Catalytic Converter): oxidation catalyst; CC008(Catalytic Converter): oxidation catalyst | Air Hygiene | 4,735 hp | 0.14 g/hp-hr | 4,376 hp | 0.12 g/hp-hr | 10 | CO - Carbon Monoxide | PASS | NA | Y
2014 | 536 | 0634005033 | Harrison West Compressor Station | Possum Hollow Road | Freeport | 43973 |  | Harrison | P002 | Compressor Engine #2 - 1480 HP (11.39 MMBtu/hr) Waukesha L7042 - natural gas-fired four-stroke rich burn internal combustion engine equipped with a three-way oxidation catalyst controlling CH2O, CO, NOx, & VOCs by 80, 97, 98.5 & 66 percent respectively | 2014-04-09 | CC002(Catalytic Converter): Compressor Engine #2 - 3-way Catalyst | Air Hygiene International | 1,480 hp | 2.0 g/hp-hr | 1,881 hp | 0.13 g/hp-hr | 10 | CO - Carbon Monoxide | PASS | NA | Y
2014 | 542 | 0634005049 | Gulfport Energy- Ryser #1-25H Well Pad | 77100 Scott Hill Road | Flushing | 43977 |  | Harrison | P002 | One or multiple stationary natural gas-fired spark ignition (SI) internal combustion engines (ICE) with a combined total horsepower (HP) of no more than 1,800 HP for the site. | 2014-07-07 | catalytic reduction | BCMJ Control, Inc | 325 Hp caterpillar engine s#4RD00578 | 4.0 g/Hp-hr | 134 hp | 0.14 g/Hp-hr | 10 | CO - Carbon Monoxide | PASS | NA | Y | 215 Hp Caterpillar engine-NOX 42.0 g/Hp-hr 215 Hp 0.14 g/Hp-hr 36 Hp S# G6X00951
2014 | 549 | 0634005034 | Lake Compressor Station | County Highway 21 | Freeport | 43973 |  | Harrison | P002 | Compressor Engine #2 - 1480 HP (11.39 MMBtu/hr) Waukesha L7042 - natural gas-fired four-stroke rich burn internal combustion engine equipped with a three-way oxidation catalyst controlling CH2O, CO, NOx, & VOCs by 80, 97, 98.5 & 66 percent respectively | 2014-12-15 | CC002(Catalytic Converter): Compressor Engine #2 - 3-way Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - 3-way Catalyst; CC004(Catalytic Converter): Compressor Engine #4 - 3-way Catalyst; CC005(Catalytic Converter):; CC011(Catalytic Converter | Air Hygiene, Inc | 1,480 hp | 0.25 g/hp-hr | 1,151 hp | 0.16 g/hp-hr | 10 | CO - Carbon Monoxide | PASS | NA | Y
2014 | 551 | 0634005034 | Lake Compressor Station | County Highway 21 | Freeport | 43973 |  | Harrison | P002 | Compressor Engine #2 - 1480 HP (11.39 MMBtu/hr) Waukesha L7042 - natural gas-fired four-stroke rich burn internal combustion engine equipped with a three-way oxidation catalyst controlling CH2O, CO, NOx, & VOCs by 80, 97, 98.5 & 66 percent respectively | 2014-12-16 | CC002(Catalytic Converter): Compressor Engine #2 - 3-way Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - 3-way Catalyst; CC004(Catalytic Converter): Compressor Engine #4 - 3-way Catalyst; CC005(Catalytic Converter):; CC011(Catalytic Converter | Air Hygiene, Inc | 1,480 hp | 0.25 g/hp-hr | 1,151 hp | 0.16 g/hp-hr | 10 | CO - Carbon Monoxide | PASS | NA | Y
2014 | 557 | 0634005059 | Chesapeake Exploration LLC - Kidd 21-12-6 Pad | Township Highway 219 - Beagle Club Rd | Scio | 43988 |  | Harrison | P002 | One or multiple stationary natural gas-fired spark ignition (SI) internal combustion engines (ICE) with a combined total horsepower (HP) of no more than 1,800 HP for the site.* Includes 2007 and later model year engines manufactured after the applicable effective date identified in 40 CFR 60.4230(a)(3) and engines manufactured before the NSPS effective date where compliance with the Part 60 Subpart JJJJ emissions standards for the same size engine can be demonstrated through stack testing. | 2014-06-30 | none | Alliance Source Testing | 211 Hp | 4.0 g/Hp-hr | 143 Hp | 0.17 g/Hp-hr | 10 | CO - Carbon Monoxide | PASS | NA | Y
2014 | 559 | 0607015001 | Tri-County Compressor Station (MarkWest / Ohio Oil Gath | North of intersection of Hwy 379 and Town | Barnesville | 43713 |  | Belmont | P005 | Compressor Engine #5 - 1980 HP (15.43 MMBtu/hr) Waukesha P9390 - natural gas-fired four-stroke rich burn internal combustion engine equipped with a three-way oxidation catalyst controlling CH2O, CO, NOx, & VOCs by 80, 97, 98.5 & 66 percent respectively | 2014-11-11 | CC002(Catalytic Converter): Compressor Engine #2 - 3-way Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - 3-way Catalyst; CC004(Catalytic Converter): Compressor Engine #4 - 3-way Catalyst; CC005(Catalytic Converter): Compressor Engine #5 - 3-w | Air Hygiene, Inc | 1,980 hp | 2.0 g/hp-hr | 1,482 hp | 0.18 g/hp-hr | 10 | CO - Carbon Monoxide | PASS | NA | Y
2014 | 564 | 0607015001 | Tri-County Compressor Station (MarkWest / Ohio Oil Gath | North of intersection of Hwy 379 and Town | Barnesville | 43713 |  | Belmont | P005 | Compressor Engine #5 - 1980 HP (15.43 MMBtu/hr) Waukesha P9390 - natural gas-fired four-stroke rich burn internal combustion engine equipped with a three-way oxidation catalyst controlling CH2O, CO, NOx, & VOCs by 80, 97, 98.5 & 66 percent respectively | 2014-11-12 | CC002(Catalytic Converter): Compressor Engine #2 - 3-way Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - 3-way Catalyst; CC004(Catalytic Converter): Compressor Engine #4 - 3-way Catalyst; CC005(Catalytic Converter): Compressor Engine #5 - 3-w | Air Hygiene, Inc | 1,980 hp | 2.0 g/hp-hr | 1,482 hp | 0.18 g/hp-hr | 10 | CO - Carbon Monoxide | PASS | NA | Y
2014 | 567 | 0607015001 | Tri-County Compressor Station (MarkWest / Ohio Oil Gath | North of intersection of Hwy 379 and Town | Barnesville | 43713 |  | Belmont | P005 | Compressor Engine #5 - 1980 HP (15.43 MMBtu/hr) Waukesha P9390 - natural gas-fired four-stroke rich burn internal combustion engine equipped with a three-way oxidation catalyst controlling CH2O, CO, NOx, & VOCs by 80, 97, 98.5 & 66 percent respectively | 2014-11-29 | CC002(Catalytic Converter): Compressor Engine #2 - 3-way Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - 3-way Catalyst; CC004(Catalytic Converter): Compressor Engine #4 - 3-way Catalyst; CC005(Catalytic Converter): Compressor Engine #5 - 3-w | Air Hygiene, Inc | 1,980 hp | 2.0 g/hp-hr | 1,482 hp | 0.18 g/hp-hr | 10 | CO - Carbon Monoxide | PASS | NA | Y
2014 | 570 | 0634005034 | Lake Compressor Station | County Highway 21 | Freeport | 43973 |  | Harrison | P004 | Compressor Engine #4 - 1980 HP (15.43 MMBtu/hr) Waukesha P9390 - natural gas-fired four-stroke rich burn internal combustion engine equipped with a three-way oxidation catalyst controlling CH2O, CO, NOx, & VOCs by 80, 97, 98.5 & 66 percent respectively | 2014-04-10 | CC004(Catalytic Converter): Compressor Engine #4 - 3-way Catalyst | Air Hygiene International | 1,980 hp | 2.0 g/hp-hr | 1,782 hp | 0.18 g/hp-hr | 10 | CO - Carbon Monoxide | PASS | NA | Y
2014 | 573 | 0634005034 | Lake Compressor Station | County Highway 21 | Freeport | 43973 |  | Harrison | P011 | Compressor Engine #9 - Waukesha L7042 - natural gas fired four-stroke, rich burn internal combustion engine rated at an operating capacity of 1,480 horsepower equipped with a three-way oxidation catalyst. | 2014-12-15 | CC002(Catalytic Converter): Compressor Engine #2 - 3-way Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - 3-way Catalyst; CC004(Catalytic Converter): Compressor Engine #4 - 3-way Catalyst; CC005(Catalytic Converter):; CC011(Catalytic Converter | Air Hygiene, Inc | 1,480 hp | 0.25 g/hp-hr | 1,014 hp | 0.18 g/hp-hr | 10 | CO - Carbon Monoxide | PASS | NA | Y
2014 | 575 | 0634005034 | Lake Compressor Station | County Highway 21 | Freeport | 43973 |  | Harrison | P011 | Compressor Engine #9 - Waukesha L7042 - natural gas fired four-stroke, rich burn internal combustion engine rated at an operating capacity of 1,480 horsepower equipped with a three-way oxidation catalyst. | 2014-12-16 | CC002(Catalytic Converter): Compressor Engine #2 - 3-way Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - 3-way Catalyst; CC004(Catalytic Converter): Compressor Engine #4 - 3-way Catalyst; CC005(Catalytic Converter):; CC011(Catalytic Converter | Air Hygiene, Inc | 1,480 hp | 0.25 g/hp-hr | 1,014 hp | 0.18 g/hp-hr | 10 | CO - Carbon Monoxide | PASS | NA | Y
2014 | 578 | 0210012004 | Augusta Compressor Facility- Utica Gas Services, L.L.C. | 8034 Bane Rd NE | East Twp. | 44427 |  | Carroll | P009 | 1,775-hp Caterpillar G3606 Compressor Engine w/ Oxidation Catalyst | 2014-09-16 | Oxid. Cat. 3(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 4(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 5(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 6(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 7(Catalytic Converter): | Great Plains Analytical | 1775 Hp | 1.18 lbs/hr, 2.0 g/hp/hr, 270ppmvd@15%O2 | 1788 | 0.20 lbs/hr, 0.05 g/hp/hr, 8.06 ppmvd@15%O2 | 10 | CO - Carbon Monoxide | PASS | NA | Y
2014 | 581 | 0210012004 | Augusta Compressor Facility- Utica Gas Services, L.L.C. | 8034 Bane Rd NE | East Twp. | 44427 |  | Carroll | P009 | 1,775-hp Caterpillar G3606 Compressor Engine w/ Oxidation Catalyst | 2014-09-17 | Oxid. Cat. 3(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 4(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 5(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 6(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 7(Catalytic Converter): | Great Plains Analytical | 1775 Hp | 1.18 lbs/hr, 2.0 g/hp/hr, 270ppmvd@15%O2 | 1788 | 0.20 lbs/hr, 0.05 g/hp/hr, 8.06 ppmvd@15%O2 | 10 | CO - Carbon Monoxide | PASS | NA | Y
2014 | 584 | 0210012004 | Augusta Compressor Facility- Utica Gas Services, L.L.C. | 8034 Bane Rd NE | East Twp. | 44427 |  | Carroll | P009 | 1,775-hp Caterpillar G3606 Compressor Engine w/ Oxidation Catalyst | 2014-09-18 | Oxid. Cat. 3(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 4(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 5(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 6(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 7(Catalytic Converter): | Great Plains Analytical | 1775 Hp | 1.18 lbs/hr, 2.0 g/hp/hr, 270ppmvd@15%O2 | 1788 | 0.20 lbs/hr, 0.05 g/hp/hr, 8.06 ppmvd@15%O2 | 10 | CO - Carbon Monoxide | PASS | NA | Y
2014 | 587 | 0634005033 | Harrison West Compressor Station | Possum Hollow Road | Freeport | 43973 |  | Harrison | P001 | Compressor Engine #1 - 1480 HP (11.39 MMBtu/hr) Waukesha L7042 - natural gas-fired four-stroke rich burn internal combustion engine equipped with a three-way oxidation catalyst controlling CH2O, CO, NOx, & VOCs by 80, 97, 98.5 & 66 percent respectively | 2014-12-11 | CC001(Catalytic Converter): Compressor Engine #1 - 3-way Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - 3-way Catalyst; CC004(Catalytic Converter): Compressor Engine #4 - 3-way Catalyst; CC007(Catalytic Converter): Compressor Engine #7 - 3-w | Air Hygiene, Inc. | 1,480 hp | 0.25 g/hp-hr | 1,324 hp | 0.21 g/hp-hr | 10 | CO - Carbon Monoxide | PASS | NA | Y
2014 | 590 | 0634005033 | Harrison West Compressor Station | Possum Hollow Road | Freeport | 43973 |  | Harrison | P001 | Compressor Engine #1 - 1480 HP (11.39 MMBtu/hr) Waukesha L7042 - natural gas-fired four-stroke rich burn internal combustion engine equipped with a three-way oxidation catalyst controlling CH2O, CO, NOx, & VOCs by 80, 97, 98.5 & 66 percent respectively | 2014-12-12 | CC001(Catalytic Converter): Compressor Engine #1 - 3-way Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - 3-way Catalyst; CC004(Catalytic Converter): Compressor Engine #4 - 3-way Catalyst; CC007(Catalytic Converter): Compressor Engine #7 - 3-w | Air Hygiene, Inc. | 1,480 hp | 0.25 g/hp-hr | 1,324 hp | 0.21 g/hp-hr | 10 | CO - Carbon Monoxide | PASS | NA | Y
2014 | 592 | 0634005034 | Lake Compressor Station | County Highway 21 | Freeport | 43973 |  | Harrison | P002 | Compressor Engine #2 - 1480 HP (11.39 MMBtu/hr) Waukesha L7042 - natural gas-fired four-stroke rich burn internal combustion engine equipped with a three-way oxidation catalyst controlling CH2O, CO, NOx, & VOCs by 80, 97, 98.5 & 66 percent respectively | 2014-04-11 | CC002(Catalytic Converter): Compressor Engine #2 - 3-way Catalyst | Air Hygiene International | 1,480 hp | 2.0 g/hp-hr | 1,480 hp | 0.21 g/hp-hr | 10 | CO - Carbon Monoxide | PASS | NA | Y
2014 | 597 | 0634005072 | Gulfport Energy - Milliken | 31255 Cadiz-Piedmont Rd | Freeport | 43973 |  | Harrison | P002 | One or multiple stationary natural gas-fired spark ignition (SI) internal combustion engines (ICE) wiht a combined total horsepower (HP) of no more than 1,800 HP for the site. | 2014-08-12 | catalytic | BCMJ Controls Inc | 145 Hp S# O7Y05427 | 4.0 g/Hp-hr | 122 Hp | 0.21 g/Hp-hr | 10 | CO - Carbon Monoxide | PASS | NA | Y | 60 Hp HEC engine 4.8 g/Hp-hr 60 Hp 0.68 g/Hp-hr 30 Hp
2014 | 599 | 0607015001 | Tri-County Compressor Station (MarkWest / Ohio Oil Gath | North of intersection of Hwy 379 and Town | Barnesville | 43713 |  | Belmont | P003 | Compressor Engine #3 - 1980 HP (15.43 MMBtu/hr) Waukesha P9390 - natural gas-fired four-stroke rich burn internal combustion engine equipped with a three-way oxidation catalyst controlling CH2O, CO, NOx, & VOCs by 80, 97, 98.5 & 66 percent respectively | 2014-11-11 | CC002(Catalytic Converter): Compressor Engine #2 - 3-way Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - 3-way Catalyst; CC004(Catalytic Converter): Compressor Engine #4 - 3-way Catalyst; CC005(Catalytic Converter): Compressor Engine #5 - 3-w | Air Hygiene, Inc | 1,980 hp | 2.0 g/hp-hr | 1,526 hp | 0.22 g/hp-hr | 10 | CO - Carbon Monoxide | PASS | NA | Y
2014 | 602 | 0607015001 | Tri-County Compressor Station (MarkWest / Ohio Oil Gath | North of intersection of Hwy 379 and Town | Barnesville | 43713 |  | Belmont | P003 | Compressor Engine #3 - 1980 HP (15.43 MMBtu/hr) Waukesha P9390 - natural gas-fired four-stroke rich burn internal combustion engine equipped with a three-way oxidation catalyst controlling CH2O, CO, NOx, & VOCs by 80, 97, 98.5 & 66 percent respectively | 2014-11-12 | CC002(Catalytic Converter): Compressor Engine #2 - 3-way Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - 3-way Catalyst; CC004(Catalytic Converter): Compressor Engine #4 - 3-way Catalyst; CC005(Catalytic Converter): Compressor Engine #5 - 3-w | Air Hygiene, Inc | 1,980 hp | 2.0 g/hp-hr | 1,526 hp | 0.22 g/hp-hr | 10 | CO - Carbon Monoxide | PASS | NA | Y
2014 | 604 | 0607015001 | Tri-County Compressor Station (MarkWest / Ohio Oil Gath | North of intersection of Hwy 379 and Town | Barnesville | 43713 |  | Belmont | P003 | Compressor Engine #3 - 1980 HP (15.43 MMBtu/hr) Waukesha P9390 - natural gas-fired four-stroke rich burn internal combustion engine equipped with a three-way oxidation catalyst controlling CH2O, CO, NOx, & VOCs by 80, 97, 98.5 & 66 percent respectively | 2014-11-29 | CC002(Catalytic Converter): Compressor Engine #2 - 3-way Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - 3-way Catalyst; CC004(Catalytic Converter): Compressor Engine #4 - 3-way Catalyst; CC005(Catalytic Converter): Compressor Engine #5 - 3-w | Air Hygiene, Inc | 1,980 hp | 2.0 g/hp-hr | 1,526 hp | 0.22 g/hp-hr | 10 | CO - Carbon Monoxide | PASS | NA | Y
2014 | 607 | 0634005033 | Harrison West Compressor Station | Possum Hollow Road | Freeport | 43973 |  | Harrison | P005 | Compressor Engine #5 - 1980 HP (15.43 MMBtu/hr) Waukesha P9390 - natural gas-fired four-stroke rich burn internal combustion engine equipped with a three-way oxidation catalyst controlling CH2O, CO, NOx, & VOCs by 80, 97, 98.5 & 66 percent respectively | 2014-04-08 | CC005(Catalytic Converter): Compressor Engine #5 - 3-way Catalyst | Air Hygiene International | 1,980 hp | 2.0 g/hp-hr | 1,868 | 0.23 g/hp-hr | 10A | CO - Carbon Monoxide | PASS | NA | Y
2014 | 612 | 0634005040 | Archer Compressor Facility | County Highway 45 | Cadiz | 43907 |  | Harrison | P008 | Compressor Engine #8 - 1775 HP Caterpillar G3606 (4S-LB) - natural gas-fired four-cycle lean burn internal combustion engine rated equipped with an oxidation catalyst controlling CO and VOC emissions. | 2014-11-12 | OxidCat-108(Catalytic Converter): Oxidative Catalyst | EcoTest Energy Services | 1775 Hp | 2.00 g/Hp-hr | 1608 Hp | 0.23 g/Hp-hr | 10 | CO - Carbon Monoxide | PASS | NA | Y | Method 10 not used. Methods 205, 320 and ASTM 6348-3 FTIR
2014 | 616 | 0210012004 | Augusta Compressor Facility- Utica Gas Services, L.L.C. | 8034 Bane Rd NE | East Twp. | 44427 |  | Carroll | P008 | 1,775-hp Caterpillar G3606 Compressor Engine w/ Oxidation Catalyst | 2014-09-16 | Oxid. Cat. 3(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 4(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 5(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 6(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 7(Catalytic Converter): | Great Plains Analytical | 1775 Hp | 1.18 lbs/hr, 2.0 g/hp/hr, 270ppmvd@15%O2 | 1809 | 0.23 lbs/hr, 0.05 g/hp/hr, 9.11 ppmvd@15%O2 | 10 | CO - Carbon Monoxide | PASS | NA | Y
2014 | 619 | 0210012004 | Augusta Compressor Facility- Utica Gas Services, L.L.C. | 8034 Bane Rd NE | East Twp. | 44427 |  | Carroll | P008 | 1,775-hp Caterpillar G3606 Compressor Engine w/ Oxidation Catalyst | 2014-09-17 | Oxid. Cat. 3(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 4(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 5(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 6(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 7(Catalytic Converter): | Great Plains Analytical | 1775 Hp | 1.18 lbs/hr, 2.0 g/hp/hr, 270ppmvd@15%O2 | 1809 | 0.23 lbs/hr, 0.05 g/hp/hr, 9.11 ppmvd@15%O2 | 10 | CO - Carbon Monoxide | PASS | NA | Y
2014 | 623 | 0210012004 | Augusta Compressor Facility- Utica Gas Services, L.L.C. | 8034 Bane Rd NE | East Twp. | 44427 |  | Carroll | P008 | 1,775-hp Caterpillar G3606 Compressor Engine w/ Oxidation Catalyst | 2014-09-18 | Oxid. Cat. 3(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 4(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 5(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 6(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 7(Catalytic Converter): | Great Plains Analytical | 1775 Hp | 1.18 lbs/hr, 2.0 g/hp/hr, 270ppmvd@15%O2 | 1809 | 0.23 lbs/hr, 0.05 g/hp/hr, 9.11 ppmvd@15%O2 | 10 | CO - Carbon Monoxide | PASS | NA | Y
2014 | 627 | 0661005010 | E2 Appalachian Compression LLC - Upper Hill | Opossum Run Rd and Town Hwy 120 | Sarahsville | 43779 |  | Noble | P007 | 1,680 Hp. Waukesha (L7044GSI) natural gas-fired, rich burn, turbocharged, with oxidation catalyst, compressor engine. | 2014-11-06 | C-7(Catalytic Converter): Engine Catalyst; C-8(Catalytic Converter): Engine Catalyst; C-9(Catalytic Converter): Engine Catalyst | E2 Energy Services | 1680 Hp | 0.94 lb/hr | 1528 Hp | 0.26 lb/hr | 10 | CO - Carbon Monoxide | PASS | NA | Y | Method 10 not used. Method 3A and ASTM 6348-03 used
2014 | 629 | 0656105005 | E2 Appalachian Compression LLC - Reusser | Twp Hwy 68 and Twp Hwy 66 | Woodsfield | 43793 |  | Monroe | P006 | 1680 Hp. natural gas rich burn compressor engine - Waukesha L7044GSI | 2014-12-08 | C-3(Catalytic Converter): Engine #3 Catalyst; C-4(Catalytic Converter): Engine #4 Catalyst; C-5(Catalytic Converter): Engine #5 Catalyst; C-6(Catalytic Converter): Engine #6Catalyst; C-8(Catalytic Converter): Engine #8 Catalyst | E2 Energy Services | 1,680 hp | 0.94 lb/hr | 1,551 hp | 0.27 lb/hr | 6348 03 | CO - Carbon Monoxide | PASS | NA | Y
2014 | 632 | 0656105005 | E2 Appalachian Compression LLC - Reusser | Twp Hwy 68 and Twp Hwy 66 | Woodsfield | 43793 |  | Monroe | P006 | 1680 Hp. natural gas rich burn compressor engine - Waukesha L7044GSI | 2014-12-10 | C-3(Catalytic Converter): Engine #3 Catalyst; C-4(Catalytic Converter): Engine #4 Catalyst; C-5(Catalytic Converter): Engine #5 Catalyst; C-6(Catalytic Converter): Engine #6Catalyst; C-8(Catalytic Converter): Engine #8 Catalyst | E2 Energy Services | 1,680 hp | 0.94 lb/hr | 1,551 hp | 0.27 lb/hr | 6348 03 | CO - Carbon Monoxide | PASS | NA | Y
2014 | 634 | 0656105005 | E2 Appalachian Compression LLC - Reusser | Twp Hwy 68 and Twp Hwy 66 | Woodsfield | 43793 |  | Monroe | P006 | 1680 Hp. natural gas rich burn compressor engine - Waukesha L7044GSI | 2014-12-11 | C-3(Catalytic Converter): Engine #3 Catalyst; C-4(Catalytic Converter): Engine #4 Catalyst; C-5(Catalytic Converter): Engine #5 Catalyst; C-6(Catalytic Converter): Engine #6Catalyst; C-8(Catalytic Converter): Engine #8 Catalyst | E2 Energy Services | 1,680 hp | 0.94 lb/hr | 1,551 hp | 0.27 lb/hr | 6348 03 | CO - Carbon Monoxide | PASS | NA | Y
2014 | 637 | 0210012004 | Augusta Compressor Facility- Utica Gas Services, L.L.C. | 8034 Bane Rd NE | East Twp. | 44427 |  | Carroll | P007 | 1,775-hp Caterpillar G3606 Compressor Engine w/ Oxidation Catalyst | 2014-09-16 | Oxid. Cat. 3(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 4(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 5(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 6(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 7(Catalytic Converter): | Great Plains Analytical | 1775 Hp | 1.18 lbs/hr, 2.0 g/hp/hr, 270ppmvd@15%O2 | 1839 | 0.27 lbs/hr, 0.06 g/hp/hr, 10.1 ppmvd@15%O2 | 10 | CO - Carbon Monoxide | PASS | NA | Y
2014 | 640 | 0210012004 | Augusta Compressor Facility- Utica Gas Services, L.L.C. | 8034 Bane Rd NE | East Twp. | 44427 |  | Carroll | P007 | 1,775-hp Caterpillar G3606 Compressor Engine w/ Oxidation Catalyst | 2014-09-17 | Oxid. Cat. 3(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 4(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 5(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 6(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 7(Catalytic Converter): | Great Plains Analytical | 1775 Hp | 1.18 lbs/hr, 2.0 g/hp/hr, 270ppmvd@15%O2 | 1839 | 0.27 lbs/hr, 0.06 g/hp/hr, 10.1 ppmvd@15%O2 | 10 | CO - Carbon Monoxide | PASS | NA | Y
2014 | 643 | 0210012004 | Augusta Compressor Facility- Utica Gas Services, L.L.C. | 8034 Bane Rd NE | East Twp. | 44427 |  | Carroll | P007 | 1,775-hp Caterpillar G3606 Compressor Engine w/ Oxidation Catalyst | 2014-09-18 | Oxid. Cat. 3(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 4(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 5(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 6(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 7(Catalytic Converter): | Great Plains Analytical | 1775 Hp | 1.18 lbs/hr, 2.0 g/hp/hr, 270ppmvd@15%O2 | 1839 | 0.27 lbs/hr, 0.06 g/hp/hr, 10.1 ppmvd@15%O2 | 10 | CO - Carbon Monoxide | PASS | NA | Y
2014 | 646 | 0634005033 | Harrison West Compressor Station | Possum Hollow Road | Freeport | 43973 |  | Harrison | P004 | Compressor Engine #4 - 1980 HP (15.43 MMBtu/hr) Waukesha P9390 - natural gas-fired four-stroke rich burn internal combustion engine equipped with a three-way oxidation catalyst controlling CH2O, CO, NOx, & VOCs by 80, 97, 98.5 & 66 percent respectively | 2014-04-08 | CC004(Catalytic Converter): Compressor Engine #4 - 3-way Catalyst | Air Hygiene International | 1,980 hp | 2.0 g/hp-hr | 1,782 hp | 0.28 g/hr-hr | 10 | CO - Carbon Monoxide | PASS | NA | Y
2014 | 649 | 0210012004 | Augusta Compressor Facility- Utica Gas Services, L.L.C. | 8034 Bane Rd NE | East Twp. | 44427 |  | Carroll | P012 | 1,775-hp Caterpillar G3606 Compressor Engine w/ Oxidation Catalyst | 2014-09-16 | Oxid. Cat. 3(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 4(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 5(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 6(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 7(Catalytic Converter): | Great Plains Analytical | 1775 Hp | 1.18 lbs/hr, 2.0 g/hp/hr, 270ppmvd@15%O2 | 1817 | 0.28 lbs/hr, 0.07 g/hp/hr, 10.74ppmvd@15%O2 | 10 | CO - Carbon Monoxide | PASS | NA | Y
2014 | 653 | 0210012004 | Augusta Compressor Facility- Utica Gas Services, L.L.C. | 8034 Bane Rd NE | East Twp. | 44427 |  | Carroll | P012 | 1,775-hp Caterpillar G3606 Compressor Engine w/ Oxidation Catalyst | 2014-09-17 | Oxid. Cat. 3(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 4(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 5(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 6(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 7(Catalytic Converter): | Great Plains Analytical | 1775 Hp | 1.18 lbs/hr, 2.0 g/hp/hr, 270ppmvd@15%O2 | 1817 | 0.28 lbs/hr, 0.07 g/hp/hr, 10.74ppmvd@15%O2 | 10 | CO - Carbon Monoxide | PASS | NA | Y
2014 | 657 | 0210012004 | Augusta Compressor Facility- Utica Gas Services, L.L.C. | 8034 Bane Rd NE | East Twp. | 44427 |  | Carroll | P012 | 1,775-hp Caterpillar G3606 Compressor Engine w/ Oxidation Catalyst | 2014-09-18 | Oxid. Cat. 3(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 4(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 5(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 6(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 7(Catalytic Converter): | Great Plains Analytical | 1775 Hp | 1.18 lbs/hr, 2.0 g/hp/hr, 270ppmvd@15%O2 | 1817 | 0.28 lbs/hr, 0.07 g/hp/hr, 10.74ppmvd@15%O2 | 10 | CO - Carbon Monoxide | PASS | NA | Y
2014 | 660 | 0210012004 | Augusta Compressor Facility- Utica Gas Services, L.L.C. | 8034 Bane Rd NE | East Twp. | 44427 |  | Carroll | P010 | 1,775-hp Caterpillar G3606 Compressor Engine w/ Oxidation Catalyst | 2014-09-16 | Oxid. Cat. 3(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 4(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 5(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 6(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 7(Catalytic Converter): | Great Plains Analytical | 1775 Hp | 1.18 lbs/hr, 2.0 g/hp/hr, 270ppmvd@15%O2 | 1819 | 0.28 lbs/hr, 0.07g/hp/hr, 10.94 ppmvd@15%O2 | 10 | CO - Carbon Monoxide | PASS | NA | Y
2014 | 662 | 0210012004 | Augusta Compressor Facility- Utica Gas Services, L.L.C. | 8034 Bane Rd NE | East Twp. | 44427 |  | Carroll | P013 | 1,775-hp Caterpillar G3606 Compressor Engine w/ Oxidation Catalyst | 2014-09-18 | Oxid. Cat. 3(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 4(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 5(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 6(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 7(Catalytic Converter): | Great Plains Analytical | 1775 Hp | 1.18 lbs/hr, 2.0 g/hp/hr, 270ppmvd@15%O2 | 1780 | 0.30 lbs/hr, 0.07 g/hp/hr, 11.62 ppmvd@15%O2 | 10 | CO - Carbon Monoxide | PASS | NA | Y
2014 | 665 | 0210012004 | Augusta Compressor Facility- Utica Gas Services, L.L.C. | 8034 Bane Rd NE | East Twp. | 44427 |  | Carroll | P006 | 1,775-hp Caterpillar G3606 Compressor Engine w/ Oxidation Catalyst | 2014-09-16 | Oxid. Cat. 3(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 4(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 5(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 6(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 7(Catalytic Converter): | Great Plains Analytical | 1775 Hp | 1.18 lbs/hr, 2.0 g/hp/hr, 270ppmvd@15%O2 | 1831 | 0.33 lbs/hr, 0.08 g/hp/hr, 12.9 ppmvd@15%O2 | 10 | CO - Carbon Monoxide | PASS | NA | Y
2014 | 667 | 0210012004 | Augusta Compressor Facility- Utica Gas Services, L.L.C. | 8034 Bane Rd NE | East Twp. | 44427 |  | Carroll | P006 | 1,775-hp Caterpillar G3606 Compressor Engine w/ Oxidation Catalyst | 2014-09-17 | Oxid. Cat. 3(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 4(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 5(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 6(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 7(Catalytic Converter): | Great Plains Analytical | 1775 Hp | 1.18 lbs/hr, 2.0 g/hp/hr, 270ppmvd@15%O2 | 1831 | 0.33 lbs/hr, 0.08 g/hp/hr, 12.9 ppmvd@15%O2 | 10 | CO - Carbon Monoxide | PASS | NA | Y
2014 | 671 | 0210012004 | Augusta Compressor Facility- Utica Gas Services, L.L.C. | 8034 Bane Rd NE | East Twp. | 44427 |  | Carroll | P006 | 1,775-hp Caterpillar G3606 Compressor Engine w/ Oxidation Catalyst | 2014-09-18 | Oxid. Cat. 3(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 4(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 5(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 6(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 7(Catalytic Converter): | Great Plains Analytical | 1775 Hp | 1.18 lbs/hr, 2.0 g/hp/hr, 270ppmvd@15%O2 | 1831 | 0.33 lbs/hr, 0.08 g/hp/hr, 12.9 ppmvd@15%O2 | 10 | CO - Carbon Monoxide | PASS | NA | Y
2014 | 674 | 0634005033 | Harrison West Compressor Station | Possum Hollow Road | Freeport | 43973 |  | Harrison | P001 | Compressor Engine #1 - 1480 HP (11.39 MMBtu/hr) Waukesha L7042 - natural gas-fired four-stroke rich burn internal combustion engine equipped with a three-way oxidation catalyst controlling CH2O, CO, NOx, & VOCs by 80, 97, 98.5 & 66 percent respectively | 2014-04-09 | CC001(Catalytic Converter): Compressor Engine #1 - 3-way Catalyst | Air Hygiene International | 1,480 hp | 2.0 g/hp-hr | 1,406 hp | 0.34 g/hp-hr | 10 | CO - Carbon Monoxide | PASS | NA | Y
2014 | 686 | 0634005033 | Harrison West Compressor Station | Possum Hollow Road | Freeport | 43973 |  | Harrison | P007 | Compressor Engine #7 - 1980 HP (15.43 MMBtu/hr) Waukesha P9390 - natural gas-fired four-stroke rich burn internal combustion engine equipped with a three-way oxidation catalyst controlling CH2O, CO, NOx, & VOCs by 80, 97, 98.5 & 66 percent respectively | 2014-04-09 | CC007(Catalytic Converter): Compressor Engine #7 - 3-way Catalyst | Air Hygiene International | 1,980 hp | 2.0 g/hp-hr | 1,822 hp | 0.35 g/hp-hr | 10 | CO - Carbon Monoxide | PASS | NA | Y
2014 | 693 | 0634005034 | Lake Compressor Station | County Highway 21 | Freeport | 43973 |  | Harrison | P003 | Compressor Engine #3 - 1980 HP (15.43 MMBtu/hr) Waukesha P9390 - natural gas-fired four-stroke rich burn internal combustion engine equipped with a three-way oxidation catalyst controlling CH2O, CO, NOx, & VOCs by 80, 97, 98.5 & 66 percent respectively | 2014-04-10 | CC003(Catalytic Converter): Compressor Engine #3 - 3-way Catalyst | Air Hygiene Internatjional | 1,980 hp | 2.0 g/hp-hr | 1,782 hp | 0.35 g/hp-hr | 10 | CO - Carbon Monoxide | PASS | NA | Y
2014 | 696 | 0210012004 | Augusta Compressor Facility- Utica Gas Services, L.L.C. | 8034 Bane Rd NE | East Twp. | 44427 |  | Carroll | P011 | 1,775-hp Caterpillar G3606 Compressor Engine w/ Oxidation Catalyst | 2014-09-16 | Oxid. Cat. 3(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 4(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 5(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 6(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 7(Catalytic Converter): | Great Plains Analytical | 1775 Hp | 1.18 lbs/hr, 2.0 g/hp/hr, 270ppmvd@15%O2 | 1821 | 0.38 lbs/hr, 0.09 g/hp/hr, 16.14 ppmvd@15%O2 | 10 | CO - Carbon Monoxide | PASS | NA | Y
2014 | 698 | 0210012004 | Augusta Compressor Facility- Utica Gas Services, L.L.C. | 8034 Bane Rd NE | East Twp. | 44427 |  | Carroll | P011 | 1,775-hp Caterpillar G3606 Compressor Engine w/ Oxidation Catalyst | 2014-09-17 | Oxid. Cat. 3(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 4(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 5(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 6(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 7(Catalytic Converter): | Great Plains Analytical | 1775 Hp | 1.18 lbs/hr, 2.0 g/hp/hr, 270ppmvd@15%O2 | 1821 | 0.38 lbs/hr, 0.09 g/hp/hr, 16.14 ppmvd@15%O2 | 10 | CO - Carbon Monoxide | PASS | NA | Y
2014 | 703 | 0210012004 | Augusta Compressor Facility- Utica Gas Services, L.L.C. | 8034 Bane Rd NE | East Twp. | 44427 |  | Carroll | P011 | 1,775-hp Caterpillar G3606 Compressor Engine w/ Oxidation Catalyst | 2014-09-18 | Oxid. Cat. 3(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 4(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 5(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 6(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 7(Catalytic Converter): | Great Plains Analytical | 1775 Hp | 1.18 lbs/hr, 2.0 g/hp/hr, 270ppmvd@15%O2 | 1821 | 0.38 lbs/hr, 0.09 g/hp/hr, 16.14 ppmvd@15%O2 | 10 | CO - Carbon Monoxide | PASS | NA | Y
2014 | 706 | 0630005024 | Gulfport Energy Corporation - Karen 23-9-7 Pad | Oxford Rd | Quaker City | 43773 |  | Guernsey | P002 | One or multiple stationary natural gas-fired spark ignition (SI) internal combustion engines (ICE) with a combined total horsepower (HP) of no more than 1,800 HP for the site. Includes 2007 and later model year engines manufactured after the applicable effective date identified in 40 CFR 60.4230(a)(3) and engines manufactured before the NSPS effective date where compliance with the Part 60 Subpart JJJJ emissions standards for the same size engine can be demonstrated through stack testing. | 2014-12-04 | none | Great Plains Analytical Services | 118 Hp | 4.0 g/Hp-hr | 63 Hp | 0.397 g/Hp-hr | 10 | CO - Carbon Monoxide | PASS | NA | Y | method 10 not used. methods 1-3a and ASTM 6348-03 FTIR
2014 | 717 | 0656105005 | E2 Appalachian Compression LLC - Reusser | Twp Hwy 68 and Twp Hwy 66 | Woodsfield | 43793 |  | Monroe | P008 | 1680 Hp. natural gas rich burn compressor engine - Waukesha L7044GSI | 2014-12-08 | C-3(Catalytic Converter): Engine #3 Catalyst; C-4(Catalytic Converter): Engine #4 Catalyst; C-5(Catalytic Converter): Engine #5 Catalyst; C-6(Catalytic Converter): Engine #6Catalyst; C-8(Catalytic Converter): Engine #8 Catalyst | E2 Energy Services | 1,680 hp | 0.94 lb/hr | 1,551 hp | 0.46 lb/hr | 6348 03 | CO - Carbon Monoxide | PASS | NA | Y
2014 | 718 | 0656105005 | E2 Appalachian Compression LLC - Reusser | Twp Hwy 68 and Twp Hwy 66 | Woodsfield | 43793 |  | Monroe | P008 | 1680 Hp. natural gas rich burn compressor engine - Waukesha L7044GSI | 2014-12-10 | C-3(Catalytic Converter): Engine #3 Catalyst; C-4(Catalytic Converter): Engine #4 Catalyst; C-5(Catalytic Converter): Engine #5 Catalyst; C-6(Catalytic Converter): Engine #6Catalyst; C-8(Catalytic Converter): Engine #8 Catalyst | E2 Energy Services | 1,680 hp | 0.94 lb/hr | 1,551 hp | 0.46 lb/hr | 6348 03 | CO - Carbon Monoxide | PASS | NA | Y
2014 | 719 | 0656105005 | E2 Appalachian Compression LLC - Reusser | Twp Hwy 68 and Twp Hwy 66 | Woodsfield | 43793 |  | Monroe | P008 | 1680 Hp. natural gas rich burn compressor engine - Waukesha L7044GSI | 2014-12-11 | C-3(Catalytic Converter): Engine #3 Catalyst; C-4(Catalytic Converter): Engine #4 Catalyst; C-5(Catalytic Converter): Engine #5 Catalyst; C-6(Catalytic Converter): Engine #6Catalyst; C-8(Catalytic Converter): Engine #8 Catalyst | E2 Energy Services | 1,680 hp | 0.94 lb/hr | 1,551 hp | 0.46 lb/hr | 6348 03 | CO - Carbon Monoxide | PASS | NA | Y
2014 | 724 | 0630005012 | Gulfport Energy- Groh Well Pad | 19667 Cadiz Rd | Quaker City | 42773 |  | Guernsey | P002 | One 50-hp Zenith ZPP416 and one 203-hp Caterpillar G3306B NA natural gas-fired engines for compressors. One or multiple stationary natural gas-fired spark ignition (SI) internal combustion engines (ICE) wiht a combined total horsepower (HP) or no more than 1,800 HP for the site. | 2014-08-07 | none | BCMJ Controls Inc. | 145 Hp | 4.0 g/Hp-hr | 128 Hp | 0.51 g/Hp-hr | 10 | CO - Carbon Monoxide | PASS | NA | Y
2014 | 772 | 0661005010 | E2 Appalachian Compression LLC - Upper Hill | Opossum Run Rd and Town Hwy 120 | Sarahsville | 43779 |  | Noble | P009 | 1,680 Hp. Waukesha (L7044GSI) natural gas-fired, rich burn, turbocharged, with oxidation catalyst, compressor engine. | 2014-11-06 | C-7(Catalytic Converter): Engine Catalyst; C-8(Catalytic Converter): Engine Catalyst; C-9(Catalytic Converter): Engine Catalyst | E2 Energy Services | 1680 Hp | 0.94 lb/hr | 1585 Hp | 0.52 lb/hr | 10 | CO - Carbon Monoxide | PASS | NA | Y | Method 10 not used. Method 3A and ASTM 6348-03 used
2014 | 776 | 0656105005 | E2 Appalachian Compression LLC - Reusser | Twp Hwy 68 and Twp Hwy 66 | Woodsfield | 43793 |  | Monroe | P005 | 1680 Hp. natural gas rich burn compressor engine - Waukesha L7044GSI | 2014-12-08 | C-3(Catalytic Converter): Engine #3 Catalyst; C-4(Catalytic Converter): Engine #4 Catalyst; C-5(Catalytic Converter): Engine #5 Catalyst; C-6(Catalytic Converter): Engine #6Catalyst; C-8(Catalytic Converter): Engine #8 Catalyst | E2 Energy Services | 1,680 hp | 0.94 lb/hr | 1,557 hp | 0.61 lb/hr | 6348 03 | CO - Carbon Monoxide | PASS | NA | Y
2014 | 778 | 0661005010 | E2 Appalachian Compression LLC - Upper Hill | Opossum Run Rd and Town Hwy 120 | Sarahsville | 43779 |  | Noble | P008 | 1,680 Hp. Waukesha (L7044GSI) natural gas-fired, rich burn, turbocharged, with oxidation catalyst, compressor engine. | 2014-11-06 | C-7(Catalytic Converter): Engine Catalyst; C-8(Catalytic Converter): Engine Catalyst; C-9(Catalytic Converter): Engine Catalyst | E2 Energy Services | 1680 Hp | 0.94 lb/hr | 1221 Hp | 0.62 lb/hr | 10 | CO - Carbon Monoxide | PASS | NA | Y | Method 10 not used. Method 3A and ASTM 6348-03 used
2014 | 782 | 0661005010 | E2 Appalachian Compression LLC - Upper Hill | Opossum Run Rd and Town Hwy 120 | Sarahsville | 43779 |  | Noble | P004 | 1,680 Hp. Waukesha (L7044GSI) natural gas-fired, rich burn, turbocharged, with oxidation catalyst, compressor engine. | 2014-11-10 | C-4(Catalytic Converter): Engine Catalyst | E2 Energy Services | 1680 Hp | 0.94 lb/hr | 1547 Hp | 0.63 lb/hr | 10 | CO - Carbon Monoxide | PASS | NA | Y | Method 10 not used. Method 3a and ASTM 6348-03 used
2014 | 826 | 0656105005 | E2 Appalachian Compression LLC - Reusser | Twp Hwy 68 and Twp Hwy 66 | Woodsfield | 43793 |  | Monroe | P004 | 1680 Hp. natural gas rich burn compressor engine - Waukesha L7044GSI | 2014-12-08 | C-3(Catalytic Converter): Engine #3 Catalyst; C-4(Catalytic Converter): Engine #4 Catalyst; C-5(Catalytic Converter): Engine #5 Catalyst; C-6(Catalytic Converter): Engine #6Catalyst; C-8(Catalytic Converter): Engine #8 Catalyst | E2 Energy Services | 1,680 hp | 0.94 lb/hr | 1,590 hp | 0.65 lb/hr | 6348 03 | CO - Carbon Monoxide | PASS | NA | Y
2014 | 829 | 0656105005 | E2 Appalachian Compression LLC - Reusser | Twp Hwy 68 and Twp Hwy 66 | Woodsfield | 43793 |  | Monroe | P004 | 1680 Hp. natural gas rich burn compressor engine - Waukesha L7044GSI | 2014-12-10 | C-3(Catalytic Converter): Engine #3 Catalyst; C-4(Catalytic Converter): Engine #4 Catalyst; C-5(Catalytic Converter): Engine #5 Catalyst; C-6(Catalytic Converter): Engine #6Catalyst; C-8(Catalytic Converter): Engine #8 Catalyst | E2 Energy Services | 1,680 hp | 0.94 lb/hr | 1,590 hp | 0.65 lb/hr | 6348 03 | CO - Carbon Monoxide | PASS | NA | Y
2014 | 831 | 0656105005 | E2 Appalachian Compression LLC - Reusser | Twp Hwy 68 and Twp Hwy 66 | Woodsfield | 43793 |  | Monroe | P004 | 1680 Hp. natural gas rich burn compressor engine - Waukesha L7044GSI | 2014-12-11 | C-3(Catalytic Converter): Engine #3 Catalyst; C-4(Catalytic Converter): Engine #4 Catalyst; C-5(Catalytic Converter): Engine #5 Catalyst; C-6(Catalytic Converter): Engine #6Catalyst; C-8(Catalytic Converter): Engine #8 Catalyst | E2 Energy Services | 1,680 hp | 0.94 lb/hr | 1,590 hp | 0.65 lb/hr | 6348 03 | CO - Carbon Monoxide | PASS | NA | Y
2014 | 834 | 0630005024 | Gulfport Energy Corporation - Karen 23-9-7 Pad | Oxford Rd | Quaker City | 43773 |  | Guernsey | P002 | One or multiple stationary natural gas-fired spark ignition (SI) internal combustion engines (ICE) with a combined total horsepower (HP) of no more than 1,800 HP for the site. Includes 2007 and later model year engines manufactured after the applicable effective date identified in 40 CFR 60.4230(a)(3) and engines manufactured before the NSPS effective date where compliance with the Part 60 Subpart JJJJ emissions standards for the same size engine can be demonstrated through stack testing. | 2014-08-08 | catalyst | BCMJ Controls, Inc | 118 Hp | 4.0 g/Hp-hr | 52 Hp | 0.69 g/Hp-hr | 10 | CO - Carbon Monoxide | PASS | NA | Y
2014 | 838 | 0634005034 | Lake Compressor Station | County Highway 21 | Freeport | 43973 |  | Harrison | P005 | Compressor Engine #5 - 1980 HP (15.43 MMBtu/hr) Waukesha P9390 - natural gas-fired four-stroke rich burn internal combustion engine equipped with a three-way oxidation catalyst controlling CH2O, CO, NOx, & VOCs by 80, 97, 98.5 & 66 percent respectively | 2014-04-10 | CC005(Catalytic Converter): Compressor Engine #5 - 3-way Catalyst | Air Hygiene International | 1,980 hp | 2.0 g/hp-hr | 1,441 hp | 0.71 g/hp-hr | 10 | CO - Carbon Monoxide | PASS | NA | Y
2014 | 840 | 0656105005 | E2 Appalachian Compression LLC - Reusser | Twp Hwy 68 and Twp Hwy 66 | Woodsfield | 43793 |  | Monroe | P003 | 1680 Hp. natural gas rich burn compressor engine - Waukesha L7044GSI | 2014-12-08 | C-3(Catalytic Converter): Engine #3 Catalyst; C-4(Catalytic Converter): Engine #4 Catalyst; C-5(Catalytic Converter): Engine #5 Catalyst; C-6(Catalytic Converter): Engine #6Catalyst; C-8(Catalytic Converter): Engine #8 Catalyst | E2 Energy Services | 1,680 hp | 0.94 lb/hr | 1,551 hp | 0.74 lb/hr | 6348 03 | CO - Carbon Monoxide | PASS | NA | Y
2014 | 843 | 0656105005 | E2 Appalachian Compression LLC - Reusser | Twp Hwy 68 and Twp Hwy 66 | Woodsfield | 43793 |  | Monroe | P003 | 1680 Hp. natural gas rich burn compressor engine - Waukesha L7044GSI | 2014-12-10 | C-3(Catalytic Converter): Engine #3 Catalyst; C-4(Catalytic Converter): Engine #4 Catalyst; C-5(Catalytic Converter): Engine #5 Catalyst; C-6(Catalytic Converter): Engine #6Catalyst; C-8(Catalytic Converter): Engine #8 Catalyst | E2 Energy Services | 1,680 hp | 0.94 lb/hr | 1,551 hp | 0.74 lb/hr | 6348 03 | CO - Carbon Monoxide | PASS | NA | Y
2014 | 846 | 0656105005 | E2 Appalachian Compression LLC - Reusser | Twp Hwy 68 and Twp Hwy 66 | Woodsfield | 43793 |  | Monroe | P003 | 1680 Hp. natural gas rich burn compressor engine - Waukesha L7044GSI | 2014-12-11 | C-3(Catalytic Converter): Engine #3 Catalyst; C-4(Catalytic Converter): Engine #4 Catalyst; C-5(Catalytic Converter): Engine #5 Catalyst; C-6(Catalytic Converter): Engine #6Catalyst; C-8(Catalytic Converter): Engine #8 Catalyst | E2 Energy Services | 1,680 hp | 0.94 lb/hr | 1,551 hp | 0.74 lb/hr | 6348 03 | CO - Carbon Monoxide | PASS | NA | Y
2014 | 849 | 0210012030 | Blue Racer Midstream LLC - Carroll Co Field Station #1 | Cobbler Rd NE | Carrollton | 44615 |  | Carroll | P001 | 1,340 HP Caterpillar G3516LE 4SLB Compressor Engine #1 with Oxidation Catalyst. Engine model year: 2013. | 2014-09-24 | CC-1(Catalytic Converter): Oxidation Catalyst 1; CC-2(Catalytic Converter): Oxidation Catalyst 2 | Air/ Compliance Consultants | 1380 Hp | 270 ppmvd@15%O2 & 2.0 g/bhp-hr | 1159 Hp or 83.9% | 0.78 ppmvd@15%O2 & 0.0069 g/bhp-hr | 10 | CO - Carbon Monoxide | PASS | NA | Y | Testing at a lower rate than 90% of Maximum was allowed because they were barely able to achieve each of these loads independently of the other engine, without taking the other engine down. 90% of the time the engines operate at 50% or lower and they have records to show that. Utilized M320 with SF6 Tracer as a surrogate for M10 as allowed by JJJJ
2014 | 852 | 0210012002 | Utica Gas Services, LLC-Carrollton Compressor Facility | 2098 Panda Road SE | Carrollton | 44615 |  | Carroll | P013 | 1,775 HP natural gas-fired Caterpillar G3606 engine #10equipped with an oxidation catalyst | 2014-02-10 | Oxid. Cat.(Catalytic Converter): Oxidative Catalyst | Air Hygiene Services | 1775 HP | 270ppmvd@15%O2, 1.18lbs/hr, 2.0g/hp-hr | 1593 HP | 0.79ppmvd@15%O2, 0.02lbs/hr, 0.00g/hp-hr | 10 | CO - Carbon Monoxide | PASS | NA | Y
2014 | 856 | 0210012002 | Utica Gas Services, LLC-Carrollton Compressor Facility | 2098 Panda Road SE | Carrollton | 44615 |  | Carroll | P013 | 1,775 HP natural gas-fired Caterpillar G3606 engine #10equipped with an oxidation catalyst | 2014-02-11 | Oxid. Cat.(Catalytic Converter): Oxidative Catalyst | Air Hygiene Services | 1775 HP | 270ppmvd@15%O2, 1.18lbs/hr, 2.0g/hp-hr | 1593 HP | 0.79ppmvd@15%O2, 0.02lbs/hr, 0.00g/hp-hr | 10 | CO - Carbon Monoxide | PASS | NA | Y
2014 | 859 | 0210012002 | Utica Gas Services, LLC-Carrollton Compressor Facility | 2098 Panda Road SE | Carrollton | 44615 |  | Carroll | P013 | 1,775 HP natural gas-fired Caterpillar G3606 engine #10equipped with an oxidation catalyst | 2014-02-12 | Oxid. Cat.(Catalytic Converter): Oxidative Catalyst | Air Hygiene Services | 1775 HP | 270ppmvd@15%O2, 1.18lbs/hr, 2.0g/hp-hr | 1593 HP | 0.79ppmvd@15%O2, 0.02lbs/hr, 0.00g/hp-hr | 10 | CO - Carbon Monoxide | PASS | NA | Y
2014 | 860 | 0661005010 | E2 Appalachian Compression LLC - Upper Hill | Opossum Run Rd and Town Hwy 120 | Sarahsville | 43779 |  | Noble | P002 | 1,680 Hp. Waukesha (L7044GSI) natural gas-fired, rich burn, turbocharged, with oxidation catalyst, compressor engine. | 2014-11-12 | C-2(Catalytic Converter): Engine Catalyst; C-3(Catalytic Converter): Engine Catalyst | E2 Energy Services | 1680 Hp | 0.94 lb/hr | 1575 Hp | 0.87 lb/hr | 10 | CO - Carbon Monoxide | PASS | NA | Y | Method 10 not used. Method 3a and ASTM 6348-03
2014 | 864 | 0661005010 | E2 Appalachian Compression LLC - Upper Hill | Opossum Run Rd and Town Hwy 120 | Sarahsville | 43779 |  | Noble | P002 | 1,680 Hp. Waukesha (L7044GSI) natural gas-fired, rich burn, turbocharged, with oxidation catalyst, compressor engine. | 2014-11-13 | C-2(Catalytic Converter): Engine Catalyst; C-3(Catalytic Converter): Engine Catalyst | E2 Energy Services | 1680 Hp | 0.94 lb/hr | 1575 Hp | 0.87 lb/hr | 10 | CO - Carbon Monoxide | PASS | NA | Y | Method 10 not used. Method 3a and ASTM 6348-03
2014 | 866 | 0661005010 | E2 Appalachian Compression LLC - Upper Hill | Opossum Run Rd and Town Hwy 120 | Sarahsville | 43779 |  | Noble | P003 | 1,680 Hp. Waukesha (L7044GSI) natural gas-fired, rich burn, turbocharged, with oxidation catalyst, compressor engine. | 2014-11-12 | C-2(Catalytic Converter): Engine Catalyst; C-3(Catalytic Converter): Engine Catalyst | E2 Energy Services | 1680 Hp | 0.94 lb/hr | 1512 Hp | 0.89 lb/hr | 10 | CO - Carbon Monoxide | PASS | NA | Y | Method 10 not used. Method 3a and ASTM 6348-03
2014 | 870 | 0661005010 | E2 Appalachian Compression LLC - Upper Hill | Opossum Run Rd and Town Hwy 120 | Sarahsville | 43779 |  | Noble | P003 | 1,680 Hp. Waukesha (L7044GSI) natural gas-fired, rich burn, turbocharged, with oxidation catalyst, compressor engine. | 2014-11-13 | C-2(Catalytic Converter): Engine Catalyst; C-3(Catalytic Converter): Engine Catalyst | E2 Energy Services | 1680 Hp | 0.94 lb/hr | 1512 Hp | 0.89 lb/hr | 10 | CO - Carbon Monoxide | PASS | NA | Y | Method 10 not used. Method 3a and ASTM 6348-03
2014 | 873 | 0634005043 | Gulfport Energy- BK Stephens | 75501 Tyson Road | Cadiz | 43907 |  | Harrison | P002 | One or multiple stationary natural gas-fired spark ignition (SI) internal combustion engines (ICE) wiht a combined total horsepower (HP) of no more than 1,800 HP for the site. | 2014-07-02 | none | BCMJ Control Inc | 400 Hp | 4.0 g/Hp-hr | 280 Hp | 1.09 g/Hp-hr | 10 | CO - Carbon Monoxide | PASS | NA | Y | 400 Hp Waukesha engine-Serial #-C-17249/1-results above 203 Hp Caterpillar engine-Serial #4FD18737- tested rate: 0.16 g/Hp-hr NOX 0.1 g/Hp-hr CO 0.13 g/Hp-hr VOC allowable rate: 2.0 g/Hp-hr NOX 4.0 g/Hp-hr CO 1.0 g/Hp-hr VOC
2014 | 880 | 0634005054 | Gulfport Energy - Lyons Well Pad | 27650 Friendly Ridge Rd | Tippecanoe | 44699 |  | Harrison | P002 | Two 50-hp Blackmer 942 natural gas-fired engines for compressors. | 2014-08-06 | non selective catalytic reduction | BCMJ Controls, Inc | 380 Hp | 4.0 g/Hp-hr | 296 Hp | 1.11 g/Hp-hr | 10 | CO - Carbon Monoxide | PASS | NA | Y
2014 | 883 | 0656105006 | Eclipse Resources 1 LP - Tippens Pad | 40417 Eddy Ridge Road | Woodsfield | 43793 |  | Monroe | P002 | One or multiple stationary natural gas-fired spark ignition (SI) internal combustion engines (ICE) with a combined total horsepower (HP) of no more than 1,800 HP for the site.* Includes 2007 and later model year engines manufactured after the applicable effective date identified in 40 CFR 60.4230(a)(3) and engines manufactured before the NSPS effective date where compliance with the Part 60 Subpart JJJJ emissions standards for the same size engine can be demonstrated through stack testing. | 2014-06-25 | none | Windrock, Inc | 47 Hp Arrow Model 42 engine | 4.8 g/Hp-hr | 33 Hp | 1.14 g/Hp-hr | 10 | CO - Carbon Monoxide | PASS | NA | Y | Arrow engine E001 serial # 4B081005143 was tested (it may have been removed from site or status not updated in Stars) Cummins Model GRA855 also tested-CO allowable emission rate-4.0 g/hp-hr Maximum Operating Rate-225 Hp Emission Rate- 1.0 g/Hp-hr Tested Operating Rate-173 Hp
2014 | 891 | 0210012030 | Blue Racer Midstream LLC - Carroll Co Field Station #1 | Cobbler Rd NE | Carrollton | 44615 |  | Carroll | P002 | 1,340 HP Caterpillar G3516LE 4SLB Compressor Engine #2 with Oxidation Catalyst. Engine model year: 2013. | 2014-09-24 | CC-1(Catalytic Converter): Oxidation Catalyst 1; CC-2(Catalytic Converter): Oxidation Catalyst 2 | Air/ Compliance Consultants | 1380 Hp | 270 ppmvd@15%O2 & 2.0 g/bhp-hr | 1006 Hp or 72.8% | 1.42 ppmvd@15%O2 & 0.013 g/bhp-hr | 10 | CO - Carbon Monoxide | PASS | NA | Y | Testing at a lower rate than 90% of Maximum was allowed because they were barely able to achieve each of these loads independently of the other engine, without taking the other engine down. 90% of the time the engines operate at 50% or lower and they have records to show that. Utilized M320 with SF6 Tracer as a surrogate for M10 as allowed by JJJJ
2014 | 906 | 0335012004 | Napoleon Biogas, LLC | 12329 County Road P-3 | Napoleon | 43545 |  | Henry | P002 | Jenbacher Engine (1996 hp) | 2014-12-16 | None | KBD Technic | 1966 hp | 2.7 g/bhp-hr | 1912 hp | 1.9 g/bhp-hr | 10 | CO - Carbon Monoxide | PASS | Y | Y
2014 | 908 | 0661005010 | E2 Appalachian Compression LLC - Upper Hill | Opossum Run Rd and Town Hwy 120 | Sarahsville | 43779 |  | Noble | P009 | 1,680 Hp. Waukesha (L7044GSI) natural gas-fired, rich burn, turbocharged, with oxidation catalyst, compressor engine. | 2014-07-15 | C-9(Catalytic Converter): Engine Catalyst | E2 Energy Services | 1,680 Hp | 0.94 lb/hr | 1,545 Hp | 1.96 lbs/hr | 10 | CO - Carbon Monoxide | FAIL | NA | Y
2014 | 912 | 0210012002 | Utica Gas Services, LLC-Carrollton Compressor Facility | 2098 Panda Road SE | Carrollton | 44615 |  | Carroll | P011 | 1,775 HP natural gas-fired Caterpillar G3606 engine #8 equipped with an oxidation catalyst | 2014-02-10 | Oxid. Cat.(Catalytic Converter): Oxidative Catalyst | Air Hygiene Services | 1775 HP | 270ppmvd@15%O2, 1.18lbs/hr, 2.0g/hp-hr | 1620 HP | 10.14ppmvd@15%O2, 0.23lbs/hr, 0.06g/hp-hr | 10 | CO - Carbon Monoxide | PASS | NA | Y
2014 | 915 | 0210012002 | Utica Gas Services, LLC-Carrollton Compressor Facility | 2098 Panda Road SE | Carrollton | 44615 |  | Carroll | P011 | 1,775 HP natural gas-fired Caterpillar G3606 engine #8 equipped with an oxidation catalyst | 2014-02-11 | Oxid. Cat.(Catalytic Converter): Oxidative Catalyst | Air Hygiene Services | 1775 HP | 270ppmvd@15%O2, 1.18lbs/hr, 2.0g/hp-hr | 1620 HP | 10.14ppmvd@15%O2, 0.23lbs/hr, 0.06g/hp-hr | 10 | CO - Carbon Monoxide | PASS | NA | Y
2014 | 918 | 0210012002 | Utica Gas Services, LLC-Carrollton Compressor Facility | 2098 Panda Road SE | Carrollton | 44615 |  | Carroll | P011 | 1,775 HP natural gas-fired Caterpillar G3606 engine #8 equipped with an oxidation catalyst | 2014-02-12 | Oxid. Cat.(Catalytic Converter): Oxidative Catalyst | Air Hygiene Services | 1775 HP | 270ppmvd@15%O2, 1.18lbs/hr, 2.0g/hp-hr | 1620 HP | 10.14ppmvd@15%O2, 0.23lbs/hr, 0.06g/hp-hr | 10 | CO - Carbon Monoxide | PASS | NA | Y
2014 | 926 | 0210012002 | Utica Gas Services, LLC-Carrollton Compressor Facility | 2098 Panda Road SE | Carrollton | 44615 |  | Carroll | P009 | 1,775 HP natural gas-fired Caterpillar G3606 engine #6 equipped with an oxidation catalyst | 2014-02-10 | Oxid. Cat.(Catalytic Converter): Oxidative Catalyst | Air Hygiene Services | 1775 HP | 270ppmvd@15%O2, 1.18lbs/hr, 2.0g/hp-hr | 1623 HP | 10.32ppmvd@15%O2, 0.22lbs/hr, 0.06g/hp-hr | 10 | CO - Carbon Monoxide | PASS | NA | Y
2014 | 929 | 0210012002 | Utica Gas Services, LLC-Carrollton Compressor Facility | 2098 Panda Road SE | Carrollton | 44615 |  | Carroll | P009 | 1,775 HP natural gas-fired Caterpillar G3606 engine #6 equipped with an oxidation catalyst | 2014-02-11 | Oxid. Cat.(Catalytic Converter): Oxidative Catalyst | Air Hygiene Services | 1775 HP | 270ppmvd@15%O2, 1.18lbs/hr, 2.0g/hp-hr | 1623 HP | 10.32ppmvd@15%O2, 0.22lbs/hr, 0.06g/hp-hr | 10 | CO - Carbon Monoxide | PASS | NA | Y
2014 | 931 | 0210012002 | Utica Gas Services, LLC-Carrollton Compressor Facility | 2098 Panda Road SE | Carrollton | 44615 |  | Carroll | P009 | 1,775 HP natural gas-fired Caterpillar G3606 engine #6 equipped with an oxidation catalyst | 2014-02-12 | Oxid. Cat.(Catalytic Converter): Oxidative Catalyst | Air Hygiene Services | 1775 HP | 270ppmvd@15%O2, 1.18lbs/hr, 2.0g/hp-hr | 1623 HP | 10.32ppmvd@15%O2, 0.22lbs/hr, 0.06g/hp-hr | 10 | CO - Carbon Monoxide | PASS | NA | Y
2014 | 988 | 0210012002 | Utica Gas Services, LLC-Carrollton Compressor Facility | 2098 Panda Road SE | Carrollton | 44615 |  | Carroll | P005 | 1,775 HP natural gas-fired Caterpillar G3606 engine #2 equipped with an oxidation catalyst | 2014-02-10 | Oxid. Cat.(Catalytic Converter): Oxidative Catalyst | Air Hygiene Services | 1775 HP | 540ppmvd@15%O2, 1.18lbs/hr, 4.0g/hp-hr | 1666 HP | 11.10ppmvd@15%O2, 0.26lbs/hr, 0.07g/hp-hr | 10 | CO - Carbon Monoxide | PASS | NA | Y
2014 | 991 | 0210012002 | Utica Gas Services, LLC-Carrollton Compressor Facility | 2098 Panda Road SE | Carrollton | 44615 |  | Carroll | P005 | 1,775 HP natural gas-fired Caterpillar G3606 engine #2 equipped with an oxidation catalyst | 2014-02-11 | Oxid. Cat.(Catalytic Converter): Oxidative Catalyst | Air Hygiene Services | 1775 HP | 540ppmvd@15%O2, 1.18lbs/hr, 4.0g/hp-hr | 1666 HP | 11.10ppmvd@15%O2, 0.26lbs/hr, 0.07g/hp-hr | 10 | CO - Carbon Monoxide | PASS | NA | Y
2014 | 995 | 0210012002 | Utica Gas Services, LLC-Carrollton Compressor Facility | 2098 Panda Road SE | Carrollton | 44615 |  | Carroll | P005 | 1,775 HP natural gas-fired Caterpillar G3606 engine #2 equipped with an oxidation catalyst | 2014-02-12 | Oxid. Cat.(Catalytic Converter): Oxidative Catalyst | Air Hygiene Services | 1775 HP | 540ppmvd@15%O2, 1.18lbs/hr, 4.0g/hp-hr | 1666 HP | 11.10ppmvd@15%O2, 0.26lbs/hr, 0.07g/hp-hr | 10 | CO - Carbon Monoxide | PASS | NA | Y
2014 | 1029 | 0210032001 | Chesapeake Exploration LLC - Edie 17-13-6 Pad | Amsterdam Road SW | Leesville | 44639 |  | Carroll | P002 | Natural Gas Engines | 2014-04-07 | Catalyst | Alliance Source Testing | 211HP | 270 ppmvd@15%O2 | 155 HP or 73.5% of Max | 114.4 ppmvd@15%O2 | 10 | CO - Carbon Monoxide | PASS | NA | Y | Engine will require a retest if engine exceeds 10% of the tested rate.
2014 | 1042 | 0210012002 | Utica Gas Services, LLC-Carrollton Compressor Facility | 2098 Panda Road SE | Carrollton | 44615 |  | Carroll | P008 | 1,775 HP natural gas-fired Caterpillar G3606 engine #5 equipped with an oxidation catalyst | 2014-02-10 | Oxid. Cat.(Catalytic Converter): Oxidative Catalyst | Air Hygiene Services | 1775 HP | 270ppmvd@15%O2, 1.18lbs/hr, 2.0g/hp-hr | 1622 HP | 12.66ppmvd@15%O2, .28lbs/hr, 0.08g/hp-hr | 10 | CO - Carbon Monoxide | PASS | NA | Y
2014 | 1046 | 0210012002 | Utica Gas Services, LLC-Carrollton Compressor Facility | 2098 Panda Road SE | Carrollton | 44615 |  | Carroll | P008 | 1,775 HP natural gas-fired Caterpillar G3606 engine #5 equipped with an oxidation catalyst | 2014-02-11 | Oxid. Cat.(Catalytic Converter): Oxidative Catalyst | Air Hygiene Services | 1775 HP | 270ppmvd@15%O2, 1.18lbs/hr, 2.0g/hp-hr | 1622 HP | 12.66ppmvd@15%O2, .28lbs/hr, 0.08g/hp-hr | 10 | CO - Carbon Monoxide | PASS | NA | Y
2014 | 1055 | 0210012002 | Utica Gas Services, LLC-Carrollton Compressor Facility | 2098 Panda Road SE | Carrollton | 44615 |  | Carroll | P008 | 1,775 HP natural gas-fired Caterpillar G3606 engine #5 equipped with an oxidation catalyst | 2014-02-12 | Oxid. Cat.(Catalytic Converter): Oxidative Catalyst | Air Hygiene Services | 1775 HP | 270ppmvd@15%O2, 1.18lbs/hr, 2.0g/hp-hr | 1622 HP | 12.66ppmvd@15%O2, .28lbs/hr, 0.08g/hp-hr | 10 | CO - Carbon Monoxide | PASS | NA | Y
2014 | 1242 | 0210012002 | Utica Gas Services, LLC-Carrollton Compressor Facility | 2098 Panda Road SE | Carrollton | 44615 |  | Carroll | P007 | 1,775 HP natural gas-fired Caterpillar G3606 engine #4 equipped with an oxidation catalyst | 2014-02-10 | Oxid. Cat.(Catalytic Converter): Oxidative Catalyst | Air Hygiene Services | 1775 HP | 270ppmvd@15%O2, 1.18lbs/hr, 2.0g/hp-hr | 1613 HP | 13.38ppmvd@15%O2, 0.30lbs/hr, 0.08g/hp-hr | 10 | CO - Carbon Monoxide | PASS | NA | Y
2014 | 1404 | 0210012002 | Utica Gas Services, LLC-Carrollton Compressor Facility | 2098 Panda Road SE | Carrollton | 44615 |  | Carroll | P007 | 1,775 HP natural gas-fired Caterpillar G3606 engine #4 equipped with an oxidation catalyst | 2014-02-11 | Oxid. Cat.(Catalytic Converter): Oxidative Catalyst | Air Hygiene Services | 1775 HP | 270ppmvd@15%O2, 1.18lbs/hr, 2.0g/hp-hr | 1613 HP | 13.38ppmvd@15%O2, 0.30lbs/hr, 0.08g/hp-hr | 10 | CO - Carbon Monoxide | PASS | NA | Y
2014 | 1407 | 0210012002 | Utica Gas Services, LLC-Carrollton Compressor Facility | 2098 Panda Road SE | Carrollton | 44615 |  | Carroll | P007 | 1,775 HP natural gas-fired Caterpillar G3606 engine #4 equipped with an oxidation catalyst | 2014-02-12 | Oxid. Cat.(Catalytic Converter): Oxidative Catalyst | Air Hygiene Services | 1775 HP | 270ppmvd@15%O2, 1.18lbs/hr, 2.0g/hp-hr | 1613 HP | 13.38ppmvd@15%O2, 0.30lbs/hr, 0.08g/hp-hr | 10 | CO - Carbon Monoxide | PASS | NA | Y
2014 | 1409 | 0210002056 | Chesapeake Exploration LLC - Bryan Shaw 21-13-5 Pad | Perron Rd SE | Harlem Springs | 43903 |  | Carroll | P002 | One or multiple stationary natural gas-fired spark ignition (SI) internal combustion engines (ICE) with a combined total horsepower (HP) of no more than 1,800 HP for the site. Includes 2007 and later model year engines manufactured after the applicable effective date identified in 40 CFR 60.4230(a)(3) and engines manufactured before the NSPS effective date where compliance with the Part 60 Subpart JJJJ emissions standards for the same size engine can be demonstrated through stack testing. | 2014-10-08 | Catalyst | Alliance Source Testing, Inc. | 185 Bhp | CO-270 ppmvd @ 15% O2 | 167 Bhp | 135.9 ppmvd | 10 | CO - Carbon Monoxide | PASS | NA | Y | Engine Tested was site rated at 185 Bhp and had serial # G6X08444
2014 | 1411 | 0210002026 | Chesapeake Exploration LLC - Gartrell 23-13-6 Pad | Ohio 164 | Orange Twp. | 44695 |  | Carroll | P002 | 215 hp CAT G3406NA natural gas engine flash gas compressor equipped with catalyst. | 2014-04-08 | Catalyst | Alliance Source Testing | 211 HP | 270ppmvd@15%O2 | 175 HP or 83% of Max | 148ppmvd@15%O2 | 10 | CO - Carbon Monoxide | PASS | NA | Y | If engine exceeds 10% of the tested rate the engine will require a retest.
2014 | 1412 | 0285000366 | East Ohio Gas - Chippewa Station | 17045 Galehouse Road | Doylestown | 44230 |  | Wayne | B010 | 2,370 hp 4SLB SI ICE; CAT G3608 | 2014-06-02 | Engine 5 Converter(Catalytic Converter): Engine #5; Cat B010(Catalytic Converter): Catalytic Converter for B010, engine #6; Catalytic(Catalytic Converter): Engine 7 Catalytic converter | Air/Compliance Consultants, Inc. | 2370 Hp | 540 ppm @ 15% O2 or 2.0 g/bhp-hr 93%DE | 2315 Hp | 15.87 ppm @ 15% O2 or 0.12 g/bhp-hr 93.5%DE | 10 | CO - Carbon Monoxide | PASS | NA | Y | B009-2.8 Catalyst Pressure and 853 degF Catalyst temp, B010-2.16 Catalyst Pressure and 908 degF Catalyst temp, B014-1.0 Catalyst Pressure and 851 degF Catalyst Temperature
2014 | 1423 | 0285000366 | East Ohio Gas - Chippewa Station | 17045 Galehouse Road | Doylestown | 44230 |  | Wayne | B010 | 2,370 hp 4SLB SI ICE; CAT G3608 | 2014-06-03 | Engine 5 Converter(Catalytic Converter): Engine #5; Cat B010(Catalytic Converter): Catalytic Converter for B010, engine #6; Catalytic(Catalytic Converter): Engine 7 Catalytic converter | Air/Compliance Consultants, Inc. | 2370 Hp | 540 ppm @ 15% O2 or 2.0 g/bhp-hr 93%DE | 2315 Hp | 15.87 ppm @ 15% O2 or 0.12 g/bhp-hr 93.5%DE | 10 | CO - Carbon Monoxide | PASS | NA | Y | B009-2.8 Catalyst Pressure and 853 degF Catalyst temp, B010-2.16 Catalyst Pressure and 908 degF Catalyst temp, B014-1.0 Catalyst Pressure and 851 degF Catalyst Temperature
2014 | 1425 | 0634005048 | Gulfport Energy- Boy Scout Well Pad | 79900 Adams Rd | Tippecanoe | 44699 |  | Harrison | P002 | One 60 hp Waukesha 310 and one 64 hp HEC 3491-OPV natural gas engines for compressors | 2014-07-02 | none | BCMJ Controls, Inc | 400 Hp | 4.0 g/Hp-hr Catterpillar | 217 Hp | 2.59 g/Hp-hr | 10 | CO - Carbon Monoxide | PASS | NA | Y | 118 hp Cummins engine(same allowable rates as above) 0.42 g/Hp-hr CO 145 Hp Caterpillar engine (one hour run only-same allowable rates as above) 1.16 g/Hp-hr CO
2014 | 1437 | 0210002039 | Kilgore Compressor Station-Utica Gas Services, LLC | Pontiff Rd | Kilgore | 43988 |  | Carroll | P001 | 1,775 hp NG-fired 4SLB Stationary ICE equipped w/catalyst Caterpillar G3606 Serial Number: 4ZS01713 | 2014-01-16 | CC001(Catalytic Converter): Compressor Engine #1 - Oxidation Catalyst; CC002(Catalytic Converter): Compressor Engine #2 - Oxidation Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - Oxidation Catalyst; CC004(Catalytic Converter): Compressor Eng | Alliance Source Testing, Inc. | 1775 HP | NSPS 2.0g/hp-hr & 270 ppm@ 15%O2, TV 1.18lbs/hr | 1722 HP | NSPS .02g/hp-hr & 3.0 ppm@ 15%O2, TV 0.08lbs/hr | 10 | CO - Carbon Monoxide | PASS | NA | Y | The report was accepted as verification of compliance by the OEPA. However a few instances onsite were witnessed and variances were allowed to the testers for only accepting two runs as verification of compliance for P005 (NOx) and P009 (CO). Many issues could be attributed to the cold weather, however are preventable, and all efforts to prevent these issues from happening in the future will, and have been, taken into account for future test acceptance.
2014 | 1629 | 0125102034 | Dominion - Groveport Compressor Station | 5509 Berger Road | Groveport | 43125 |  | Franklin | B003 | 3200 HP Engine-spark ignition, 2-stroke, lean burn | 2014-09-09 | None | Dominion Transmission, Inc. | 3200 HP | 18.33 lbs CO/hr | 2988.7 HP | 16.28 lbs CO/hr | 10 | CO - Carbon Monoxide | PASS | NA | Y | ITT Methods were approved by staff that no longer works at Ohio EPA and did not call attention to it.
2014 | 1631 | 0125102034 | Dominion - Groveport Compressor Station | 5509 Berger Road | Groveport | 43125 |  | Franklin | B003 | 3200 HP Engine-spark ignition, 2-stroke, lean burn | 2014-09-10 | None | Dominion Transmission, Inc. | 3200 HP | 18.33 lbs CO/hr | 2988.7 HP | 16.28 lbs CO/hr | 10 | CO - Carbon Monoxide | PASS | NA | Y | ITT Methods were approved by staff that no longer works at Ohio EPA and did not call attention to it.
2014 | 1635 | 0125102034 | Dominion - Groveport Compressor Station | 5509 Berger Road | Groveport | 43125 |  | Franklin | B002 | 4200 HP Engine-spark ignition, 2-stroke, lean burn | 2014-09-09 | None | Dominion Transmission, Inc. | 4200 HP | 25.93 lbs CO/hr | 3919 HP | 16.55 lbs CO/hr | 10 | CO - Carbon Monoxide | PASS | NA | Y | ITT Methods were approved by staff that no longer works at Ohio EPA and did not call attention to it.
2014 | 1636 | 0125102034 | Dominion - Groveport Compressor Station | 5509 Berger Road | Groveport | 43125 |  | Franklin | B002 | 4200 HP Engine-spark ignition, 2-stroke, lean burn | 2014-09-10 | None | Dominion Transmission, Inc. | 4200 HP | 25.93 lbs CO/hr | 3919 HP | 16.55 lbs CO/hr | 10 | CO - Carbon Monoxide | PASS | NA | Y | ITT Methods were approved by staff that no longer works at Ohio EPA and did not call attention to it.
2014 | 1639 | 0215050202 | BRINKER COMPRESSOR STATION | 5213 Leetonia Rd | Leetonia | 44431 |  | Columbiana | B001 | Ingersoll-Rand 38 KVG, serial no. 83NL844, 4-stroke rich burn, natural gas fired reciprocating internal combustion engine (RICE) having a maximum capacity of 10.3 mmBTU/hr (880 BHP). Compressor no.15501. | 2014-01-31 | CAT1(Catalytic Converter): COMPR #15501 CATLAYTIC CONVERTER; CAT2(Catalytic Converter): COMPR 315502 CATALYTIC CONVERTER; CAT3(Catalytic Converter): COMPR #15503 CATALYTIC CONVERTER | Alliance Source Testing, Inc. | 880 Hp | 270 ppmvd @ 15% O2 | 815 Hp | 17.4 ppmvd @ 15% O2 | 10 | CO - Carbon Monoxide | PASS | NA | Y | B001 Tested on 1/31/14 because of span selection error and B002/B003 tested on 12/2/13.
2014 | 1642 | 0125102034 | Dominion - Groveport Compressor Station | 5509 Berger Road | Groveport | 43125 |  | Franklin | B001 | 4200 HP Engine-spark ignition, 2-stroke, lean burn | 2014-09-09 | None | Dominion Transmission, Inc. | 4200 HP | 25.93 lbs CO/hr | 3931 HP | 18.49 lbs CO/hr | 10 | CO - Carbon Monoxide | PASS | NA | Y | ITT Methods were approved by staff that no longer works at Ohio EPA and did not call attention to it.
2014 | 1647 | 0125102034 | Dominion - Groveport Compressor Station | 5509 Berger Road | Groveport | 43125 |  | Franklin | B001 | 4200 HP Engine-spark ignition, 2-stroke, lean burn | 2014-09-10 | None | Dominion Transmission, Inc. | 4200 HP | 25.93 lbs CO/hr | 3931 HP | 18.49 lbs CO/hr | 10 | CO - Carbon Monoxide | PASS | NA | Y | ITT Methods were approved by staff that no longer works at Ohio EPA and did not call attention to it.
2014 | 1650 | 0335012004 | Napoleon Biogas, LLC | 12329 County Road P-3 | Napoleon | 43545 |  | Henry | P001 | Jenbacher Engine (1996 hp) | 2014-12-17 | None | KBD Technic | 1966 hp | 2.7 g/bhp-hr | 1912 hp | 2.0 g/bhp-hr | 10 | CO - Carbon Monoxide | PASS | Y | Y
2014 | 1665 | 0250000911 | East Ohio Gas Company - Austintown | 9686 NEW ROAD | Austintown Twp. | 44451 | 9708 | Mahoning | B002 | Natural gas fired reciprocating internal combustion engine rated at 1265 HP (9.55 mmBtu/hr)-Caterpillar Model G3516LE, 4 stroke lean burn (4SLB) spark ignition (SI) internal combustion engine (ICE) with a Miratech catalytic converter; complying with emission limitations in 40 CFR 63, Subpart ZZZZ Table 2d #9; and installed before 6/12/06. | 2014-04-15 | Oxidative Catalyst 1(Other): B001 Catalytic Oxidizer; Oxidative Catalyst 2(Other): B002 Catalytic oxidizer | Environmental Quality Management | 1,265 Hp | 47 ppm @ 15% O2 and 93% destruction efficiency | 738 or 58% | 2.15 ppm @ 15% O2 and 99% DE | 10 | CO - Carbon Monoxide | PASS | NA | Y
2014 | 1682 | 0215050202 | BRINKER COMPRESSOR STATION | 5213 Leetonia Rd | Leetonia | 44431 |  | Columbiana | B002 | Ingersoll-Rand 38 KVG, serial no. 83NL845, 4-stroke rich burn, natural gas fired reciprocating internal combustion engine (RICE) having a maximum capacity of 10.3 mmBTU/hr (880 BHP). Compressor no.15502. | 2014-01-31 | CAT1(Catalytic Converter): COMPR #15501 CATLAYTIC CONVERTER; CAT2(Catalytic Converter): COMPR 315502 CATALYTIC CONVERTER; CAT3(Catalytic Converter): COMPR #15503 CATALYTIC CONVERTER | Alliance Source Testing, Inc. | 880 Hp | 270 ppmvd @ 15% O2 | 833 Hp | 2.3 ppmvd @ 15% O2 | 10 | CO - Carbon Monoxide | PASS | NA | Y | B001 Tested on 1/31/14 because of span selection error and B002/B003 tested on 12/2/13.
2014 | 1735 | 0250000911 | East Ohio Gas Company - Austintown | 9686 NEW ROAD | Austintown Twp. | 44451 | 9708 | Mahoning | B001 | Natural gas fired reciprocating internal combustion engine rated at 1265 HP (9.55 mmBtu/hr)-Caterpillar Model G3516LE, 4 stroke lean burn (4SLB) spark ignition (SI) internal combustion engine (ICE) with a Miratech catalytic converter; complying with emission limitations in 40 CFR 63, Subpart ZZZZ Table 2d #9; and installed before 6/12/06. | 2014-04-15 | Oxidative Catalyst 1(Other): B001 Catalytic Oxidizer; Oxidative Catalyst 2(Other): B002 Catalytic oxidizer | Environmental Quality Management | 1,265 Hp | 47 ppm @ 15% O2 and 93% destruction efficiency | 793 or 62% | 2.99ppm @ 15% O2 and 98% DE | 10 | CO - Carbon Monoxide | PASS | NA | Y
2014 | 1738 | 0634005058 | Atlas Noble, LLC - Cramblett Well Pad | Bowers Road | North Twp. | 43988 |  | Harrison | P002 | 415 Hp Caterpillar G379 TA natural gas fired recovery compressor engine equipped with a catalytic converter. (non JJJJ engine). 68 Hp Caterpillar VRG330 natural gas fired vapor recovery unit equipped with a catalytic convertor. | 2014-03-04 | none | Air Compliance Consultants | 415 hp | 540 ppm | 204 hp | 21 ppm | 10 | CO - Carbon Monoxide | PASS | NA | Y
2014 | 1741 | 0210002047 | Chesapeake Exploration LLC - Hutchison 33-15-5 Pad | Moccasin Road NE | Augusta Twp. | 44615 |  | Carroll | P002 | Natural Gas Engines | 2014-07-01 | Catalyst | Alliance Source Testing, Inc. | 211 Hp | 270ppmvd@15%O2 | 150 or 71% of Max | 229.7ppmvd@15%O2 | 10 | CO - Carbon Monoxide | PASS | NA | Y | Unit not tested at 90% of Max and was very close to its limit on this occasion.
2014 | 1744 | 0278002033 | Halcon Operating Co Inc - Avalon Farms Production Facility | 3393 Warren Sharon Rd | Vienna Twp.. | 44473 |  | Trumbull | P002 | Natural Gas Engines | 2014-04-08 | CTRL-3(Other): NSCR | Air Compliance/Consultants | 400 HP | 270 ppmvd @ 15% O2 and 2.0 g/bhp-hr | 260 Hp | 23.71 ppmvd and 0.23 g | 10 | CO - Carbon Monoxide | PASS | Y | Y
2014 | 1747 | 0210012002 | Utica Gas Services, LLC-Carrollton Compressor Facility | 2098 Panda Road SE | Carrollton | 44615 |  | Carroll | P004 | 1,775 HP natural gas-fired Caterpillar G3606 engine #1 equipped with an oxidation catalyst. | 2014-02-10 | Oxid. Cat.(Catalytic Converter): Oxidative Catalyst | Air Hygiene Services | 1775 HP | 540ppmvd@15%O2, 1.18lbs/hr, 4.0g/hp-hr | 1684 HP | 26.91ppmvd@15%O2, 0.66lbs/hr, 0.18g/hp-hr | 10 | CO - Carbon Monoxide | PASS | NA | Y
2014 | 1749 | 0210012002 | Utica Gas Services, LLC-Carrollton Compressor Facility | 2098 Panda Road SE | Carrollton | 44615 |  | Carroll | P004 | 1,775 HP natural gas-fired Caterpillar G3606 engine #1 equipped with an oxidation catalyst. | 2014-02-11 | Oxid. Cat.(Catalytic Converter): Oxidative Catalyst | Air Hygiene Services | 1775 HP | 540ppmvd@15%O2, 1.18lbs/hr, 4.0g/hp-hr | 1684 HP | 26.91ppmvd@15%O2, 0.66lbs/hr, 0.18g/hp-hr | 10 | CO - Carbon Monoxide | PASS | NA | Y
2014 | 1752 | 0210012002 | Utica Gas Services, LLC-Carrollton Compressor Facility | 2098 Panda Road SE | Carrollton | 44615 |  | Carroll | P004 | 1,775 HP natural gas-fired Caterpillar G3606 engine #1 equipped with an oxidation catalyst. | 2014-02-12 | Oxid. Cat.(Catalytic Converter): Oxidative Catalyst | Air Hygiene Services | 1775 HP | 540ppmvd@15%O2, 1.18lbs/hr, 4.0g/hp-hr | 1684 HP | 26.91ppmvd@15%O2, 0.66lbs/hr, 0.18g/hp-hr | 10 | CO - Carbon Monoxide | PASS | NA | Y
2014 | 1755 | 0634005045 | Gulfport Energy- Clay Well Pad | 31501 Morrison Road | Freeport | 43973 |  | Harrison | P002 | One or multiple stationary natural gas-fired spark ignition (SI) internal combustion engines (ICE) with a combined total horsepower (HP) of no more than 1,800 HP for the site. Includes 2007 and later model year engines manufactured after the applicable effective date identified in 40 CFR 60.4230(a)(3) and engines manufactured before the NSPS effective date where compliance with the Part 60 Subpart JJJJ emissions standards for the same size engine can be demonstrated through stack testing. | 2014-07-08 | none-carbureted air fuel mix to control emissions | BCMJ Control, Inc. | 145 Hp | 4.0 g/Hp-hr | 53 Hp | 3.86 h/Hp-hr | 10 | CO - Carbon Monoxide | PASS | NA | Y | (second engine) Serial # 9TG00298 4.0 g/Hp-hr 630 Hp 0.001 g/Hp-hr 350 Hp Method 320
2014 | 1759 | 0210002029 | Chesapeake Exploration LLC - Colescott 11-12-5 Pad | Branch Rd | Kilgore | 44615 |  | Carroll | P002 | 215 hp CAT G3406NA flash gas compressor using natural gas engines and equipped with a catalyst. | 2014-04-08 | Catalyst | Alliance Source Testing | 211 HP | 270 ppmvd@15%O2 | 165 HP or 78% of Max | 39.1 ppmvd@15%O2 | 10 | CO - Carbon Monoxide | PASS | NA | Y | Engine will have to retest if the engine exceed 10% operation of the tested rate.
2014 | 1761 | 0250002027 | Poland-CLL Production Facility | East of Cowden Rd and Moore Rd | Poland Twp. | 44436 |  | Mahoning | P002 | 1,340-hp Caterpillar G3516LE natural gas-fired compressor engine with oxidation catalyst, manufactured on 5/31/2007 | 2014-07-01 | Catalytic Co(Catalytic Converter): Catalytic Converter | Alliance Source Testing, Inc. | 1340 Hp | 270 ppmvd@15%O2 and 2.0g/bhp-hr | 590 Hp or 44% | 4.18 ppmvd@15%O2 and 0.04g/bhp-hr | 10 | CO - Carbon Monoxide | PASS | NA | Y | NSPS JJJJ Required test The facility was aware of the fact that they were well below the 90% threshold and are aware that they will have to test again if they run at a rate of 10% greater than the tested.
2014 | 1765 | 0285000388 | East Ohio Gas Company - Paint | STATE RTE 250 | Wooster | 44624 |  | Wayne | B002 | Natural gas fired Internal Combustion Engine with max input capacity of 11.9 MMBtu/hr - Caterpillar G3516TALE with 1340 HP, 4-stroke, selective catalytic reduction (SCR) | 2014-07-29 | Three way Catalyst; CatOx(Catalytic Converter): Catalytic oxidizer for Engine 2 | Air/Compliance Consultants, Inc. | 1340 HP | 540 ppm @ 15% O2 and 4.0 g/hp-hr | 1207 HP or 90.1 | 4.22 ppm @ 15% O2 and 0.036 g/hp-hr | 10 | CO - Carbon Monoxide | PASS | NA | Y
2014 | 1769 | 0285000366 | East Ohio Gas - Chippewa Station | 17045 Galehouse Road | Doylestown | 44230 |  | Wayne | B014 | 2,370 hp 4SLB SI ICE: CAT 3608 w/catalyst | 2014-06-02 | Engine 5 Converter(Catalytic Converter): Engine #5; Cat B010(Catalytic Converter): Catalytic Converter for B010, engine #6; Catalytic(Catalytic Converter): Engine 7 Catalytic converter | Air/Compliance Consultants, Inc. | 2370 Hp | 270 ppm @ 15% O2 or 2.0 g/bhp-hr | 2362 Hp | 4.59 ppm @ 15% O2 or 0.035g/bhp-hr | 10 | CO - Carbon Monoxide | PASS | NA | Y | B009-2.8 Catalyst Pressure and 853 degF Catalyst temp, B010-2.16 Catalyst Pressure and 908 degF Catalyst temp, B014-1.0 Catalyst Pressure and 851 degF Catalyst Temperature
2014 | 1772 | 0285000366 | East Ohio Gas - Chippewa Station | 17045 Galehouse Road | Doylestown | 44230 |  | Wayne | B014 | 2,370 hp 4SLB SI ICE: CAT 3608 w/catalyst | 2014-06-03 | Engine 5 Converter(Catalytic Converter): Engine #5; Cat B010(Catalytic Converter): Catalytic Converter for B010, engine #6; Catalytic(Catalytic Converter): Engine 7 Catalytic converter | Air/Compliance Consultants, Inc. | 2370 Hp | 270 ppm @ 15% O2 or 2.0 g/bhp-hr | 2362 Hp | 4.59 ppm @ 15% O2 or 0.035g/bhp-hr | 10 | CO - Carbon Monoxide | PASS | NA | Y | B009-2.8 Catalyst Pressure and 853 degF Catalyst temp, B010-2.16 Catalyst Pressure and 908 degF Catalyst temp, B014-1.0 Catalyst Pressure and 851 degF Catalyst Temperature
2014 | 1775 | 0215050202 | BRINKER COMPRESSOR STATION | 5213 Leetonia Rd | Leetonia | 44431 |  | Columbiana | B003 | Ingersoll-Rand 48 KVSFT 563, serial no. 48FT563, 4-stroke lean burn, natural gas fired reciprocating internal combustion engine (RICE) having a maximum capacity of 13.7 mmBTU/hr (1,320 BHP). Compressor no.15503. | 2014-01-31 | CAT1(Catalytic Converter): COMPR #15501 CATLAYTIC CONVERTER; CAT2(Catalytic Converter): COMPR 315502 CATALYTIC CONVERTER; CAT3(Catalytic Converter): COMPR #15503 CATALYTIC CONVERTER | Alliance Source Testing, Inc. | 1320 Hp | 47 ppmvd @ 15% O2 | 1251 Hp | 4.9 ppmvd @ 15% O2 | 10 | CO - Carbon Monoxide | PASS | NA | Y | B001 Tested on 1/31/14 because of span selection error and B002/B003 tested on 12/2/13.
2014 | 1777 | 0215112002 | Chesapeake Exploration LLC - Pitts 22-14-4 Pad | Nature Rd SE (Carroll Rd) | Summitville | 43962 |  | Columbiana | P002 | Natural Gas Engines | 2014-12-22 | Catalyst | Alliance Source Testing | 211 HP MAX 195 Site rate HP | CO-270 ppmvd @ 15% O2 | 193 Hp | 46.8 ppmvd | 10 | CO - Carbon Monoxide | PASS | NA | Y
2014 | 1780 | 0210012045 | Chesapeake Exploration LLC - Stanton 29-13-5 Pad | Canyon Road SE | Carrollton | 44615 |  | Carroll | P002 | One or multiple stationary natural gas-fired spark ignition (SI) internal combustion engines (ICE) with a combined total horsepower (HP) of no more than 1,800 HP for the site.* Includes 2007 and later model year engines manufactured after the applicable effective date identified in 40 CFR 60.4230(a)(3); and engines manufactured before the effective date of the NSPS, where compliance with the Part 60 Subpart JJJJ emissions standards for the same size engine can be met by retrofitting the engine with a control device and demonstrated through stack testing. | 2014-12-22 | Catalyst | Alliance Source Testing | 211 HP MAX 195 Site rate HP | CO-270 ppmvd @ 15% O2 | 175 Hp | 47.5 ppmvd @ 15% O2 | 10 | CO - Carbon Monoxide | PASS | NA | Y
2014 | 1783 | 0857103154 | PINNACLE GAS PRODUCERS LLC | 4220 PINNACLE RD | MORAINE | 45439 |  | Montgomery | B001 | 12 MMBtu/hour (1,626 bhp) pipeline quality gas/natural gas-fired compressor engine | 2014-05-20 | N/A | DTE ENERGY | 1200 RPM | 9.85 LB/HR CO | 856 RPM | 5.63 LB/HR CO | 10 | CO - Carbon Monoxide | PASS | NA | Y | Fuel BTU Content 978. Average gas process rate for the plant on this date 3.54MMSCF/day.
2014 | 1787 | 0210012022 | Chesapeake Exploration LLC - Krichbaum 2-14-5 Pad | County Highway 21 | Carrollton | 44615 |  | Carroll | P002 | Natural Gas Engines | 2014-03-04 | Catalyst | Alliance Source Testing, Inc. | 211 hp | 270 ppmvd @ 15% O2 | 168 hp | 51.3 ppmvd @ 15% O2 | 10 | CO - Carbon Monoxide | PASS | NA | Y
2014 | 1789 | 0210012038 | Chesapeake Exploration LLC - GF Farms 25-14-5 Pad | Steubenville Rd SE | Carrollton | 44615 |  | Carroll | P002 | Natural Gas Engines | 2014-11-12 | Catalyst | Alliance Source Testing | 211 Bhp | CO-270 ppmvd @ 15% O2 | 167 bhp/96.0% | 54.5 ppmvd | 10 | CO - Carbon Monoxide | PASS | NA | Y
2014 | 1803 | 0210012002 | Utica Gas Services, LLC-Carrollton Compressor Facility | 2098 Panda Road SE | Carrollton | 44615 |  | Carroll | P006 | 1,775 HP natural gas-fired Caterpillar G3606 engine #3 equipped with an oxidation catalyst | 2014-02-10 | Oxid. Cat.(Catalytic Converter): Oxidative Catalyst | Air Hygiene Services | 1775 HP | 270ppmvd@15%O2, 1.18lbs/hr, 2.0g/hp-hr | 1617 HP | 8.07ppmvd@15%O2, 1.18lbs/hr, 0.05g/hp-hr | 10 | CO - Carbon Monoxide | PASS | NA | Y
2014 | 1807 | 0210012002 | Utica Gas Services, LLC-Carrollton Compressor Facility | 2098 Panda Road SE | Carrollton | 44615 |  | Carroll | P006 | 1,775 HP natural gas-fired Caterpillar G3606 engine #3 equipped with an oxidation catalyst | 2014-02-11 | Oxid. Cat.(Catalytic Converter): Oxidative Catalyst | Air Hygiene Services | 1775 HP | 270ppmvd@15%O2, 1.18lbs/hr, 2.0g/hp-hr | 1617 HP | 8.07ppmvd@15%O2, 1.18lbs/hr, 0.05g/hp-hr | 10 | CO - Carbon Monoxide | PASS | NA | Y
2014 | 1811 | 0210012002 | Utica Gas Services, LLC-Carrollton Compressor Facility | 2098 Panda Road SE | Carrollton | 44615 |  | Carroll | P006 | 1,775 HP natural gas-fired Caterpillar G3606 engine #3 equipped with an oxidation catalyst | 2014-02-12 | Oxid. Cat.(Catalytic Converter): Oxidative Catalyst | Air Hygiene Services | 1775 HP | 270ppmvd@15%O2, 1.18lbs/hr, 2.0g/hp-hr | 1617 HP | 8.07ppmvd@15%O2, 1.18lbs/hr, 0.05g/hp-hr | 10 | CO - Carbon Monoxide | PASS | NA | Y
2014 | 1839 | 0634005037 | Chesapeake Exploration LLC - Gotshall 14-12-5 Pad | Burrier Rd | Scio | 43986 |  | Harrison | P002 | Flash gas compressor equipped with catalyst, 211 hp, CAT G3306TA (Spark Ignition Internal Combustion Engine, P002) | 2014-04-09 | none | Alliance Source Testing | 211 hp | 540 ppm | 175 hp | 85.7 ppm | 10 | CO - Carbon Monoxide | PASS | NA | Y
2014 | 1842 | 0210002057 | Chesapeake Exploration LLC - Javersak 28-12-5 Pad | Saber Road | Kilgore | 43903 |  | Carroll | P002 | One or multiple stationary natural gas-fired spark ignition (SI) internal combustion engines (ICE) with a combined total horsepower (HP) of no more than 1,800 HP for the site.* Includes 2007 and later model year engines manufactured after the applicable effective date identified in 40 CFR 60.4230(a)(3); and engines manufactured before the effective date of the NSPS, where compliance with the Part 60 Subpart JJJJ emissions standards for the same size engine can be met by retrofitting the engine with a control device and demonstrated through stack testing. | 2014-11-13 | Catalyst | Alliance Source Testing | 174 Site Rate 211 Max | 270 ppmvd @ 15% O2 | 167 of Site Rate 96% | 86.4 ppmvd @ 15%O2 | 10 | CO - Carbon Monoxide | PASS | NA | Y
2014 | 1885 | 0210012002 | Utica Gas Services, LLC-Carrollton Compressor Facility | 2098 Panda Road SE | Carrollton | 44615 |  | Carroll | P010 | 1,775 HP natural gas-fired Caterpillar G3606 engine #7 equipped with an oxidation catalyst | 2014-02-10 | Oxid. Cat.(Catalytic Converter): Oxidative Catalyst | Air Hygiene Services | 1775 HP | 270ppmvd@15%O2, 1.18lbs/hr, 2.0g/hp-hr | 1615 HP | 9.68ppmvd@15%O2, 0.21lbs/hr, 0.06g/hp-hr | 10 | CO - Carbon Monoxide | PASS | NA | Y
2014 | 1888 | 0210012002 | Utica Gas Services, LLC-Carrollton Compressor Facility | 2098 Panda Road SE | Carrollton | 44615 |  | Carroll | P010 | 1,775 HP natural gas-fired Caterpillar G3606 engine #7 equipped with an oxidation catalyst | 2014-02-11 | Oxid. Cat.(Catalytic Converter): Oxidative Catalyst | Air Hygiene Services | 1775 HP | 270ppmvd@15%O2, 1.18lbs/hr, 2.0g/hp-hr | 1615 HP | 9.68ppmvd@15%O2, 0.21lbs/hr, 0.06g/hp-hr | 10 | CO - Carbon Monoxide | PASS | NA | Y
2014 | 1891 | 0210012002 | Utica Gas Services, LLC-Carrollton Compressor Facility | 2098 Panda Road SE | Carrollton | 44615 |  | Carroll | P010 | 1,775 HP natural gas-fired Caterpillar G3606 engine #7 equipped with an oxidation catalyst | 2014-02-12 | Oxid. Cat.(Catalytic Converter): Oxidative Catalyst | Air Hygiene Services | 1775 HP | 270ppmvd@15%O2, 1.18lbs/hr, 2.0g/hp-hr | 1615 HP | 9.68ppmvd@15%O2, 0.21lbs/hr, 0.06g/hp-hr | 10 | CO - Carbon Monoxide | PASS | NA | Y
2014 | 1893 | 0210012002 | Utica Gas Services, LLC-Carrollton Compressor Facility | 2098 Panda Road SE | Carrollton | 44615 |  | Carroll | P012 | 1,775 HP natural gas-fired Caterpillar G3606 engine #9 equipped with an oxidation catalyst | 2014-02-10 | Oxid. Cat.(Catalytic Converter): Oxidative Catalyst | Air Hygiene Services | 1775 HP | 270ppmvd@15%O2, 1.18lbs/hr, 2.0g/hp-hr | 1643 HP | 9.77ppmvd@15%O2, 0.23lbs/hr, 0.06g/hp-hr | 10 | CO - Carbon Monoxide | PASS | NA | Y
2014 | 1898 | 0210012002 | Utica Gas Services, LLC-Carrollton Compressor Facility | 2098 Panda Road SE | Carrollton | 44615 |  | Carroll | P012 | 1,775 HP natural gas-fired Caterpillar G3606 engine #9 equipped with an oxidation catalyst | 2014-02-11 | Oxid. Cat.(Catalytic Converter): Oxidative Catalyst | Air Hygiene Services | 1775 HP | 270ppmvd@15%O2, 1.18lbs/hr, 2.0g/hp-hr | 1643 HP | 9.77ppmvd@15%O2, 0.23lbs/hr, 0.06g/hp-hr | 10 | CO - Carbon Monoxide | PASS | NA | Y
2014 | 1899 | 0210012002 | Utica Gas Services, LLC-Carrollton Compressor Facility | 2098 Panda Road SE | Carrollton | 44615 |  | Carroll | P012 | 1,775 HP natural gas-fired Caterpillar G3606 engine #9 equipped with an oxidation catalyst | 2014-02-12 | Oxid. Cat.(Catalytic Converter): Oxidative Catalyst | Air Hygiene Services | 1775 HP | 270ppmvd@15%O2, 1.18lbs/hr, 2.0g/hp-hr | 1643 HP | 9.77ppmvd@15%O2, 0.23lbs/hr, 0.06g/hp-hr | 10 | CO - Carbon Monoxide | PASS | NA | Y
2014 | 1931 | 0285000366 | East Ohio Gas - Chippewa Station | 17045 Galehouse Road | Doylestown | 44230 |  | Wayne | B009 | 2,370 hp SI ICE pipeline compressor w/catalyst: CAT G3608-LE-TA | 2014-06-02 | Engine 5 Converter(Catalytic Converter): Engine #5; Cat B010(Catalytic Converter): Catalytic Converter for B010, engine #6; Catalytic(Catalytic Converter): Engine 7 Catalytic converter | Air/Compliance Consultants, Inc. | 2370 Hp | 93% Destruction Efficiency | 2343 Hp | 97.3% Destruction | 10 | CO - Carbon Monoxide | PASS | NA | Y | B009-2.8 Catalyst Pressure and 853 degF Catalyst temp, B010-2.16 Catalyst Pressure and 908 degF Catalyst temp, B014-1.0 Catalyst Pressure and 851 degF Catalyst Temperature
2014 | 1933 | 0285000366 | East Ohio Gas - Chippewa Station | 17045 Galehouse Road | Doylestown | 44230 |  | Wayne | B009 | 2,370 hp SI ICE pipeline compressor w/catalyst: CAT G3608-LE-TA | 2014-06-03 | Engine 5 Converter(Catalytic Converter): Engine #5; Cat B010(Catalytic Converter): Catalytic Converter for B010, engine #6; Catalytic(Catalytic Converter): Engine 7 Catalytic converter | Air/Compliance Consultants, Inc. | 2370 Hp | 93% Destruction Efficiency | 2343 Hp | 97.3% Destruction | 10 | CO - Carbon Monoxide | PASS | NA | Y | B009-2.8 Catalyst Pressure and 853 degF Catalyst temp, B010-2.16 Catalyst Pressure and 908 degF Catalyst temp, B014-1.0 Catalyst Pressure and 851 degF Catalyst Temperature
2014 | 1935 | 0210002039 | Kilgore Compressor Station-Utica Gas Services, LLC | Pontiff Rd | Kilgore | 43988 |  | Carroll | P001 | 1,775 hp NG-fired 4SLB Stationary ICE equipped w/catalyst Caterpillar G3606 Serial Number: 4ZS01713 | 2014-01-14 | CC001(Catalytic Converter): Compressor Engine #1 - Oxidation Catalyst; CC002(Catalytic Converter): Compressor Engine #2 - Oxidation Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - Oxidation Catalyst; CC004(Catalytic Converter): Compressor Eng | Alliance Source Testing, Inc. | 1775 HP | NSPS 2.0g/hp-hr & 270 ppm@ 15%O2, TV 1.18lbs/hr | 1722 HP | NSPS .02g/hp-hr & 3.0 ppm@ 15%O2, TV 0.08lbs/hr | 10 | CO - Carbon Monoxide | PASS | NA | Y | The report was accepted as verification of compliance by the OEPA. However a few instances onsite were witnessed and variances were allowed to the testers for only accepting two runs as verification of compliance for P005 (NOx) and P009 (CO). Many issues could be attributed to the cold weather, however are preventable, and all efforts to prevent these issues from happening in the future will, and have been, taken into account for future test acceptance.
2014 | 1939 | 0210002039 | Kilgore Compressor Station-Utica Gas Services, LLC | Pontiff Rd | Kilgore | 43988 |  | Carroll | P001 | 1,775 hp NG-fired 4SLB Stationary ICE equipped w/catalyst Caterpillar G3606 Serial Number: 4ZS01713 | 2014-01-15 | CC001(Catalytic Converter): Compressor Engine #1 - Oxidation Catalyst; CC002(Catalytic Converter): Compressor Engine #2 - Oxidation Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - Oxidation Catalyst; CC004(Catalytic Converter): Compressor Eng | Alliance Source Testing, Inc. | 1775 HP | NSPS 2.0g/hp-hr & 270 ppm@ 15%O2, TV 1.18lbs/hr | 1722 HP | NSPS .02g/hp-hr & 3.0 ppm@ 15%O2, TV 0.08lbs/hr | 10 | CO - Carbon Monoxide | PASS | NA | Y | The report was accepted as verification of compliance by the OEPA. However a few instances onsite were witnessed and variances were allowed to the testers for only accepting two runs as verification of compliance for P005 (NOx) and P009 (CO). Many issues could be attributed to the cold weather, however are preventable, and all efforts to prevent these issues from happening in the future will, and have been, taken into account for future test acceptance.
2014 | 1951 | 0210002039 | Kilgore Compressor Station-Utica Gas Services, LLC | Pontiff Rd | Kilgore | 43988 |  | Carroll | P001 | 1,775 hp NG-fired 4SLB Stationary ICE equipped w/catalyst Caterpillar G3606 Serial Number: 4ZS01713 | 2014-01-17 | CC001(Catalytic Converter): Compressor Engine #1 - Oxidation Catalyst; CC002(Catalytic Converter): Compressor Engine #2 - Oxidation Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - Oxidation Catalyst; CC004(Catalytic Converter): Compressor Eng | Alliance Source Testing, Inc. | 1775 HP | NSPS 2.0g/hp-hr & 270 ppm@ 15%O2, TV 1.18lbs/hr | 1722 HP | NSPS .02g/hp-hr & 3.0 ppm@ 15%O2, TV 0.08lbs/hr | 10 | CO - Carbon Monoxide | PASS | NA | Y | The report was accepted as verification of compliance by the OEPA. However a few instances onsite were witnessed and variances were allowed to the testers for only accepting two runs as verification of compliance for P005 (NOx) and P009 (CO). Many issues could be attributed to the cold weather, however are preventable, and all efforts to prevent these issues from happening in the future will, and have been, taken into account for future test acceptance.
2014 | 1980 | 0210002039 | Kilgore Compressor Station-Utica Gas Services, LLC | Pontiff Rd | Kilgore | 43988 |  | Carroll | P008 | 1,775 hp NG-fired 4SLB Stationary ICE equipped w/catalyst Caterpillar G3606: Serial Number: 4ZS01808 | 2014-01-18 | CC001(Catalytic Converter): Compressor Engine #1 - Oxidation Catalyst; CC002(Catalytic Converter): Compressor Engine #2 - Oxidation Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - Oxidation Catalyst; CC004(Catalytic Converter): Compressor Eng | Alliance Source Testing, Inc. | 1775 HP | NSPS 2.0g/hp-hr & 270 ppm@ 15%O2, TV 1.18lbs/hr | 1769 HP | NSPS 0.3g/hp-hr & 3.7 ppm@ 15%O2, TV 0.10lbs/hr | 10 | CO - Carbon Monoxide | PASS | NA | Y | The report was accepted as verification of compliance by the OEPA. However a few instances onsite were witnessed and variances were allowed to the testers for only accepting two runs as verification of compliance for P005 (NOx) and P009 (CO). Many issues could be attributed to the cold weather, however are preventable, and all efforts to prevent these issues from happening in the future will, and have been, taken into account for future test acceptance.
2014 | 1998 | 0210002039 | Kilgore Compressor Station-Utica Gas Services, LLC | Pontiff Rd | Kilgore | 43988 |  | Carroll | P001 | 1,775 hp NG-fired 4SLB Stationary ICE equipped w/catalyst Caterpillar G3606 Serial Number: 4ZS01713 | 2014-01-18 | CC001(Catalytic Converter): Compressor Engine #1 - Oxidation Catalyst; CC002(Catalytic Converter): Compressor Engine #2 - Oxidation Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - Oxidation Catalyst; CC004(Catalytic Converter): Compressor Eng | Alliance Source Testing, Inc. | 1775 HP | NSPS 2.0g/hp-hr & 270 ppm@ 15%O2, TV 1.18lbs/hr | 1722 HP | NSPS .02g/hp-hr & 3.0 ppm@ 15%O2, TV 0.08lbs/hr | 10 | CO - Carbon Monoxide | PASS | NA | Y | The report was accepted as verification of compliance by the OEPA. However a few instances onsite were witnessed and variances were allowed to the testers for only accepting two runs as verification of compliance for P005 (NOx) and P009 (CO). Many issues could be attributed to the cold weather, however are preventable, and all efforts to prevent these issues from happening in the future will, and have been, taken into account for future test acceptance.
2014 | 2000 | 0210002039 | Kilgore Compressor Station-Utica Gas Services, LLC | Pontiff Rd | Kilgore | 43988 |  | Carroll | P006 | 1,775 hp NG-fired 4SLB Stationary ICE equipped w/catalyst Caterpillar G3606: Serial Number: 4ZS01805 | 2014-01-14 | CC001(Catalytic Converter): Compressor Engine #1 - Oxidation Catalyst; CC002(Catalytic Converter): Compressor Engine #2 - Oxidation Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - Oxidation Catalyst; CC004(Catalytic Converter): Compressor Eng | Alliance Source Testing, Inc. | 1775 HP | NSPS 2.0g/hp-hr & 270 ppm@ 15%O2, TV 1.18lbs/hr | 1698 HP | NSPS 0.02g/hp-hr & 2.7 ppm@ 15%O2, TV 0.07lbs/hr | 10 | CO - Carbon Monoxide | PASS | NA | Y | The report was accepted as verification of compliance by the OEPA. However a few instances onsite were witnessed and variances were allowed to the testers for only accepting two runs as verification of compliance for P005 (NOx) and P009 (CO). Many issues could be attributed to the cold weather, however are preventable, and all efforts to prevent these issues from happening in the future will, and have been, taken into account for future test acceptance.
2014 | 2006 | 0210002039 | Kilgore Compressor Station-Utica Gas Services, LLC | Pontiff Rd | Kilgore | 43988 |  | Carroll | P006 | 1,775 hp NG-fired 4SLB Stationary ICE equipped w/catalyst Caterpillar G3606: Serial Number: 4ZS01805 | 2014-01-15 | CC001(Catalytic Converter): Compressor Engine #1 - Oxidation Catalyst; CC002(Catalytic Converter): Compressor Engine #2 - Oxidation Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - Oxidation Catalyst; CC004(Catalytic Converter): Compressor Eng | Alliance Source Testing, Inc. | 1775 HP | NSPS 2.0g/hp-hr & 270 ppm@ 15%O2, TV 1.18lbs/hr | 1698 HP | NSPS 0.02g/hp-hr & 2.7 ppm@ 15%O2, TV 0.07lbs/hr | 10 | CO - Carbon Monoxide | PASS | NA | Y | The report was accepted as verification of compliance by the OEPA. However a few instances onsite were witnessed and variances were allowed to the testers for only accepting two runs as verification of compliance for P005 (NOx) and P009 (CO). Many issues could be attributed to the cold weather, however are preventable, and all efforts to prevent these issues from happening in the future will, and have been, taken into account for future test acceptance.
2014 | 2007 | 0210002039 | Kilgore Compressor Station-Utica Gas Services, LLC | Pontiff Rd | Kilgore | 43988 |  | Carroll | P006 | 1,775 hp NG-fired 4SLB Stationary ICE equipped w/catalyst Caterpillar G3606: Serial Number: 4ZS01805 | 2014-01-16 | CC001(Catalytic Converter): Compressor Engine #1 - Oxidation Catalyst; CC002(Catalytic Converter): Compressor Engine #2 - Oxidation Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - Oxidation Catalyst; CC004(Catalytic Converter): Compressor Eng | Alliance Source Testing, Inc. | 1775 HP | NSPS 2.0g/hp-hr & 270 ppm@ 15%O2, TV 1.18lbs/hr | 1698 HP | NSPS 0.02g/hp-hr & 2.7 ppm@ 15%O2, TV 0.07lbs/hr | 10 | CO - Carbon Monoxide | PASS | NA | Y | The report was accepted as verification of compliance by the OEPA. However a few instances onsite were witnessed and variances were allowed to the testers for only accepting two runs as verification of compliance for P005 (NOx) and P009 (CO). Many issues could be attributed to the cold weather, however are preventable, and all efforts to prevent these issues from happening in the future will, and have been, taken into account for future test acceptance.
2014 | 2014 | 0210002039 | Kilgore Compressor Station-Utica Gas Services, LLC | Pontiff Rd | Kilgore | 43988 |  | Carroll | P006 | 1,775 hp NG-fired 4SLB Stationary ICE equipped w/catalyst Caterpillar G3606: Serial Number: 4ZS01805 | 2014-01-17 | CC001(Catalytic Converter): Compressor Engine #1 - Oxidation Catalyst; CC002(Catalytic Converter): Compressor Engine #2 - Oxidation Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - Oxidation Catalyst; CC004(Catalytic Converter): Compressor Eng | Alliance Source Testing, Inc. | 1775 HP | NSPS 2.0g/hp-hr & 270 ppm@ 15%O2, TV 1.18lbs/hr | 1698 HP | NSPS 0.02g/hp-hr & 2.7 ppm@ 15%O2, TV 0.07lbs/hr | 10 | CO - Carbon Monoxide | PASS | NA | Y | The report was accepted as verification of compliance by the OEPA. However a few instances onsite were witnessed and variances were allowed to the testers for only accepting two runs as verification of compliance for P005 (NOx) and P009 (CO). Many issues could be attributed to the cold weather, however are preventable, and all efforts to prevent these issues from happening in the future will, and have been, taken into account for future test acceptance.
2014 | 2017 | 0210002039 | Kilgore Compressor Station-Utica Gas Services, LLC | Pontiff Rd | Kilgore | 43988 |  | Carroll | P006 | 1,775 hp NG-fired 4SLB Stationary ICE equipped w/catalyst Caterpillar G3606: Serial Number: 4ZS01805 | 2014-01-18 | CC001(Catalytic Converter): Compressor Engine #1 - Oxidation Catalyst; CC002(Catalytic Converter): Compressor Engine #2 - Oxidation Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - Oxidation Catalyst; CC004(Catalytic Converter): Compressor Eng | Alliance Source Testing, Inc. | 1775 HP | NSPS 2.0g/hp-hr & 270 ppm@ 15%O2, TV 1.18lbs/hr | 1698 HP | NSPS 0.02g/hp-hr & 2.7 ppm@ 15%O2, TV 0.07lbs/hr | 10 | CO - Carbon Monoxide | PASS | NA | Y | The report was accepted as verification of compliance by the OEPA. However a few instances onsite were witnessed and variances were allowed to the testers for only accepting two runs as verification of compliance for P005 (NOx) and P009 (CO). Many issues could be attributed to the cold weather, however are preventable, and all efforts to prevent these issues from happening in the future will, and have been, taken into account for future test acceptance.
2014 | 2019 | 0210002039 | Kilgore Compressor Station-Utica Gas Services, LLC | Pontiff Rd | Kilgore | 43988 |  | Carroll | P005 | 1,775 hp NG-fired 4SLB Stationary ICE equipped w/catalyst Caterpillar G3606: Serial Number: 4ZS01804 | 2014-01-14 | CC001(Catalytic Converter): Compressor Engine #1 - Oxidation Catalyst; CC002(Catalytic Converter): Compressor Engine #2 - Oxidation Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - Oxidation Catalyst; CC004(Catalytic Converter): Compressor Eng | Alliance Source Testing, Inc. | 1775 HP | NSPS 2.0g/hp-hr & 270 ppm@ 15%O2, TV 1.18lbs/hr | 1698 HP | NSPS 0.02g/hp-hr & 3.4 ppm@ 15%O2, TV 0.09lbs/hr | 10 | CO - Carbon Monoxide | PASS | NA | Y | The report was accepted as verification of compliance by the OEPA. However a few instances onsite were witnessed and variances were allowed to the testers for only accepting two runs as verification of compliance for P005 (NOx) and P009 (CO). Many issues could be attributed to the cold weather, however are preventable, and all efforts to prevent these issues from happening in the future will, and have been, taken into account for future test acceptance.
2014 | 2021 | 0210002039 | Kilgore Compressor Station-Utica Gas Services, LLC | Pontiff Rd | Kilgore | 43988 |  | Carroll | P005 | 1,775 hp NG-fired 4SLB Stationary ICE equipped w/catalyst Caterpillar G3606: Serial Number: 4ZS01804 | 2014-01-15 | CC001(Catalytic Converter): Compressor Engine #1 - Oxidation Catalyst; CC002(Catalytic Converter): Compressor Engine #2 - Oxidation Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - Oxidation Catalyst; CC004(Catalytic Converter): Compressor Eng | Alliance Source Testing, Inc. | 1775 HP | NSPS 2.0g/hp-hr & 270 ppm@ 15%O2, TV 1.18lbs/hr | 1698 HP | NSPS 0.02g/hp-hr & 3.4 ppm@ 15%O2, TV 0.09lbs/hr | 10 | CO - Carbon Monoxide | PASS | NA | Y | The report was accepted as verification of compliance by the OEPA. However a few instances onsite were witnessed and variances were allowed to the testers for only accepting two runs as verification of compliance for P005 (NOx) and P009 (CO). Many issues could be attributed to the cold weather, however are preventable, and all efforts to prevent these issues from happening in the future will, and have been, taken into account for future test acceptance.
2014 | 2024 | 0210002039 | Kilgore Compressor Station-Utica Gas Services, LLC | Pontiff Rd | Kilgore | 43988 |  | Carroll | P005 | 1,775 hp NG-fired 4SLB Stationary ICE equipped w/catalyst Caterpillar G3606: Serial Number: 4ZS01804 | 2014-01-16 | CC001(Catalytic Converter): Compressor Engine #1 - Oxidation Catalyst; CC002(Catalytic Converter): Compressor Engine #2 - Oxidation Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - Oxidation Catalyst; CC004(Catalytic Converter): Compressor Eng | Alliance Source Testing, Inc. | 1775 HP | NSPS 2.0g/hp-hr & 270 ppm@ 15%O2, TV 1.18lbs/hr | 1698 HP | NSPS 0.02g/hp-hr & 3.4 ppm@ 15%O2, TV 0.09lbs/hr | 10 | CO - Carbon Monoxide | PASS | NA | Y | The report was accepted as verification of compliance by the OEPA. However a few instances onsite were witnessed and variances were allowed to the testers for only accepting two runs as verification of compliance for P005 (NOx) and P009 (CO). Many issues could be attributed to the cold weather, however are preventable, and all efforts to prevent these issues from happening in the future will, and have been, taken into account for future test acceptance.
2014 | 2028 | 0210002039 | Kilgore Compressor Station-Utica Gas Services, LLC | Pontiff Rd | Kilgore | 43988 |  | Carroll | P005 | 1,775 hp NG-fired 4SLB Stationary ICE equipped w/catalyst Caterpillar G3606: Serial Number: 4ZS01804 | 2014-01-17 | CC001(Catalytic Converter): Compressor Engine #1 - Oxidation Catalyst; CC002(Catalytic Converter): Compressor Engine #2 - Oxidation Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - Oxidation Catalyst; CC004(Catalytic Converter): Compressor Eng | Alliance Source Testing, Inc. | 1775 HP | NSPS 2.0g/hp-hr & 270 ppm@ 15%O2, TV 1.18lbs/hr | 1698 HP | NSPS 0.02g/hp-hr & 3.4 ppm@ 15%O2, TV 0.09lbs/hr | 10 | CO - Carbon Monoxide | PASS | NA | Y | The report was accepted as verification of compliance by the OEPA. However a few instances onsite were witnessed and variances were allowed to the testers for only accepting two runs as verification of compliance for P005 (NOx) and P009 (CO). Many issues could be attributed to the cold weather, however are preventable, and all efforts to prevent these issues from happening in the future will, and have been, taken into account for future test acceptance.
2014 | 2031 | 0210002039 | Kilgore Compressor Station-Utica Gas Services, LLC | Pontiff Rd | Kilgore | 43988 |  | Carroll | P005 | 1,775 hp NG-fired 4SLB Stationary ICE equipped w/catalyst Caterpillar G3606: Serial Number: 4ZS01804 | 2014-01-18 | CC001(Catalytic Converter): Compressor Engine #1 - Oxidation Catalyst; CC002(Catalytic Converter): Compressor Engine #2 - Oxidation Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - Oxidation Catalyst; CC004(Catalytic Converter): Compressor Eng | Alliance Source Testing, Inc. | 1775 HP | NSPS 2.0g/hp-hr & 270 ppm@ 15%O2, TV 1.18lbs/hr | 1698 HP | NSPS 0.02g/hp-hr & 3.4 ppm@ 15%O2, TV 0.09lbs/hr | 10 | CO - Carbon Monoxide | PASS | NA | Y | The report was accepted as verification of compliance by the OEPA. However a few instances onsite were witnessed and variances were allowed to the testers for only accepting two runs as verification of compliance for P005 (NOx) and P009 (CO). Many issues could be attributed to the cold weather, however are preventable, and all efforts to prevent these issues from happening in the future will, and have been, taken into account for future test acceptance.
2014 | 2033 | 0210002039 | Kilgore Compressor Station-Utica Gas Services, LLC | Pontiff Rd | Kilgore | 43988 |  | Carroll | P003 | 1,775 hp NG-fired 4SLB Stationary ICE equipped w/catalyst Caterpillar G3606: Serial Number: 4ZS01797 | 2014-01-14 | CC001(Catalytic Converter): Compressor Engine #1 - Oxidation Catalyst; CC002(Catalytic Converter): Compressor Engine #2 - Oxidation Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - Oxidation Catalyst; CC004(Catalytic Converter): Compressor Eng | Alliance Source Testing, Inc. | 1775 HP | NSPS 2.0g/hp-hr & 270 ppm@ 15%O2, TV 1.18lbs/hr | 1669 HP | NSPS 0.03g/hp-hr & 3.5 ppm@ 15%O2, TV 0.09lbs/hr | 10 | CO - Carbon Monoxide | PASS | NA | Y | The report was accepted as verification of compliance by the OEPA. However a few instances onsite were witnessed and variances were allowed to the testers for only accepting two runs as verification of compliance for P005 (NOx) and P009 (CO). Many issues could be attributed to the cold weather, however are preventable, and all efforts to prevent these issues from happening in the future will, and have been, taken into account for future test acceptance.
2014 | 2036 | 0210002039 | Kilgore Compressor Station-Utica Gas Services, LLC | Pontiff Rd | Kilgore | 43988 |  | Carroll | P003 | 1,775 hp NG-fired 4SLB Stationary ICE equipped w/catalyst Caterpillar G3606: Serial Number: 4ZS01797 | 2014-01-15 | CC001(Catalytic Converter): Compressor Engine #1 - Oxidation Catalyst; CC002(Catalytic Converter): Compressor Engine #2 - Oxidation Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - Oxidation Catalyst; CC004(Catalytic Converter): Compressor Eng | Alliance Source Testing, Inc. | 1775 HP | NSPS 2.0g/hp-hr & 270 ppm@ 15%O2, TV 1.18lbs/hr | 1669 HP | NSPS 0.03g/hp-hr & 3.5 ppm@ 15%O2, TV 0.09lbs/hr | 10 | CO - Carbon Monoxide | PASS | NA | Y | The report was accepted as verification of compliance by the OEPA. However a few instances onsite were witnessed and variances were allowed to the testers for only accepting two runs as verification of compliance for P005 (NOx) and P009 (CO). Many issues could be attributed to the cold weather, however are preventable, and all efforts to prevent these issues from happening in the future will, and have been, taken into account for future test acceptance.
2014 | 2039 | 0210002039 | Kilgore Compressor Station-Utica Gas Services, LLC | Pontiff Rd | Kilgore | 43988 |  | Carroll | P003 | 1,775 hp NG-fired 4SLB Stationary ICE equipped w/catalyst Caterpillar G3606: Serial Number: 4ZS01797 | 2014-01-16 | CC001(Catalytic Converter): Compressor Engine #1 - Oxidation Catalyst; CC002(Catalytic Converter): Compressor Engine #2 - Oxidation Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - Oxidation Catalyst; CC004(Catalytic Converter): Compressor Eng | Alliance Source Testing, Inc. | 1775 HP | NSPS 2.0g/hp-hr & 270 ppm@ 15%O2, TV 1.18lbs/hr | 1669 HP | NSPS 0.03g/hp-hr & 3.5 ppm@ 15%O2, TV 0.09lbs/hr | 10 | CO - Carbon Monoxide | PASS | NA | Y | The report was accepted as verification of compliance by the OEPA. However a few instances onsite were witnessed and variances were allowed to the testers for only accepting two runs as verification of compliance for P005 (NOx) and P009 (CO). Many issues could be attributed to the cold weather, however are preventable, and all efforts to prevent these issues from happening in the future will, and have been, taken into account for future test acceptance.
2014 | 2043 | 0210002039 | Kilgore Compressor Station-Utica Gas Services, LLC | Pontiff Rd | Kilgore | 43988 |  | Carroll | P003 | 1,775 hp NG-fired 4SLB Stationary ICE equipped w/catalyst Caterpillar G3606: Serial Number: 4ZS01797 | 2014-01-17 | CC001(Catalytic Converter): Compressor Engine #1 - Oxidation Catalyst; CC002(Catalytic Converter): Compressor Engine #2 - Oxidation Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - Oxidation Catalyst; CC004(Catalytic Converter): Compressor Eng | Alliance Source Testing, Inc. | 1775 HP | NSPS 2.0g/hp-hr & 270 ppm@ 15%O2, TV 1.18lbs/hr | 1669 HP | NSPS 0.03g/hp-hr & 3.5 ppm@ 15%O2, TV 0.09lbs/hr | 10 | CO - Carbon Monoxide | PASS | NA | Y | The report was accepted as verification of compliance by the OEPA. However a few instances onsite were witnessed and variances were allowed to the testers for only accepting two runs as verification of compliance for P005 (NOx) and P009 (CO). Many issues could be attributed to the cold weather, however are preventable, and all efforts to prevent these issues from happening in the future will, and have been, taken into account for future test acceptance.
2014 | 2045 | 0210002039 | Kilgore Compressor Station-Utica Gas Services, LLC | Pontiff Rd | Kilgore | 43988 |  | Carroll | P003 | 1,775 hp NG-fired 4SLB Stationary ICE equipped w/catalyst Caterpillar G3606: Serial Number: 4ZS01797 | 2014-01-18 | CC001(Catalytic Converter): Compressor Engine #1 - Oxidation Catalyst; CC002(Catalytic Converter): Compressor Engine #2 - Oxidation Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - Oxidation Catalyst; CC004(Catalytic Converter): Compressor Eng | Alliance Source Testing, Inc. | 1775 HP | NSPS 2.0g/hp-hr & 270 ppm@ 15%O2, TV 1.18lbs/hr | 1669 HP | NSPS 0.03g/hp-hr & 3.5 ppm@ 15%O2, TV 0.09lbs/hr | 10 | CO - Carbon Monoxide | PASS | NA | Y | The report was accepted as verification of compliance by the OEPA. However a few instances onsite were witnessed and variances were allowed to the testers for only accepting two runs as verification of compliance for P005 (NOx) and P009 (CO). Many issues could be attributed to the cold weather, however are preventable, and all efforts to prevent these issues from happening in the future will, and have been, taken into account for future test acceptance.
2014 | 2048 | 0210002039 | Kilgore Compressor Station-Utica Gas Services, LLC | Pontiff Rd | Kilgore | 43988 |  | Carroll | P009 | 1,775 hp NG-fired 4SLB Stationary ICE equipped w/catalyst Caterpillar G3606: Serial Number: 4ZS01776 | 2014-01-14 | CC001(Catalytic Converter): Compressor Engine #1 - Oxidation Catalyst; CC002(Catalytic Converter): Compressor Engine #2 - Oxidation Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - Oxidation Catalyst; CC004(Catalytic Converter): Compressor Eng | Alliance Source Testing, Inc. | 1775 HP | NSPS 2.0g/hp-hr & 270 ppm@ 15%O2, TV 1.18lbs/hr | 1722 HP *all CO results are 2 run average(P009) | NSPS 0.03g/hp-hr & 4.7 ppm@ 15%O2, TV 0.13lbs/hr | 10 | CO - Carbon Monoxide | PASS | NA | Y | The report was accepted as verification of compliance by the OEPA. However a few instances onsite were witnessed and variances were allowed to the testers for only accepting two runs as verification of compliance for P005 (NOx) and P009 (CO). Many issues could be attributed to the cold weather, however are preventable, and all efforts to prevent these issues from happening in the future will, and have been, taken into account for future test acceptance.
2014 | 2053 | 0210002039 | Kilgore Compressor Station-Utica Gas Services, LLC | Pontiff Rd | Kilgore | 43988 |  | Carroll | P009 | 1,775 hp NG-fired 4SLB Stationary ICE equipped w/catalyst Caterpillar G3606: Serial Number: 4ZS01776 | 2014-01-15 | CC001(Catalytic Converter): Compressor Engine #1 - Oxidation Catalyst; CC002(Catalytic Converter): Compressor Engine #2 - Oxidation Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - Oxidation Catalyst; CC004(Catalytic Converter): Compressor Eng | Alliance Source Testing, Inc. | 1775 HP | NSPS 2.0g/hp-hr & 270 ppm@ 15%O2, TV 1.18lbs/hr | 1722 HP *all CO results are 2 run average(P009) | NSPS 0.03g/hp-hr & 4.7 ppm@ 15%O2, TV 0.13lbs/hr | 10 | CO - Carbon Monoxide | PASS | NA | Y | The report was accepted as verification of compliance by the OEPA. However a few instances onsite were witnessed and variances were allowed to the testers for only accepting two runs as verification of compliance for P005 (NOx) and P009 (CO). Many issues could be attributed to the cold weather, however are preventable, and all efforts to prevent these issues from happening in the future will, and have been, taken into account for future test acceptance.
2014 | 2056 | 0210002039 | Kilgore Compressor Station-Utica Gas Services, LLC | Pontiff Rd | Kilgore | 43988 |  | Carroll | P009 | 1,775 hp NG-fired 4SLB Stationary ICE equipped w/catalyst Caterpillar G3606: Serial Number: 4ZS01776 | 2014-01-16 | CC001(Catalytic Converter): Compressor Engine #1 - Oxidation Catalyst; CC002(Catalytic Converter): Compressor Engine #2 - Oxidation Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - Oxidation Catalyst; CC004(Catalytic Converter): Compressor Eng | Alliance Source Testing, Inc. | 1775 HP | NSPS 2.0g/hp-hr & 270 ppm@ 15%O2, TV 1.18lbs/hr | 1722 HP *all CO results are 2 run average(P009) | NSPS 0.03g/hp-hr & 4.7 ppm@ 15%O2, TV 0.13lbs/hr | 10 | CO - Carbon Monoxide | PASS | NA | Y | The report was accepted as verification of compliance by the OEPA. However a few instances onsite were witnessed and variances were allowed to the testers for only accepting two runs as verification of compliance for P005 (NOx) and P009 (CO). Many issues could be attributed to the cold weather, however are preventable, and all efforts to prevent these issues from happening in the future will, and have been, taken into account for future test acceptance.
2014 | 2057 | 0210002039 | Kilgore Compressor Station-Utica Gas Services, LLC | Pontiff Rd | Kilgore | 43988 |  | Carroll | P009 | 1,775 hp NG-fired 4SLB Stationary ICE equipped w/catalyst Caterpillar G3606: Serial Number: 4ZS01776 | 2014-01-17 | CC001(Catalytic Converter): Compressor Engine #1 - Oxidation Catalyst; CC002(Catalytic Converter): Compressor Engine #2 - Oxidation Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - Oxidation Catalyst; CC004(Catalytic Converter): Compressor Eng | Alliance Source Testing, Inc. | 1775 HP | NSPS 2.0g/hp-hr & 270 ppm@ 15%O2, TV 1.18lbs/hr | 1722 HP *all CO results are 2 run average(P009) | NSPS 0.03g/hp-hr & 4.7 ppm@ 15%O2, TV 0.13lbs/hr | 10 | CO - Carbon Monoxide | PASS | NA | Y | The report was accepted as verification of compliance by the OEPA. However a few instances onsite were witnessed and variances were allowed to the testers for only accepting two runs as verification of compliance for P005 (NOx) and P009 (CO). Many issues could be attributed to the cold weather, however are preventable, and all efforts to prevent these issues from happening in the future will, and have been, taken into account for future test acceptance.
2014 | 2071 | 0210002039 | Kilgore Compressor Station-Utica Gas Services, LLC | Pontiff Rd | Kilgore | 43988 |  | Carroll | P009 | 1,775 hp NG-fired 4SLB Stationary ICE equipped w/catalyst Caterpillar G3606: Serial Number: 4ZS01776 | 2014-01-18 | CC001(Catalytic Converter): Compressor Engine #1 - Oxidation Catalyst; CC002(Catalytic Converter): Compressor Engine #2 - Oxidation Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - Oxidation Catalyst; CC004(Catalytic Converter): Compressor Eng | Alliance Source Testing, Inc. | 1775 HP | NSPS 2.0g/hp-hr & 270 ppm@ 15%O2, TV 1.18lbs/hr | 1722 HP *all CO results are 2 run average(P009) | NSPS 0.03g/hp-hr & 4.7 ppm@ 15%O2, TV 0.13lbs/hr | 10 | CO - Carbon Monoxide | PASS | NA | Y | The report was accepted as verification of compliance by the OEPA. However a few instances onsite were witnessed and variances were allowed to the testers for only accepting two runs as verification of compliance for P005 (NOx) and P009 (CO). Many issues could be attributed to the cold weather, however are preventable, and all efforts to prevent these issues from happening in the future will, and have been, taken into account for future test acceptance.
2014 | 2073 | 0210002039 | Kilgore Compressor Station-Utica Gas Services, LLC | Pontiff Rd | Kilgore | 43988 |  | Carroll | P007 | 1,775 hp NG-fired 4SLB Stationary ICE equipped w/catalyst Caterpillar G3606: Serial Number: 4ZS01807 | 2014-01-14 | CC001(Catalytic Converter): Compressor Engine #1 - Oxidation Catalyst; CC002(Catalytic Converter): Compressor Engine #2 - Oxidation Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - Oxidation Catalyst; CC004(Catalytic Converter): Compressor Eng | Alliance Source Testing, Inc. | 1775 HP | NSPS 2.0g/hp-hr & 270 ppm@ 15%O2, TV 1.18lbs/hr | 1716 HP | NSPS 0.04g/hp-hr & 5.1 ppm@ 15%O2, TV 0.14lbs/hr | 10 | CO - Carbon Monoxide | PASS | NA | Y | The report was accepted as verification of compliance by the OEPA. However a few instances onsite were witnessed and variances were allowed to the testers for only accepting two runs as verification of compliance for P005 (NOx) and P009 (CO). Many issues could be attributed to the cold weather, however are preventable, and all efforts to prevent these issues from happening in the future will, and have been, taken into account for future test acceptance.
2014 | 2076 | 0210002039 | Kilgore Compressor Station-Utica Gas Services, LLC | Pontiff Rd | Kilgore | 43988 |  | Carroll | P007 | 1,775 hp NG-fired 4SLB Stationary ICE equipped w/catalyst Caterpillar G3606: Serial Number: 4ZS01807 | 2014-01-15 | CC001(Catalytic Converter): Compressor Engine #1 - Oxidation Catalyst; CC002(Catalytic Converter): Compressor Engine #2 - Oxidation Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - Oxidation Catalyst; CC004(Catalytic Converter): Compressor Eng | Alliance Source Testing, Inc. | 1775 HP | NSPS 2.0g/hp-hr & 270 ppm@ 15%O2, TV 1.18lbs/hr | 1716 HP | NSPS 0.04g/hp-hr & 5.1 ppm@ 15%O2, TV 0.14lbs/hr | 10 | CO - Carbon Monoxide | PASS | NA | Y | The report was accepted as verification of compliance by the OEPA. However a few instances onsite were witnessed and variances were allowed to the testers for only accepting two runs as verification of compliance for P005 (NOx) and P009 (CO). Many issues could be attributed to the cold weather, however are preventable, and all efforts to prevent these issues from happening in the future will, and have been, taken into account for future test acceptance.
2014 | 2079 | 0210002039 | Kilgore Compressor Station-Utica Gas Services, LLC | Pontiff Rd | Kilgore | 43988 |  | Carroll | P007 | 1,775 hp NG-fired 4SLB Stationary ICE equipped w/catalyst Caterpillar G3606: Serial Number: 4ZS01807 | 2014-01-16 | CC001(Catalytic Converter): Compressor Engine #1 - Oxidation Catalyst; CC002(Catalytic Converter): Compressor Engine #2 - Oxidation Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - Oxidation Catalyst; CC004(Catalytic Converter): Compressor Eng | Alliance Source Testing, Inc. | 1775 HP | NSPS 2.0g/hp-hr & 270 ppm@ 15%O2, TV 1.18lbs/hr | 1716 HP | NSPS 0.04g/hp-hr & 5.1 ppm@ 15%O2, TV 0.14lbs/hr | 10 | CO - Carbon Monoxide | PASS | NA | Y | The report was accepted as verification of compliance by the OEPA. However a few instances onsite were witnessed and variances were allowed to the testers for only accepting two runs as verification of compliance for P005 (NOx) and P009 (CO). Many issues could be attributed to the cold weather, however are preventable, and all efforts to prevent these issues from happening in the future will, and have been, taken into account for future test acceptance.
2014 | 2083 | 0210002039 | Kilgore Compressor Station-Utica Gas Services, LLC | Pontiff Rd | Kilgore | 43988 |  | Carroll | P007 | 1,775 hp NG-fired 4SLB Stationary ICE equipped w/catalyst Caterpillar G3606: Serial Number: 4ZS01807 | 2014-01-17 | CC001(Catalytic Converter): Compressor Engine #1 - Oxidation Catalyst; CC002(Catalytic Converter): Compressor Engine #2 - Oxidation Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - Oxidation Catalyst; CC004(Catalytic Converter): Compressor Eng | Alliance Source Testing, Inc. | 1775 HP | NSPS 2.0g/hp-hr & 270 ppm@ 15%O2, TV 1.18lbs/hr | 1716 HP | NSPS 0.04g/hp-hr & 5.1 ppm@ 15%O2, TV 0.14lbs/hr | 10 | CO - Carbon Monoxide | PASS | NA | Y | The report was accepted as verification of compliance by the OEPA. However a few instances onsite were witnessed and variances were allowed to the testers for only accepting two runs as verification of compliance for P005 (NOx) and P009 (CO). Many issues could be attributed to the cold weather, however are preventable, and all efforts to prevent these issues from happening in the future will, and have been, taken into account for future test acceptance.
2014 | 2085 | 0210002039 | Kilgore Compressor Station-Utica Gas Services, LLC | Pontiff Rd | Kilgore | 43988 |  | Carroll | P007 | 1,775 hp NG-fired 4SLB Stationary ICE equipped w/catalyst Caterpillar G3606: Serial Number: 4ZS01807 | 2014-01-18 | CC001(Catalytic Converter): Compressor Engine #1 - Oxidation Catalyst; CC002(Catalytic Converter): Compressor Engine #2 - Oxidation Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - Oxidation Catalyst; CC004(Catalytic Converter): Compressor Eng | Alliance Source Testing, Inc. | 1775 HP | NSPS 2.0g/hp-hr & 270 ppm@ 15%O2, TV 1.18lbs/hr | 1716 HP | NSPS 0.04g/hp-hr & 5.1 ppm@ 15%O2, TV 0.14lbs/hr | 10 | CO - Carbon Monoxide | PASS | NA | Y | The report was accepted as verification of compliance by the OEPA. However a few instances onsite were witnessed and variances were allowed to the testers for only accepting two runs as verification of compliance for P005 (NOx) and P009 (CO). Many issues could be attributed to the cold weather, however are preventable, and all efforts to prevent these issues from happening in the future will, and have been, taken into account for future test acceptance.
2014 | 2088 | 0210002039 | Kilgore Compressor Station-Utica Gas Services, LLC | Pontiff Rd | Kilgore | 43988 |  | Carroll | P002 | 1,775 hp NG-fired 4SLB Stationary ICE equipped w/catalyst Caterpillar G3606: Serial Number: 4ZS01796 | 2014-01-14 | CC001(Catalytic Converter): Compressor Engine #1 - Oxidation Catalyst; CC002(Catalytic Converter): Compressor Engine #2 - Oxidation Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - Oxidation Catalyst; CC004(Catalytic Converter): Compressor Eng | Alliance Source Testing, Inc. | 1775 HP | NSPS 2.0g/hp-hr & 270 ppm@ 15%O2, TV 1.18lbs/hr | 1698 HP | NSPS 0.04g/hp-hr & 5.6 ppm@ 15%O2, TV 0.15lbs/hr | 10 | CO - Carbon Monoxide | PASS | NA | Y | The report was accepted as verification of compliance by the OEPA. However a few instances onsite were witnessed and variances were allowed to the testers for only accepting two runs as verification of compliance for P005 (NOx) and P009 (CO). Many issues could be attributed to the cold weather, however are preventable, and all efforts to prevent these issues from happening in the future will, and have been, taken into account for future test acceptance.
2014 | 2093 | 0210002039 | Kilgore Compressor Station-Utica Gas Services, LLC | Pontiff Rd | Kilgore | 43988 |  | Carroll | P002 | 1,775 hp NG-fired 4SLB Stationary ICE equipped w/catalyst Caterpillar G3606: Serial Number: 4ZS01796 | 2014-01-15 | CC001(Catalytic Converter): Compressor Engine #1 - Oxidation Catalyst; CC002(Catalytic Converter): Compressor Engine #2 - Oxidation Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - Oxidation Catalyst; CC004(Catalytic Converter): Compressor Eng | Alliance Source Testing, Inc. | 1775 HP | NSPS 2.0g/hp-hr & 270 ppm@ 15%O2, TV 1.18lbs/hr | 1698 HP | NSPS 0.04g/hp-hr & 5.6 ppm@ 15%O2, TV 0.15lbs/hr | 10 | CO - Carbon Monoxide | PASS | NA | Y | The report was accepted as verification of compliance by the OEPA. However a few instances onsite were witnessed and variances were allowed to the testers for only accepting two runs as verification of compliance for P005 (NOx) and P009 (CO). Many issues could be attributed to the cold weather, however are preventable, and all efforts to prevent these issues from happening in the future will, and have been, taken into account for future test acceptance.
2014 | 2094 | 0210002039 | Kilgore Compressor Station-Utica Gas Services, LLC | Pontiff Rd | Kilgore | 43988 |  | Carroll | P002 | 1,775 hp NG-fired 4SLB Stationary ICE equipped w/catalyst Caterpillar G3606: Serial Number: 4ZS01796 | 2014-01-16 | CC001(Catalytic Converter): Compressor Engine #1 - Oxidation Catalyst; CC002(Catalytic Converter): Compressor Engine #2 - Oxidation Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - Oxidation Catalyst; CC004(Catalytic Converter): Compressor Eng | Alliance Source Testing, Inc. | 1775 HP | NSPS 2.0g/hp-hr & 270 ppm@ 15%O2, TV 1.18lbs/hr | 1698 HP | NSPS 0.04g/hp-hr & 5.6 ppm@ 15%O2, TV 0.15lbs/hr | 10 | CO - Carbon Monoxide | PASS | NA | Y | The report was accepted as verification of compliance by the OEPA. However a few instances onsite were witnessed and variances were allowed to the testers for only accepting two runs as verification of compliance for P005 (NOx) and P009 (CO). Many issues could be attributed to the cold weather, however are preventable, and all efforts to prevent these issues from happening in the future will, and have been, taken into account for future test acceptance.
2014 | 2097 | 0210002039 | Kilgore Compressor Station-Utica Gas Services, LLC | Pontiff Rd | Kilgore | 43988 |  | Carroll | P002 | 1,775 hp NG-fired 4SLB Stationary ICE equipped w/catalyst Caterpillar G3606: Serial Number: 4ZS01796 | 2014-01-17 | CC001(Catalytic Converter): Compressor Engine #1 - Oxidation Catalyst; CC002(Catalytic Converter): Compressor Engine #2 - Oxidation Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - Oxidation Catalyst; CC004(Catalytic Converter): Compressor Eng | Alliance Source Testing, Inc. | 1775 HP | NSPS 2.0g/hp-hr & 270 ppm@ 15%O2, TV 1.18lbs/hr | 1698 HP | NSPS 0.04g/hp-hr & 5.6 ppm@ 15%O2, TV 0.15lbs/hr | 10 | CO - Carbon Monoxide | PASS | NA | Y | The report was accepted as verification of compliance by the OEPA. However a few instances onsite were witnessed and variances were allowed to the testers for only accepting two runs as verification of compliance for P005 (NOx) and P009 (CO). Many issues could be attributed to the cold weather, however are preventable, and all efforts to prevent these issues from happening in the future will, and have been, taken into account for future test acceptance.
2014 | 2102 | 0210002039 | Kilgore Compressor Station-Utica Gas Services, LLC | Pontiff Rd | Kilgore | 43988 |  | Carroll | P002 | 1,775 hp NG-fired 4SLB Stationary ICE equipped w/catalyst Caterpillar G3606: Serial Number: 4ZS01796 | 2014-01-18 | CC001(Catalytic Converter): Compressor Engine #1 - Oxidation Catalyst; CC002(Catalytic Converter): Compressor Engine #2 - Oxidation Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - Oxidation Catalyst; CC004(Catalytic Converter): Compressor Eng | Alliance Source Testing, Inc. | 1775 HP | NSPS 2.0g/hp-hr & 270 ppm@ 15%O2, TV 1.18lbs/hr | 1698 HP | NSPS 0.04g/hp-hr & 5.6 ppm@ 15%O2, TV 0.15lbs/hr | 10 | CO - Carbon Monoxide | PASS | NA | Y | The report was accepted as verification of compliance by the OEPA. However a few instances onsite were witnessed and variances were allowed to the testers for only accepting two runs as verification of compliance for P005 (NOx) and P009 (CO). Many issues could be attributed to the cold weather, however are preventable, and all efforts to prevent these issues from happening in the future will, and have been, taken into account for future test acceptance.
2014 | 2103 | 0210002039 | Kilgore Compressor Station-Utica Gas Services, LLC | Pontiff Rd | Kilgore | 43988 |  | Carroll | P010 | 1,775 hp NG-fired 4SLB Stationary ICE equipped w/catalyst Caterpillar G3606: Serial Number: 4ZS01814 | 2014-01-14 | CC001(Catalytic Converter): Compressor Engine #1 - Oxidation Catalyst; CC002(Catalytic Converter): Compressor Engine #2 - Oxidation Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - Oxidation Catalyst; CC004(Catalytic Converter): Compressor Eng | Alliance Source Testing, Inc. | 1775 HP | NSPS 2.0g/hp-hr & 270 ppm@ 15%O2, TV 1.18lbs/hr | 1663 HP | NSPS 0.1g/hp-hr & 9.4 ppm@ 15%O2, TV 0.25lbs/hr | 10 | CO - Carbon Monoxide | PASS | NA | Y | The report was accepted as verification of compliance by the OEPA. However a few instances onsite were witnessed and variances were allowed to the testers for only accepting two runs as verification of compliance for P005 (NOx) and P009 (CO). Many issues could be attributed to the cold weather, however are preventable, and all efforts to prevent these issues from happening in the future will, and have been, taken into account for future test acceptance.
2014 | 2106 | 0210002039 | Kilgore Compressor Station-Utica Gas Services, LLC | Pontiff Rd | Kilgore | 43988 |  | Carroll | P010 | 1,775 hp NG-fired 4SLB Stationary ICE equipped w/catalyst Caterpillar G3606: Serial Number: 4ZS01814 | 2014-01-15 | CC001(Catalytic Converter): Compressor Engine #1 - Oxidation Catalyst; CC002(Catalytic Converter): Compressor Engine #2 - Oxidation Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - Oxidation Catalyst; CC004(Catalytic Converter): Compressor Eng | Alliance Source Testing, Inc. | 1775 HP | NSPS 2.0g/hp-hr & 270 ppm@ 15%O2, TV 1.18lbs/hr | 1663 HP | NSPS 0.1g/hp-hr & 9.4 ppm@ 15%O2, TV 0.25lbs/hr | 10 | CO - Carbon Monoxide | PASS | NA | Y | The report was accepted as verification of compliance by the OEPA. However a few instances onsite were witnessed and variances were allowed to the testers for only accepting two runs as verification of compliance for P005 (NOx) and P009 (CO). Many issues could be attributed to the cold weather, however are preventable, and all efforts to prevent these issues from happening in the future will, and have been, taken into account for future test acceptance.
2014 | 2111 | 0210002039 | Kilgore Compressor Station-Utica Gas Services, LLC | Pontiff Rd | Kilgore | 43988 |  | Carroll | P010 | 1,775 hp NG-fired 4SLB Stationary ICE equipped w/catalyst Caterpillar G3606: Serial Number: 4ZS01814 | 2014-01-16 | CC001(Catalytic Converter): Compressor Engine #1 - Oxidation Catalyst; CC002(Catalytic Converter): Compressor Engine #2 - Oxidation Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - Oxidation Catalyst; CC004(Catalytic Converter): Compressor Eng | Alliance Source Testing, Inc. | 1775 HP | NSPS 2.0g/hp-hr & 270 ppm@ 15%O2, TV 1.18lbs/hr | 1663 HP | NSPS 0.1g/hp-hr & 9.4 ppm@ 15%O2, TV 0.25lbs/hr | 10 | CO - Carbon Monoxide | PASS | NA | Y | The report was accepted as verification of compliance by the OEPA. However a few instances onsite were witnessed and variances were allowed to the testers for only accepting two runs as verification of compliance for P005 (NOx) and P009 (CO). Many issues could be attributed to the cold weather, however are preventable, and all efforts to prevent these issues from happening in the future will, and have been, taken into account for future test acceptance.
2014 | 2112 | 0210002039 | Kilgore Compressor Station-Utica Gas Services, LLC | Pontiff Rd | Kilgore | 43988 |  | Carroll | P010 | 1,775 hp NG-fired 4SLB Stationary ICE equipped w/catalyst Caterpillar G3606: Serial Number: 4ZS01814 | 2014-01-17 | CC001(Catalytic Converter): Compressor Engine #1 - Oxidation Catalyst; CC002(Catalytic Converter): Compressor Engine #2 - Oxidation Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - Oxidation Catalyst; CC004(Catalytic Converter): Compressor Eng | Alliance Source Testing, Inc. | 1775 HP | NSPS 2.0g/hp-hr & 270 ppm@ 15%O2, TV 1.18lbs/hr | 1663 HP | NSPS 0.1g/hp-hr & 9.4 ppm@ 15%O2, TV 0.25lbs/hr | 10 | CO - Carbon Monoxide | PASS | NA | Y | The report was accepted as verification of compliance by the OEPA. However a few instances onsite were witnessed and variances were allowed to the testers for only accepting two runs as verification of compliance for P005 (NOx) and P009 (CO). Many issues could be attributed to the cold weather, however are preventable, and all efforts to prevent these issues from happening in the future will, and have been, taken into account for future test acceptance.
2014 | 2116 | 0210002039 | Kilgore Compressor Station-Utica Gas Services, LLC | Pontiff Rd | Kilgore | 43988 |  | Carroll | P010 | 1,775 hp NG-fired 4SLB Stationary ICE equipped w/catalyst Caterpillar G3606: Serial Number: 4ZS01814 | 2014-01-18 | CC001(Catalytic Converter): Compressor Engine #1 - Oxidation Catalyst; CC002(Catalytic Converter): Compressor Engine #2 - Oxidation Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - Oxidation Catalyst; CC004(Catalytic Converter): Compressor Eng | Alliance Source Testing, Inc. | 1775 HP | NSPS 2.0g/hp-hr & 270 ppm@ 15%O2, TV 1.18lbs/hr | 1663 HP | NSPS 0.1g/hp-hr & 9.4 ppm@ 15%O2, TV 0.25lbs/hr | 10 | CO - Carbon Monoxide | PASS | NA | Y | The report was accepted as verification of compliance by the OEPA. However a few instances onsite were witnessed and variances were allowed to the testers for only accepting two runs as verification of compliance for P005 (NOx) and P009 (CO). Many issues could be attributed to the cold weather, however are preventable, and all efforts to prevent these issues from happening in the future will, and have been, taken into account for future test acceptance.
2014 | 2120 | 0210002039 | Kilgore Compressor Station-Utica Gas Services, LLC | Pontiff Rd | Kilgore | 43988 |  | Carroll | P004 | 1,775 hp NG-fired 4SLB Stationary ICE equipped w/catalyst Caterpillar G3606: Serial Number: 4ZS01800 | 2014-01-14 | CC001(Catalytic Converter): Compressor Engine #1 - Oxidation Catalyst; CC002(Catalytic Converter): Compressor Engine #2 - Oxidation Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - Oxidation Catalyst; CC004(Catalytic Converter): Compressor Eng | Alliance Source Testing, Inc. | 1775 HP | NSPS 2.0g/hp-hr & 270 ppm@ 15%O2, TV 1.18lbs/hr | 1698 HP | NSPS 0.3g/hp-hr & 3.6 ppm@ 15%O2, TV 0.10lbs/hr | 10 | CO - Carbon Monoxide | PASS | NA | Y | The report was accepted as verification of compliance by the OEPA. However a few instances onsite were witnessed and variances were allowed to the testers for only accepting two runs as verification of compliance for P005 (NOx) and P009 (CO). Many issues could be attributed to the cold weather, however are preventable, and all efforts to prevent these issues from happening in the future will, and have been, taken into account for future test acceptance.
2014 | 2122 | 0210002039 | Kilgore Compressor Station-Utica Gas Services, LLC | Pontiff Rd | Kilgore | 43988 |  | Carroll | P004 | 1,775 hp NG-fired 4SLB Stationary ICE equipped w/catalyst Caterpillar G3606: Serial Number: 4ZS01800 | 2014-01-15 | CC001(Catalytic Converter): Compressor Engine #1 - Oxidation Catalyst; CC002(Catalytic Converter): Compressor Engine #2 - Oxidation Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - Oxidation Catalyst; CC004(Catalytic Converter): Compressor Eng | Alliance Source Testing, Inc. | 1775 HP | NSPS 2.0g/hp-hr & 270 ppm@ 15%O2, TV 1.18lbs/hr | 1698 HP | NSPS 0.3g/hp-hr & 3.6 ppm@ 15%O2, TV 0.10lbs/hr | 10 | CO - Carbon Monoxide | PASS | NA | Y | The report was accepted as verification of compliance by the OEPA. However a few instances onsite were witnessed and variances were allowed to the testers for only accepting two runs as verification of compliance for P005 (NOx) and P009 (CO). Many issues could be attributed to the cold weather, however are preventable, and all efforts to prevent these issues from happening in the future will, and have been, taken into account for future test acceptance.
2014 | 2125 | 0210002039 | Kilgore Compressor Station-Utica Gas Services, LLC | Pontiff Rd | Kilgore | 43988 |  | Carroll | P004 | 1,775 hp NG-fired 4SLB Stationary ICE equipped w/catalyst Caterpillar G3606: Serial Number: 4ZS01800 | 2014-01-16 | CC001(Catalytic Converter): Compressor Engine #1 - Oxidation Catalyst; CC002(Catalytic Converter): Compressor Engine #2 - Oxidation Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - Oxidation Catalyst; CC004(Catalytic Converter): Compressor Eng | Alliance Source Testing, Inc. | 1775 HP | NSPS 2.0g/hp-hr & 270 ppm@ 15%O2, TV 1.18lbs/hr | 1698 HP | NSPS 0.3g/hp-hr & 3.6 ppm@ 15%O2, TV 0.10lbs/hr | 10 | CO - Carbon Monoxide | PASS | NA | Y | The report was accepted as verification of compliance by the OEPA. However a few instances onsite were witnessed and variances were allowed to the testers for only accepting two runs as verification of compliance for P005 (NOx) and P009 (CO). Many issues could be attributed to the cold weather, however are preventable, and all efforts to prevent these issues from happening in the future will, and have been, taken into account for future test acceptance.
2014 | 2128 | 0210002039 | Kilgore Compressor Station-Utica Gas Services, LLC | Pontiff Rd | Kilgore | 43988 |  | Carroll | P004 | 1,775 hp NG-fired 4SLB Stationary ICE equipped w/catalyst Caterpillar G3606: Serial Number: 4ZS01800 | 2014-01-17 | CC001(Catalytic Converter): Compressor Engine #1 - Oxidation Catalyst; CC002(Catalytic Converter): Compressor Engine #2 - Oxidation Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - Oxidation Catalyst; CC004(Catalytic Converter): Compressor Eng | Alliance Source Testing, Inc. | 1775 HP | NSPS 2.0g/hp-hr & 270 ppm@ 15%O2, TV 1.18lbs/hr | 1698 HP | NSPS 0.3g/hp-hr & 3.6 ppm@ 15%O2, TV 0.10lbs/hr | 10 | CO - Carbon Monoxide | PASS | NA | Y | The report was accepted as verification of compliance by the OEPA. However a few instances onsite were witnessed and variances were allowed to the testers for only accepting two runs as verification of compliance for P005 (NOx) and P009 (CO). Many issues could be attributed to the cold weather, however are preventable, and all efforts to prevent these issues from happening in the future will, and have been, taken into account for future test acceptance.
2014 | 2425 | 0210002039 | Kilgore Compressor Station-Utica Gas Services, LLC | Pontiff Rd | Kilgore | 43988 |  | Carroll | P004 | 1,775 hp NG-fired 4SLB Stationary ICE equipped w/catalyst Caterpillar G3606: Serial Number: 4ZS01800 | 2014-01-18 | CC001(Catalytic Converter): Compressor Engine #1 - Oxidation Catalyst; CC002(Catalytic Converter): Compressor Engine #2 - Oxidation Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - Oxidation Catalyst; CC004(Catalytic Converter): Compressor Eng | Alliance Source Testing, Inc. | 1775 HP | NSPS 2.0g/hp-hr & 270 ppm@ 15%O2, TV 1.18lbs/hr | 1698 HP | NSPS 0.3g/hp-hr & 3.6 ppm@ 15%O2, TV 0.10lbs/hr | 10 | CO - Carbon Monoxide | PASS | NA | Y | The report was accepted as verification of compliance by the OEPA. However a few instances onsite were witnessed and variances were allowed to the testers for only accepting two runs as verification of compliance for P005 (NOx) and P009 (CO). Many issues could be attributed to the cold weather, however are preventable, and all efforts to prevent these issues from happening in the future will, and have been, taken into account for future test acceptance.
2014 | 2526 | 0210002039 | Kilgore Compressor Station-Utica Gas Services, LLC | Pontiff Rd | Kilgore | 43988 |  | Carroll | P008 | 1,775 hp NG-fired 4SLB Stationary ICE equipped w/catalyst Caterpillar G3606: Serial Number: 4ZS01808 | 2014-01-14 | CC001(Catalytic Converter): Compressor Engine #1 - Oxidation Catalyst; CC002(Catalytic Converter): Compressor Engine #2 - Oxidation Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - Oxidation Catalyst; CC004(Catalytic Converter): Compressor Eng | Alliance Source Testing, Inc. | 1775 HP | NSPS 2.0g/hp-hr & 270 ppm@ 15%O2, TV 1.18lbs/hr | 1769 HP | NSPS 0.3g/hp-hr & 3.7 ppm@ 15%O2, TV 0.10lbs/hr | 10 | CO - Carbon Monoxide | PASS | NA | Y | The report was accepted as verification of compliance by the OEPA. However a few instances onsite were witnessed and variances were allowed to the testers for only accepting two runs as verification of compliance for P005 (NOx) and P009 (CO). Many issues could be attributed to the cold weather, however are preventable, and all efforts to prevent these issues from happening in the future will, and have been, taken into account for future test acceptance.
2014 | 2554 | 0210002039 | Kilgore Compressor Station-Utica Gas Services, LLC | Pontiff Rd | Kilgore | 43988 |  | Carroll | P008 | 1,775 hp NG-fired 4SLB Stationary ICE equipped w/catalyst Caterpillar G3606: Serial Number: 4ZS01808 | 2014-01-15 | CC001(Catalytic Converter): Compressor Engine #1 - Oxidation Catalyst; CC002(Catalytic Converter): Compressor Engine #2 - Oxidation Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - Oxidation Catalyst; CC004(Catalytic Converter): Compressor Eng | Alliance Source Testing, Inc. | 1775 HP | NSPS 2.0g/hp-hr & 270 ppm@ 15%O2, TV 1.18lbs/hr | 1769 HP | NSPS 0.3g/hp-hr & 3.7 ppm@ 15%O2, TV 0.10lbs/hr | 10 | CO - Carbon Monoxide | PASS | NA | Y | The report was accepted as verification of compliance by the OEPA. However a few instances onsite were witnessed and variances were allowed to the testers for only accepting two runs as verification of compliance for P005 (NOx) and P009 (CO). Many issues could be attributed to the cold weather, however are preventable, and all efforts to prevent these issues from happening in the future will, and have been, taken into account for future test acceptance.
2014 | 2555 | 0210002039 | Kilgore Compressor Station-Utica Gas Services, LLC | Pontiff Rd | Kilgore | 43988 |  | Carroll | P008 | 1,775 hp NG-fired 4SLB Stationary ICE equipped w/catalyst Caterpillar G3606: Serial Number: 4ZS01808 | 2014-01-16 | CC001(Catalytic Converter): Compressor Engine #1 - Oxidation Catalyst; CC002(Catalytic Converter): Compressor Engine #2 - Oxidation Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - Oxidation Catalyst; CC004(Catalytic Converter): Compressor Eng | Alliance Source Testing, Inc. | 1775 HP | NSPS 2.0g/hp-hr & 270 ppm@ 15%O2, TV 1.18lbs/hr | 1769 HP | NSPS 0.3g/hp-hr & 3.7 ppm@ 15%O2, TV 0.10lbs/hr | 10 | CO - Carbon Monoxide | PASS | NA | Y | The report was accepted as verification of compliance by the OEPA. However a few instances onsite were witnessed and variances were allowed to the testers for only accepting two runs as verification of compliance for P005 (NOx) and P009 (CO). Many issues could be attributed to the cold weather, however are preventable, and all efforts to prevent these issues from happening in the future will, and have been, taken into account for future test acceptance.
2014 | 2588 | 0210002039 | Kilgore Compressor Station-Utica Gas Services, LLC | Pontiff Rd | Kilgore | 43988 |  | Carroll | P008 | 1,775 hp NG-fired 4SLB Stationary ICE equipped w/catalyst Caterpillar G3606: Serial Number: 4ZS01808 | 2014-01-17 | CC001(Catalytic Converter): Compressor Engine #1 - Oxidation Catalyst; CC002(Catalytic Converter): Compressor Engine #2 - Oxidation Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - Oxidation Catalyst; CC004(Catalytic Converter): Compressor Eng | Alliance Source Testing, Inc. | 1775 HP | NSPS 2.0g/hp-hr & 270 ppm@ 15%O2, TV 1.18lbs/hr | 1769 HP | NSPS 0.3g/hp-hr & 3.7 ppm@ 15%O2, TV 0.10lbs/hr | 10 | CO - Carbon Monoxide | PASS | NA | Y | The report was accepted as verification of compliance by the OEPA. However a few instances onsite were witnessed and variances were allowed to the testers for only accepting two runs as verification of compliance for P005 (NOx) and P009 (CO). Many issues could be attributed to the cold weather, however are preventable, and all efforts to prevent these issues from happening in the future will, and have been, taken into account for future test acceptance.
2015 | 110 | 0607015007 | Humphreys Compressor Station | Johnson Ridge Rd | Barnesville | 43713 |  | Belmont | P001 | Compressor Engine #1 - Caterpillar G3612TA - natural gas fired four-stroke, lean burn internal combustion engine rated at an operating capacity of 3,550 horsepower equipped with a double oxidation catalyst. | 2015-04-14 | CC001(Catalytic Converter): Compressor Engine #1 - Oxidation Catalyst | Air Hygiene, Inc. | 3550 hp | 2.0 g/hp-hr | 3290 hp | 0.03 g/hp-hr | 10 | CO - Carbon Monoxide | PP | NA | Y
2015 | 122 | 0661005020 | Rockies Express Pipeline - Seneca Compressor Station | Seneca Lake Rd | Quaker City | 43773 |  | Noble | P002 | Natural gas fired 4 stroke rich burn compressor engine, Waukesha P9394GSI, controlled by air/fuel ratio and nonselective catalytic reduction (NSCR) | 2015-03-03 | Engine 1(Catalytic Converter): Compressor Engine 1 catalytic converter; Engine 2(Catalytic Converter): Compressor Engine 2 catalytic converter | Compressor Engineering Corp. | 2250 hp | 4.0 g/hp-hr | 2237 hp | 0 g/hp-hr | 6348 03 | CO - Carbon Monoxide | PP | NA | Y
2015 | 123 | 0210012002 | Utica Gas Services, LLC-Carrollton Compressor Facility | 2098 Panda Road SE | Carrollton | 44615 |  | Carroll | P004 | 1,775 HP natural gas-fired Caterpillar G3606 engine #1 equipped with an oxidation catalyst. | 2015-01-20 | Oxid. Cat.(Catalytic Converter): Oxidative Catalyst | Alliance Source Testing | 1775 HP | 1.18lbs/hr, 4.0g/hp-hr | 1686 HP | 0.009 lb/hr, 0.003 g/hp-hr | 10 | CO - Carbon Monoxide | PP | NA | Y | Our facility descriptions have the engines numbered incorrectly, however the Manufacture dates correspond across both the report and permit. P013 is engine 3 onsite (10 in the permit), P006-P012 onsite are C4-C10, but in the permit 3-9. However if you follow only ***(EU P###)*** everything is accurate.
2015 | 125 | 0210012002 | Utica Gas Services, LLC-Carrollton Compressor Facility | 2098 Panda Road SE | Carrollton | 44615 |  | Carroll | P004 | 1,775 HP natural gas-fired Caterpillar G3606 engine #1 equipped with an oxidation catalyst. | 2015-01-21 | Oxid. Cat.(Catalytic Converter): Oxidative Catalyst | Alliance Source Testing | 1775 HP | 1.18lbs/hr, 4.0g/hp-hr | 1686 HP | 0.009 lb/hr, 0.003 g/hp-hr | 10 | CO - Carbon Monoxide | PP | NA | Y | Our facility descriptions have the engines numbered incorrectly, however the Manufacture dates correspond across both the report and permit. P013 is engine 3 onsite (10 in the permit), P006-P012 onsite are C4-C10, but in the permit 3-9. However if you follow only ***(EU P###)*** everything is accurate.
2015 | 128 | 0210012002 | Utica Gas Services, LLC-Carrollton Compressor Facility | 2098 Panda Road SE | Carrollton | 44615 |  | Carroll | P004 | 1,775 HP natural gas-fired Caterpillar G3606 engine #1 equipped with an oxidation catalyst. | 2015-01-22 | Oxid. Cat.(Catalytic Converter): Oxidative Catalyst | Alliance Source Testing | 1775 HP | 1.18lbs/hr, 4.0g/hp-hr | 1686 HP | 0.009 lb/hr, 0.003 g/hp-hr | 10 | CO - Carbon Monoxide | PP | NA | Y | Our facility descriptions have the engines numbered incorrectly, however the Manufacture dates correspond across both the report and permit. P013 is engine 3 onsite (10 in the permit), P006-P012 onsite are C4-C10, but in the permit 3-9. However if you follow only ***(EU P###)*** everything is accurate.
2015 | 133 | 0210012002 | Utica Gas Services, LLC-Carrollton Compressor Facility | 2098 Panda Road SE | Carrollton | 44615 |  | Carroll | P005 | 1,775 HP natural gas-fired Caterpillar G3606 engine #2 equipped with an oxidation catalyst | 2015-01-20 | Oxid. Cat.(Catalytic Converter): Oxidative Catalyst | Alliance Source Testing | 1775 HP | 1.18lbs/hr, 4.0g/hp-hr | 1686 HP | 0.010 lb/hr, 0.0003 g/hp-hr | 10 | CO - Carbon Monoxide | PP | NA | Y | Our facility descriptions have the engines numbered incorrectly, however the Manufacture dates correspond across both the report and permit. P013 is engine 3 onsite (10 in the permit), P006-P012 onsite are C4-C10, but in the permit 3-9. However if you follow only ***(EU P###)*** everything is accurate.
2015 | 174 | 0210012002 | Utica Gas Services, LLC-Carrollton Compressor Facility | 2098 Panda Road SE | Carrollton | 44615 |  | Carroll | P005 | 1,775 HP natural gas-fired Caterpillar G3606 engine #2 equipped with an oxidation catalyst | 2015-01-21 | Oxid. Cat.(Catalytic Converter): Oxidative Catalyst | Alliance Source Testing | 1775 HP | 1.18lbs/hr, 4.0g/hp-hr | 1686 HP | 0.010 lb/hr, 0.0003 g/hp-hr | 10 | CO - Carbon Monoxide | PP | NA | Y | Our facility descriptions have the engines numbered incorrectly, however the Manufacture dates correspond across both the report and permit. P013 is engine 3 onsite (10 in the permit), P006-P012 onsite are C4-C10, but in the permit 3-9. However if you follow only ***(EU P###)*** everything is accurate.
2015 | 178 | 0210012002 | Utica Gas Services, LLC-Carrollton Compressor Facility | 2098 Panda Road SE | Carrollton | 44615 |  | Carroll | P005 | 1,775 HP natural gas-fired Caterpillar G3606 engine #2 equipped with an oxidation catalyst | 2015-01-22 | Oxid. Cat.(Catalytic Converter): Oxidative Catalyst | Alliance Source Testing | 1775 HP | 1.18lbs/hr, 4.0g/hp-hr | 1686 HP | 0.010 lb/hr, 0.0003 g/hp-hr | 10 | CO - Carbon Monoxide | PP | NA | Y | Our facility descriptions have the engines numbered incorrectly, however the Manufacture dates correspond across both the report and permit. P013 is engine 3 onsite (10 in the permit), P006-P012 onsite are C4-C10, but in the permit 3-9. However if you follow only ***(EU P###)*** everything is accurate.
2015 | 181 | 0661005020 | Rockies Express Pipeline - Seneca Compressor Station | Seneca Lake Rd | Quaker City | 43773 |  | Noble | P004 | compressor engine | 2015-05-18 | Engine 5(Catalytic Converter): Compressor Engine 5 Catalytic Convertor; Engine 4(Catalytic Converter): Compressor Engine 4 Catalytic Convertor; | Compressor Engineering Cort. | 5000 hp | 0.154 g/hp-hr | 4728 hp | 0.011 g/hp-hr | 6348 03 | CO - Carbon Monoxide | PP | NA | Y
2015 | 221 | 0656005010 | Dominion East Ohio - Switzerland Compressor Station | German Ridge Road | Switzerland Twp. | 43942 |  | Monroe | P002 | 3550 Hp Natural gas-fired (4SLB) Caterpillar model 3612 LE DM5309-06 compressor engines equipped with catalytic reduction (three-way). | 2015-01-16 | AFR and catalyst controls | Air Compliance Consultants, Inc. | 3,550 hp | 0.22 g/hp-hr | 3,292 hp | 0.018 g/hp-hr | 6348 03 | CO - Carbon Monoxide | PP | NA | Y | Method 320 actually used for testing.
2015 | 226 | 0607015007 | Humphreys Compressor Station | Johnson Ridge Rd | Barnesville | 43713 |  | Belmont | P003 | Compressor Engine #1 - Caterpillar G3612TA - natural gas fired four-stroke, lean burn internal combustion engine rated at an operating capacity of 3,550 horsepower equipped with a double oxidation catalyst. | 2015-04-15 | CC003(Catalytic Converter): Compressor Engine #3 - Oxidation Catalyst | Air Hygiene, Inc. | 3550 hp | 2.0 g/hp-hr | 3294 hp | 0.02 g/hp-hr | 10 | CO - Carbon Monoxide | PP | NA | Y
2015 | 227 | 0634005033 | Harrison West Compressor Station | Possum Hollow Road | Freeport | 43973 |  | Harrison | P003 | Compressor Engine #3 - 1980 HP (15.43 MMBtu/hr) Waukesha P9390 - natural gas-fired four-stroke rich burn internal combustion engine equipped with a three-way oxidation catalyst controlling CH2O, CO, NOx, & VOCs by 80, 97, 98.5 & 66 percent respectively | 2015-05-26 | CC003(Catalytic Converter): Compressor Engine #3 - 3-way Catalyst | Air Hygiene International, Inc. | 1980 hp | 2.0 g/hp-hr | 1661 hp | 0.02 g/hp-hr | 10 | CO - Carbon Monoxide | PP | NA | Y
2015 | 231 | 0607005016 | Barnesville West Compressor Station | Hwy 801 | Warren Twp. | 43713 |  | Belmont | P008 | Compressor Engine #3 - Natural gas-fired four-stroke lean burn (4SLB) internal combustion engine rated at an operating capacity of 2,370 horsepower (hp) and equipped with an oxidation catalyst | 2015-03-26 | CC003(Catalytic Converter): Compressor Engine #3 Catalytic Converter | Air Hygiene International, Inc | 2,370 hp | 0.14 g/hp-hr | 2,174 hp | 0.03 g/hp-hr | 10 | CO - Carbon Monoxide | PP | NA | Y
2015 | 234 | 0607005016 | Barnesville West Compressor Station | Hwy 801 | Warren Twp. | 43713 |  | Belmont | P010 | Compressor Engine #5 - Natural gas-fired four-stroke lean burn (4SLB) internal combustion engine rated at an operating capacity of 2,370 horsepower (hp) and equipped with an oxidation catalyst | 2015-03-27 | CC005(Catalytic Converter): Compressor Engine #5 Catalytic Converter | Air Hygiene International, Inc | 2,370 hp | 0.14 g/hp-hr | 2,204 hp | 0.03 g/hp-hr | 10 | CO - Carbon Monoxide | PP | NA | Y
2015 | 235 | 0607015007 | Humphreys Compressor Station | Johnson Ridge Rd | Barnesville | 43713 |  | Belmont | P002 | Compressor Engine #1 - Caterpillar G3612TA - natural gas fired four-stroke, lean burn internal combustion engine rated at an operating capacity of 3,550 horsepower equipped with a double oxidation catalyst. | 2015-04-14 | CC002(Catalytic Converter): Compressor Engine #2 - Oxidation Catalyst | Air Hygiene, Inc. | 3550 hp | 2.0 g/hp-hr | 3307 hp | 0.03 g/hp-hr | 10 | CO - Carbon Monoxide | PP | NA | Y
2015 | 237 | 0634005034 | Lake Compressor Station | County Highway 21 | Freeport | 43973 |  | Harrison | P005 | Compressor Engine #5 - 1980 HP (15.43 MMBtu/hr) Waukesha P9390 - natural gas-fired four-stroke rich burn internal combustion engine equipped with a three-way oxidation catalyst controlling CH2O, CO, NOx, & VOCs by 80, 97, 98.5 & 66 percent respectively | 2015-04-16 | CC005(Catalytic Converter): Compressor Engine #5 - 3-way Catalyst; | Air Hygiene, Inc. | 1980 hp | 2.0 g/hp-hr | 1617 hp | 0.03 g/hp-hr | 10 | CO - Carbon Monoxide | PP | NA | Y
2015 | 239 | 0634005034 | Lake Compressor Station | County Highway 21 | Freeport | 43973 |  | Harrison | P004 | Compressor Engine #4 - 1980 HP (15.43 MMBtu/hr) Waukesha P9390 - natural gas-fired four-stroke rich burn internal combustion engine equipped with a three-way oxidation catalyst controlling CH2O, CO, NOx, & VOCs by 80, 97, 98.5 & 66 percent respectively | 2015-04-17 | CC004(Catalytic Converter): Compressor Engine #4 - 3-way Catalyst | Air Hygiene, Inc. | 1980 hp | 2.0 g/hp-hr | 1626 hp | 0.03 g/hp-hr | 10 | CO - Carbon Monoxide | PP | NA | Y
2015 | 242 | 0607005016 | Barnesville West Compressor Station | Hwy 801 | Warren Twp. | 43713 |  | Belmont | P006 | Compressor Engine #1 - Natural gas-fired four-stroke lean burn (4SLB) internal combustion engine rated at an operating capacity of 2,370 horsepower (hp) and equipped with an oxidation catalyst | 2015-03-25 | CC001(Catalytic Converter): Compressor Engine #1 Catalytic Converter | Air Hygiene Internatinal, Inc | 2370 hp | 0.14 g/hp-hr | 2179 hp | 0.04 g/hp-hr | 10 | CO - Carbon Monoxide | PP | NA | Y
2015 | 245 | 0607005016 | Barnesville West Compressor Station | Hwy 801 | Warren Twp. | 43713 |  | Belmont | P007 | Compressor Engine #1 - Natural gas-fired four-stroke lean burn (4SLB) internal combustion engine rated at an operating capacity of 2,370 horsepower (hp) and equipped with an oxidation catalyst | 2015-03-25 | CC002(Catalytic Converter): Compressor Engine #2 Catalytic Converter | Air Hygiene International, Inc | 2,370 hp | 0.14 g/hp-hr | 2,199 hp | 0.04 g/hp-hr | 10 | CO - Carbon Monoxide | PP | NA | Y
2015 | 249 | 0607005016 | Barnesville West Compressor Station | Hwy 801 | Warren Twp. | 43713 |  | Belmont | P011 | Compressor Engine #6 - Natural gas-fired four-stroke lean burn (4SLB) internal combustion engine rated at an operating capacity of 2,370 horsepower (hp) and equipped with an oxidation catalyst | 2015-03-27 | CC006(Catalytic Converter): Compressor Engine #6 Catalytic Converter | Air Hygiene International, Inc | 2,370 hp | 0.14 g/hp-hr | 2,309 hp | 0.04 g/hp-hr | 10 | CO - Carbon Monoxide | PP | NA | Y
2015 | 252 | 0634005056 | Scio Compressor Station | 37650 Bower Rd | Scio | 43988 |  | Harrison | P002 | Compressor Engine #2 - 1,775 HP Caterpillar G3606 (4S-LB) - natural gas-fired four-cycle lean burn internal combustion engine equipped with an oxidation catalyst controlling CO & VOC emissions | 2015-06-23 | CC002(Catalytic Converter): Compressor Engine #2 - Oxidation Catalyst | Alliance Source Testing | 1775 hp | 0.30 g/hp-hr | 1598 hp | 0.04 g/hp-hr | 10 | CO - Carbon Monoxide | PP | NA | Y
2015 | 255 | 0661005027 | E2 Appalachian LLC - Batesville | 58380 St John Rd | Quaker City | 43773 |  | Noble | P003 | 1,680 Hp. Waukesha (L7044GSI) natural gas-fired, rich burn, turbocharged, with oxidation catalyst, compressor engine | 2015-01-27 | C2701C(Catalytic Converter): Engine Catalyst | E2 Energy Services | 1680 hp | 2.0 g/hp-hr | 1277 hp | 0.04 g/hp-hr | 6348 03 | CO - Carbon Monoxide | PP | NA | Y
2015 | 259 | 0630005042 | Gulfport Energy - Miller Well Pad | Jasper Rd | Londonderry Twp. | 43973 |  | Guernsey | P002 | One 50-hp Zenith ZPP416 and one 203-hp Caterpillar G3306B NA natural gas-fired engines for compressors. One or multiple stationary natural gas-fired spark ignition (SI) internal combustion engines (ICE) wiht a combined total horsepower (HP) or no more than 1,800 HP for the site. | 2015-06-26 | catalyst | Great Plains Analytical Services | 118 hp | 4.0 g/hp-hr | 87 hp | 0.043 g/hp-hr | 6348 03 | CO - Carbon Monoxide | PP | NA | N
2015 | 261 | 0661005020 | Rockies Express Pipeline - Seneca Compressor Station | Seneca Lake Rd | Quaker City | 43773 |  | Noble | P005 | compressor engine | 2015-05-18 | Engine 5(Catalytic Converter): Compressor Engine 5 Catalytic Convertor; Engine 4(Catalytic Converter): Compressor Engine 4 Catalytic Convertor; | Compressor Engineering Cort. | 5000 hp | 0.154 g/hp-hr | 4761 hp | 0.0469 g/hp-hr | 6348 03 | CO - Carbon Monoxide | PP | NA | Y
2015 | 263 | 0634005033 | Harrison West Compressor Station | Possum Hollow Road | Freeport | 43973 |  | Harrison | P007 | Compressor Engine #7 - 1980 HP (15.43 MMBtu/hr) Waukesha P9390 - natural gas-fired four-stroke rich burn internal combustion engine equipped with a three-way oxidation catalyst controlling CH2O, CO, NOx, & VOCs by 80, 97, 98.5 & 66 percent respectively | 2015-05-28 | CC007(Catalytic Converter): Compressor Engine #7 - 3-way Catalyst | Air Hygiene International, Inc. | 1980 hp | 2.0 g/hp-hr | 1586 hp | 0.06 g/hp-hr | 10 | CO - Carbon Monoxide | PP | NA | Y
2015 | 266 | 0634005056 | Scio Compressor Station | 37650 Bower Rd | Scio | 43988 |  | Harrison | P009 | Compressor Engine #9 - 1,775 HP Caterpillar G3606 (4S-LB) - natural gas-fired four-cycle lean burn internal combustion engine equipped with an oxidation catalyst controlling CO & VOC emissions | 2015-07-01 | CC009(Catalytic Converter): Compressor Engine #9 - Oxidation Catalyst | Alliance Source Testing | 1775 hp | 0.30 g/hp-hr | 1728 hp | 0.06 g/hp-hr | 10 | CO - Carbon Monoxide | PP | NA | Y
2015 | 271 | 0634005103 | Gulfport Energy - Davidson | Possom Hollow Rd | Freeport | 43977 |  | Harrison | P002 | One or multiple stationary natural gas-fired spark ignition (SI) internal combustion engines (ICE) with a combined total horsepower (HP) of no more than 1,000 HP for the site.* Includes 2007 and later model year engines manufactured after the applicable effective date identified in 40 CFR 60.4230(a)(3); and engines manufactured before the effective date of the NSPS, where compliance with the Part 60 Subpart JJJJ emissions standards for the same size engine can be met by retrofitting the engine with a control device and demonstrated through stack testing. | 2015-06-24 | catalyst | Great Plains Analytical Services | 118 hp | 4.0 g/hp-hr | 83 hp | 0.06 g/hp-hr | 6348 03 | CO - Carbon Monoxide | PP | NA | Y
2015 | 274 | 0634005027 | Arrowhead Compressor Station | E of Clements Rd and S of Jockey Hollow | Athens Twp. | 43977 |  | Harrison | P006 | Compressor Engine #3 - Caterpillar G3608 - natural gas fired four-stroke, lean burn internal combustion engine rated at an operating capacity of 2,370 horsepower equipped with a catalytic convertor. | 2015-04-13 | CC003(Catalytic Converter): Compressor Engine #3 Catalytic Convertor; CC004(Catalytic Converter): Compressor Engine #4 Catalytic Convertor | Air Hygiene, Inc. | 2370 hp | 0.14 g/hp-hr | 2223 hp | 0.07 g/hp-hr | 10 | CO - Carbon Monoxide | PP | NA | Y
2015 | 276 | 0634005034 | Lake Compressor Station | County Highway 21 | Freeport | 43973 |  | Harrison | P001 | Compressor Engine #1 - 1480 HP (11.39 MMBtu/hr) Waukesha L7042 - natural gas-fired four-stroke rich burn internal combustion engine equipped with a three-way oxidation catalyst controlling CH2O, CO, NOx, & VOCs by 80, 97, 98.5 & 66 percent respectively | 2015-04-16 | CC001(Catalytic Converter): Compressor Engine #1 - 3-way Catalyst | Air Hygiene, Inc. | 1480 hp | 2.0 g/hp-hr | 1207 hp | 0.07 g/hp-hr | 10 | CO - Carbon Monoxide | PP | NA | Y
2015 | 278 | 0661005027 | E2 Appalachian LLC - Batesville | 58380 St John Rd | Quaker City | 43773 |  | Noble | P001 | 1,680 Hp. Waukesha (L7044GSI) natural gas-fired, rich burn, turbocharged, with oxidation catalyst, compressor engine | 2015-01-26 | C2701C(Catalytic Converter): Engine Catalyst | E2 Energy Services | 1680 hp | 2.0 g/hp-hr | 1400 hp | 0.07 g/hp-hr | 6348 03 | CO - Carbon Monoxide | PP | NA | Y
2015 | 282 | 0661005020 | Rockies Express Pipeline - Seneca Compressor Station | Seneca Lake Rd | Quaker City | 43773 |  | Noble | P003 | compressor engine 3 | 2015-05-19 | Engine 3(Catalytic Converter): Compressor Engine 1 catalytic converter | Compressor Engineering Cort. | 2250hp | 2.0 g/hp-hr | 2212 hp | 0.0787 g/hp-hr | 6348 03 | CO - Carbon Monoxide | PP | NA | Y
2015 | 286 | 0634005027 | Arrowhead Compressor Station | E of Clements Rd and S of Jockey Hollow | Athens Twp. | 43977 |  | Harrison | P007 | Compressor Engine #4 - Caterpillar G3608 - natural gas fired four-stroke, lean burn internal combustion engine rated at an operating capacity of 2,370 horsepower equipped with a catalytic convertor | 2015-04-13 | CC003(Catalytic Converter): Compressor Engine #3 Catalytic Convertor; CC004(Catalytic Converter): Compressor Engine #4 Catalytic Convertor | Air Hygiene, Inc. | 2370 hp | 0.14 g/hp-hr | 2180 hp | 0.08 g/hp-hr | 10 | CO - Carbon Monoxide | PP | NA | Y
2015 | 287 | 0634005056 | Scio Compressor Station | 37650 Bower Rd | Scio | 43988 |  | Harrison | P003 | Compressor Engine #3 - 1,775 HP Caterpillar G3606 (4S-LB) - natural gas-fired four-cycle lean burn internal combustion engine equipped with an oxidation catalyst controlling CO & VOC emissions | 2015-06-22 | CC003(Catalytic Converter): Compressor Engine #3 - Oxidation Catalyst | Alliance Source Testing | 1775 hp | 0.30 g/hp-hr | 1615 hp | 0.08 g/hp-hr | 10 | CO - Carbon Monoxide | PP | NA | Y
2015 | 291 | 0634005056 | Scio Compressor Station | 37650 Bower Rd | Scio | 43988 |  | Harrison | P008 | Compressor Engine #8 - 1,775 HP Caterpillar G3606 (4S-LB) - natural gas-fired four-cycle lean burn internal combustion engine equipped with an oxidation catalyst controlling CO & VOC emissions | 2015-06-23 | CC008(Catalytic Converter): Compressor Engine #8 - Oxidation Catalyst | Alliance Source Testing | 1775 hp | 0.30 g/hp-hr | 1598 hp | 0.08 g/hp-hr | 10 | CO - Carbon Monoxide | PP | NA | Y
2015 | 294 | 0634005056 | Scio Compressor Station | 37650 Bower Rd | Scio | 43988 |  | Harrison | P005 | Compressor Engine #5 - 1,775 HP Caterpillar G3606 (4S-LB) - natural gas-fired four-cycle lean burn internal combustion engine equipped with an oxidation catalyst controlling CO & VOC emissions | 2015-07-01 | CC005(Catalytic Converter): Compressor Engine #5 - Oxidation Catalyst | Alliance Source Testing | 1775 hp | 0.30 g/hp-hr | 1621 hp | 0.08 g/hp-hr | 10 | CO - Carbon Monoxide | PP | NA | Y
2015 | 297 | 0661005008 | Seneca Gas Plant | Zep Road | Summerfield | 43788 |  | Noble | P001 | Compressor Engine #1 - Natural gas-fired four-stroke lean burn (4SLB) internal combustion engine rated at an operating capacity of 4,735 horsepower (hp) and equipped with an oxidation catalyst. | 2015-04-27 | CC001(Catalytic Converter): Compressor Engine #1 - Catalyic Convertor; CC002(Catalytic Converter): Compressor Engine #2 - Catalytic Convertor | Air Hygiene, Inc | 4735 hp | 0.14 g/hp-hr | 4125 hp | 0.08 g/hp-hr | 10 | CO - Carbon Monoxide | PP | NA | Y
2015 | 300 | 0634005033 | Harrison West Compressor Station | Possum Hollow Road | Freeport | 43973 |  | Harrison | P005 | Compressor Engine #5 - 1980 HP (15.43 MMBtu/hr) Waukesha P9390 - natural gas-fired four-stroke rich burn internal combustion engine equipped with a three-way oxidation catalyst controlling CH2O, CO, NOx, & VOCs by 80, 97, 98.5 & 66 percent respectively | 2015-05-27 | CC005(Catalytic Converter): Compressor Engine #5 - 3-way Catalyst | Air Hygiene International, Inc. | 1980 hp | 2.0 g/hp-hr | 1650 hp | 0.09 g/hp-hr | 10 | CO - Carbon Monoxide | PP | NA | Y
2015 | 303 | 0634005033 | Harrison West Compressor Station | Possum Hollow Road | Freeport | 43973 |  | Harrison | P006 | Compressor Engine #6 - 1980 HP (15.43 MMBtu/hr) Waukesha P9390 - natural gas-fired four-stroke rich burn internal combustion engine equipped with a three-way oxidation catalyst controlling CH2O, CO, NOx, & VOCs by 80, 97, 98.5 & 66 percent respectively | 2015-05-28 | CC006(Catalytic Converter): Compressor Engine #6 - 3-way Catalyst | Air Hygiene International, Inc. | 1980 hp | 2.0 g/hp-hr | 1573 hp | 0.09 g/hp-hr | 10 | CO - Carbon Monoxide | PP | NA | Y
2015 | 306 | 0634005056 | Scio Compressor Station | 37650 Bower Rd | Scio | 43988 |  | Harrison | P006 | Compressor Engine #6 - 1,775 HP Caterpillar G3606 (4S-LB) - natural gas-fired four-cycle lean burn internal combustion engine equipped with an oxidation catalyst controlling CO & VOC emissions | 2015-06-22 | CC006(Catalytic Converter): Compressor Engine #6 - Oxidation Catalyst | Alliance Source Testing | 1775 hp | 0.30 g/hp-hr | 1609 hp | 0.09 g/hp-hr | 10 | CO - Carbon Monoxide | PP | NA | Y
2015 | 310 | 0634005056 | Scio Compressor Station | 37650 Bower Rd | Scio | 43988 |  | Harrison | P004 | Compressor Engine #4 - 1,775 HP Caterpillar G3606 (4S-LB) - natural gas-fired four-cycle lean burn internal combustion engine equipped with an oxidation catalyst controlling CO & VOC emissions | 2015-07-01 | CC004(Catalytic Converter): Compressor Engine #4 - Oxidation Catalyst | Alliance Source Testing | 1775 hp | 0.30 g/hp-hr | 1609 hp | 0.09 g/hp-hr | 10 | CO - Carbon Monoxide | PP | NA | Y
2015 | 339 | 0661005020 | Rockies Express Pipeline - Seneca Compressor Station | Seneca Lake Rd | Quaker City | 43773 |  | Noble | P001 | Natural gas fired 4 stroke rich burn compressor engine, Waukesha VHP-L7042GSI, controlled by air/fuel ratio and nonselective catalytic reduction (NSCR) | 2015-03-03 | Engine 1(Catalytic Converter): Compressor Engine 1 catalytic converter; Engine 2(Catalytic Converter): Compressor Engine 2 catalytic converter | Compressor Engineering Corp. | 1480 hp | 4.0 g/hp-hr | 1574 hp | 0.1 g/hp-hr | 6348 03 | CO - Carbon Monoxide | PP | NA | Y
2015 | 395 | 0634005034 | Lake Compressor Station | County Highway 21 | Freeport | 43973 |  | Harrison | P011 | Compressor Engine #9 - Waukesha L7042 - natural gas fired four-stroke, rich burn internal combustion engine rated at an operating capacity of 1,480 horsepower equipped with a three-way oxidation catalyst. | 2015-04-16 | CC011(Catalytic Converter): Compressor Engine #9 - 3-way Catalyst | Air Hygiene, Inc. | 1480 hp | 2.0 g/hp-hr | 1166 hp | 0.10 g/hp-hr | 10 | CO - Carbon Monoxide | PP | NA | Y
2015 | 397 | 0634005056 | Scio Compressor Station | 37650 Bower Rd | Scio | 43988 |  | Harrison | P007 | Compressor Engine #7 - 1,775 HP Caterpillar G3606 (4S-LB) - natural gas-fired four-cycle lean burn internal combustion engine equipped with an oxidation catalyst controlling CO & VOC emissions | 2015-07-01 | CC007(Catalytic Converter): Compressor Engine #7 - Oxidation Catalyst | Alliance Source Testing | 1775 hp | 0.30 g/hp-hr | 1722 hp | 0.10 g/hp-hr | 10 | CO - Carbon Monoxide | PP | NA | Y
2015 | 400 | 0634005056 | Scio Compressor Station | 37650 Bower Rd | Scio | 43988 |  | Harrison | P001 | Compressor Engine #1 - 1,775 HP Caterpillar G3606 (4S-LB) - natural gas-fired four-cycle lean burn internal combustion engine equipped with an oxidation catalyst controlling CO & VOC emissions. | 2015-07-02 | CC001(Catalytic Converter): Compressor Engine #1 - Oxidation Catalyst | Alliance Source Testing | 1775 hp | 0.30 g/hp-hr | 1745 hp | 0.10 g/hp-hr | 10 | CO - Carbon Monoxide | PP | NA | Y
2015 | 404 | 0634005034 | Lake Compressor Station | County Highway 21 | Freeport | 43973 |  | Harrison | P002 | Compressor Engine #2 - 1480 HP (11.39 MMBtu/hr) Waukesha L7042 - natural gas-fired four-stroke rich burn internal combustion engine equipped with a three-way oxidation catalyst controlling CH2O, CO, NOx, & VOCs by 80, 97, 98.5 & 66 percent respectively | 2015-04-17 | CC002(Catalytic Converter): Compressor Engine #2 - 3-way Catalyst | Air Hygiene, Inc. | 1480 hp | 2.0 g/hp-hr | 1114 hp | 0.10 g/hp--hr | 10 | CO - Carbon Monoxide | PP | NA | Y
2015 | 406 | 0210012002 | Utica Gas Services, LLC-Carrollton Compressor Facility | 2098 Panda Road SE | Carrollton | 44615 |  | Carroll | P006 | 1,775 HP natural gas-fired Caterpillar G3606 engine #3 equipped with an oxidation catalyst | 2015-01-20 | Oxid. Cat.(Catalytic Converter): Oxidative Catalyst | Alliance Source Testing | 1775 HP | 1.18lbs/hr, 2.0g/hp-hr | 1597 HP | 0.10 lb/hr, 0.03 g/hp-hr | 10 | CO - Carbon Monoxide | PP | NA | Y | Our facility descriptions have the engines numbered incorrectly, however the Manufacture dates correspond across both the report and permit. P013 is engine 3 onsite (10 in the permit), P006-P012 onsite are C4-C10, but in the permit 3-9. However if you follow only ***(EU P###)*** everything is accurate.
2015 | 410 | 0210012002 | Utica Gas Services, LLC-Carrollton Compressor Facility | 2098 Panda Road SE | Carrollton | 44615 |  | Carroll | P011 | 1,775 HP natural gas-fired Caterpillar G3606 engine #8 equipped with an oxidation catalyst | 2015-01-20 | Oxid. Cat.(Catalytic Converter): Oxidative Catalyst | Alliance Source Testing | 1775 HP | 1.18lbs/hr, 2.0g/hp-hr | 1639 HP | 0.10 lb/hr, 0.03 g/hp-hr | 10 | CO - Carbon Monoxide | PP | NA | Y | Our facility descriptions have the engines numbered incorrectly, however the Manufacture dates correspond across both the report and permit. P013 is engine 3 onsite (10 in the permit), P006-P012 onsite are C4-C10, but in the permit 3-9. However if you follow only ***(EU P###)*** everything is accurate.
2015 | 412 | 0210012002 | Utica Gas Services, LLC-Carrollton Compressor Facility | 2098 Panda Road SE | Carrollton | 44615 |  | Carroll | P012 | 1,775 HP natural gas-fired Caterpillar G3606 engine #9 equipped with an oxidation catalyst | 2015-01-20 | Oxid. Cat.(Catalytic Converter): Oxidative Catalyst | Alliance Source Testing | 1775 HP | 1.18lbs/hr, 2.0g/hp-hr | 1656 HP | 0.10 lb/hr, 0.03 g/hp-hr | 10 | CO - Carbon Monoxide | PP | NA | Y | Our facility descriptions have the engines numbered incorrectly, however the Manufacture dates correspond across both the report and permit. P013 is engine 3 onsite (10 in the permit), P006-P012 onsite are C4-C10, but in the permit 3-9. However if you follow only ***(EU P###)*** everything is accurate.
2015 | 414 | 0210012002 | Utica Gas Services, LLC-Carrollton Compressor Facility | 2098 Panda Road SE | Carrollton | 44615 |  | Carroll | P006 | 1,775 HP natural gas-fired Caterpillar G3606 engine #3 equipped with an oxidation catalyst | 2015-01-21 | Oxid. Cat.(Catalytic Converter): Oxidative Catalyst | Alliance Source Testing | 1775 HP | 1.18lbs/hr, 2.0g/hp-hr | 1597 HP | 0.10 lb/hr, 0.03 g/hp-hr | 10 | CO - Carbon Monoxide | PP | NA | Y | Our facility descriptions have the engines numbered incorrectly, however the Manufacture dates correspond across both the report and permit. P013 is engine 3 onsite (10 in the permit), P006-P012 onsite are C4-C10, but in the permit 3-9. However if you follow only ***(EU P###)*** everything is accurate.
2015 | 419 | 0210012002 | Utica Gas Services, LLC-Carrollton Compressor Facility | 2098 Panda Road SE | Carrollton | 44615 |  | Carroll | P011 | 1,775 HP natural gas-fired Caterpillar G3606 engine #8 equipped with an oxidation catalyst | 2015-01-21 | Oxid. Cat.(Catalytic Converter): Oxidative Catalyst | Alliance Source Testing | 1775 HP | 1.18lbs/hr, 2.0g/hp-hr | 1639 HP | 0.10 lb/hr, 0.03 g/hp-hr | 10 | CO - Carbon Monoxide | PP | NA | Y | Our facility descriptions have the engines numbered incorrectly, however the Manufacture dates correspond across both the report and permit. P013 is engine 3 onsite (10 in the permit), P006-P012 onsite are C4-C10, but in the permit 3-9. However if you follow only ***(EU P###)*** everything is accurate.
2015 | 422 | 0210012002 | Utica Gas Services, LLC-Carrollton Compressor Facility | 2098 Panda Road SE | Carrollton | 44615 |  | Carroll | P012 | 1,775 HP natural gas-fired Caterpillar G3606 engine #9 equipped with an oxidation catalyst | 2015-01-21 | Oxid. Cat.(Catalytic Converter): Oxidative Catalyst | Alliance Source Testing | 1775 HP | 1.18lbs/hr, 2.0g/hp-hr | 1656 HP | 0.10 lb/hr, 0.03 g/hp-hr | 10 | CO - Carbon Monoxide | PP | NA | Y | Our facility descriptions have the engines numbered incorrectly, however the Manufacture dates correspond across both the report and permit. P013 is engine 3 onsite (10 in the permit), P006-P012 onsite are C4-C10, but in the permit 3-9. However if you follow only ***(EU P###)*** everything is accurate.
2015 | 423 | 0210012002 | Utica Gas Services, LLC-Carrollton Compressor Facility | 2098 Panda Road SE | Carrollton | 44615 |  | Carroll | P006 | 1,775 HP natural gas-fired Caterpillar G3606 engine #3 equipped with an oxidation catalyst | 2015-01-22 | Oxid. Cat.(Catalytic Converter): Oxidative Catalyst | Alliance Source Testing | 1775 HP | 1.18lbs/hr, 2.0g/hp-hr | 1597 HP | 0.10 lb/hr, 0.03 g/hp-hr | 10 | CO - Carbon Monoxide | PP | NA | Y | Our facility descriptions have the engines numbered incorrectly, however the Manufacture dates correspond across both the report and permit. P013 is engine 3 onsite (10 in the permit), P006-P012 onsite are C4-C10, but in the permit 3-9. However if you follow only ***(EU P###)*** everything is accurate.
2015 | 424 | 0210012002 | Utica Gas Services, LLC-Carrollton Compressor Facility | 2098 Panda Road SE | Carrollton | 44615 |  | Carroll | P011 | 1,775 HP natural gas-fired Caterpillar G3606 engine #8 equipped with an oxidation catalyst | 2015-01-22 | Oxid. Cat.(Catalytic Converter): Oxidative Catalyst | Alliance Source Testing | 1775 HP | 1.18lbs/hr, 2.0g/hp-hr | 1639 HP | 0.10 lb/hr, 0.03 g/hp-hr | 10 | CO - Carbon Monoxide | PP | NA | Y | Our facility descriptions have the engines numbered incorrectly, however the Manufacture dates correspond across both the report and permit. P013 is engine 3 onsite (10 in the permit), P006-P012 onsite are C4-C10, but in the permit 3-9. However if you follow only ***(EU P###)*** everything is accurate.
2015 | 433 | 0210012002 | Utica Gas Services, LLC-Carrollton Compressor Facility | 2098 Panda Road SE | Carrollton | 44615 |  | Carroll | P012 | 1,775 HP natural gas-fired Caterpillar G3606 engine #9 equipped with an oxidation catalyst | 2015-01-22 | Oxid. Cat.(Catalytic Converter): Oxidative Catalyst | Alliance Source Testing | 1775 HP | 1.18lbs/hr, 2.0g/hp-hr | 1656 HP | 0.10 lb/hr, 0.03 g/hp-hr | 10 | CO - Carbon Monoxide | PP | NA | Y | Our facility descriptions have the engines numbered incorrectly, however the Manufacture dates correspond across both the report and permit. P013 is engine 3 onsite (10 in the permit), P006-P012 onsite are C4-C10, but in the permit 3-9. However if you follow only ***(EU P###)*** everything is accurate.
2015 | 438 | 0634005108 | Gulfport Energy - Vozar | McElhaney Rd | Freeport | 43973 |  | Harrison | P002 | One or multiple stationary natural gas-fired spark ignition (SI) internal combustion engines (ICE) with a combined total horsepower (HP) of no more than 1,000 HP for the site.* Includes 2007 and later model year engines manufactured after the applicable effective date identified in 40 CFR 60.4230(a)(3); and engines manufactured before the effective date of the NSPS, where compliance with the Part 60 Subpart JJJJ emissions standards for the same size engine can be met by retrofitting the engine with a control device and demonstrated through stack testing. | 2015-06-25 | catalyst | Great Plains Analytical | 118 hp | 4.0 g/hp-hr | 92 hp | 0.101 g/hp-hr | 6348 03 | CO - Carbon Monoxide | PP | NA | Y
2015 | 441 | 0634005033 | Harrison West Compressor Station | Possum Hollow Road | Freeport | 43973 |  | Harrison | P004 | Compressor Engine #4 - 1980 HP (15.43 MMBtu/hr) Waukesha P9390 - natural gas-fired four-stroke rich burn internal combustion engine equipped with a three-way oxidation catalyst controlling CH2O, CO, NOx, & VOCs by 80, 97, 98.5 & 66 percent respectively | 2015-05-27 | CC004(Catalytic Converter): Compressor Engine #4 - 3-way Catalyst | Air Hygiene International, Inc. | 1980 hp | 2.0 g/hp-hr | 1636 hp | 0.11 g/hp-hr | 10 | CO - Carbon Monoxide | PP | NA | Y
2015 | 442 | 0634005056 | Scio Compressor Station | 37650 Bower Rd | Scio | 43988 |  | Harrison | P010 | Compressor Engine #10 - 1,775 HP Caterpillar G3606 (4S-LB) - natural gas-fired four-cycle lean burn internal combustion engine equipped with an oxidation catalyst controlling CO & VOC emissions | 2015-06-23 | CC010(Catalytic Converter): Compressor Engine #10 - Oxidation Catalyst | Alliance Source Testing | 1775 hp | 0.30 g/hp-hr | 1598 hp | 0.11 g/hp-hr | 10 | CO - Carbon Monoxide | PP | NA | Y
2015 | 446 | 0661005008 | Seneca Gas Plant | Zep Road | Summerfield | 43788 |  | Noble | P002 | Compressor Engine #2 - Natural gas-fired four-stroke lean burn (4SLB) internal combustion engine rated at an operating capacity of 4,735 horsepower (hp) and equipped with an oxidation catalyst. | 2015-04-27 | CC001(Catalytic Converter): Compressor Engine #1 - Catalyic Convertor; CC002(Catalytic Converter): Compressor Engine #2 - Catalytic Convertor | Air Hygiene, Inc | 4735 hp | 0.14 g/hp-hr | 4075 hp | 0.11 g/hp-hr | 10 | CO - Carbon Monoxide | PP | NA | Y
2015 | 447 | 0634005048 | Gulfport Energy- Boy Scout Well Pad | 79900 Adams Rd | Tippecanoe | 44699 |  | Harrison | P002 | One 60 hp Waukesha 310 and one 64 hp HEC 3491-OPV natural gas engines for compressors | 2015-06-23 | catalyst | Great Plains Analytical Services | 118 hp | 4.0 g/hp-hr | 92 hp | 1.228 g/hp-hr | 6348 03 | CO - Carbon Monoxide | PP | NA | Y | 118 hp Cummins engine, serial number 46639148
2015 | 450 | 0634005049 | Gulfport Energy- Ryser #1-25H Well Pad | 77100 Scott Hill Road | Flushing | 43977 |  | Harrison | P002 | One or multiple stationary natural gas-fired spark ignition (SI) internal combustion engines (ICE) with a combined total horsepower (HP) of no more than 1,800 HP for the site. | 2015-06-24 | catalyst | Great Plains Analytical Services | 425 hp | 4.0 g/hp-hr | 353 hp | 1.367 g/hp-hr | 6348 03 | CO - Carbon Monoxide | PP | NA | Y
2015 | 455 | 0285000388 | East Ohio Gas Company - Paint | STATE RTE 250 | Wooster | 44624 |  | Wayne | B002 | Natural gas fired Internal Combustion Engine with max input capacity of 11.9 MMBtu/hr - Caterpillar G3516TALE with 1340 HP, 4-stroke, selective catalytic reduction (SCR) | 2015-07-14 | Three way Catalyst; CatOx(Catalytic Converter): Catalytic oxidizer for Engine 2 | Environmental Quality Management | 1340 HP | 540 ppm @ 15% O2 and 4.0 g/hp-hr | 1236 HP or 92.2 | 3.3 ppm @ 15% O2 and 0.025 g/hp-hr | 10 | CO - Carbon Monoxide | PP | NA | Y
2015 | 476 | 0661005027 | E2 Appalachian LLC - Batesville | 58380 St John Rd | Quaker City | 43773 |  | Noble | P004 | 1,680 Hp. Waukesha (L7044GSI) natural gas-fired, rich burn, turbocharged, with oxidation catalyst, compressor engine | 2015-02-20 | C2704C(Catalytic Converter): Engine Catalyst | E2 Energy Services | 1,680 hp | 2.0 g/hp-hr | 1,510 hp | 0.11 g/hp-hr | 6348 03 | CO - Carbon Monoxide | PP | NA | Y
2015 | 523 | 0210012002 | Utica Gas Services, LLC-Carrollton Compressor Facility | 2098 Panda Road SE | Carrollton | 44615 |  | Carroll | P013 | 1,775 HP natural gas-fired Caterpillar G3606 engine #10equipped with an oxidation catalyst | 2015-01-20 | Oxid. Cat.(Catalytic Converter): Oxidative Catalyst | Alliance Source Testing | 1775 HP | 1.18lbs/hr, 2.0g/hp-hr | 1660 HP | 0.12 lb/hr, 0.03 g/hp-hr | 10 | CO - Carbon Monoxide | PP | NA | Y | Our facility descriptions have the engines numbered incorrectly, however the Manufacture dates correspond across both the report and permit. P013 is engine 3 onsite (10 in the permit), P006-P012 onsite are C4-C10, but in the permit 3-9. However if you follow only ***(EU P###)*** everything is accurate.
2015 | 524 | 0210012002 | Utica Gas Services, LLC-Carrollton Compressor Facility | 2098 Panda Road SE | Carrollton | 44615 |  | Carroll | P013 | 1,775 HP natural gas-fired Caterpillar G3606 engine #10equipped with an oxidation catalyst | 2015-01-21 | Oxid. Cat.(Catalytic Converter): Oxidative Catalyst | Alliance Source Testing | 1775 HP | 1.18lbs/hr, 2.0g/hp-hr | 1660 HP | 0.12 lb/hr, 0.03 g/hp-hr | 10 | CO - Carbon Monoxide | PP | NA | Y | Our facility descriptions have the engines numbered incorrectly, however the Manufacture dates correspond across both the report and permit. P013 is engine 3 onsite (10 in the permit), P006-P012 onsite are C4-C10, but in the permit 3-9. However if you follow only ***(EU P###)*** everything is accurate.
2015 | 525 | 0210012002 | Utica Gas Services, LLC-Carrollton Compressor Facility | 2098 Panda Road SE | Carrollton | 44615 |  | Carroll | P013 | 1,775 HP natural gas-fired Caterpillar G3606 engine #10equipped with an oxidation catalyst | 2015-01-22 | Oxid. Cat.(Catalytic Converter): Oxidative Catalyst | Alliance Source Testing | 1775 HP | 1.18lbs/hr, 2.0g/hp-hr | 1660 HP | 0.12 lb/hr, 0.03 g/hp-hr | 10 | CO - Carbon Monoxide | PP | NA | Y | Our facility descriptions have the engines numbered incorrectly, however the Manufacture dates correspond across both the report and permit. P013 is engine 3 onsite (10 in the permit), P006-P012 onsite are C4-C10, but in the permit 3-9. However if you follow only ***(EU P###)*** everything is accurate.
2015 | 526 | 0630005043 | Gulfport Energy - Ripley Well Pad | Shipley Rd | Londonderry Twp. | 43973 |  | Guernsey | P002 | One 50-hp Zenith ZPP416 and one 203-hp Caterpillar G3306B NA natural gas-fired engines for compressors. One or multiple stationary natural gas-fired spark ignition (SI) internal combustion engines (ICE) wiht a combined total horsepower (HP) or no more than 1,800 HP for the site. | 2015-03-20 | NSCR | Great Plains Analytical Services | 118 hp | 2.0 g/hp-hr | 118 hp | 0.137 g/hp-hr | 6348 03 | CO - Carbon Monoxide | PP | NA | Y
2015 | 527 | 0634005033 | Harrison West Compressor Station | Possum Hollow Road | Freeport | 43973 |  | Harrison | P001 | Compressor Engine #1 - 1480 HP (11.39 MMBtu/hr) Waukesha L7042 - natural gas-fired four-stroke rich burn internal combustion engine equipped with a three-way oxidation catalyst controlling CH2O, CO, NOx, & VOCs by 80, 97, 98.5 & 66 percent respectively | 2015-05-26 | CC001(Catalytic Converter): Compressor Engine #1 - 3-way Catalyst | Air Hygiene International, Inc. | 1480 hp | 2.0 g/hp-hr | 1165 hp | 0.14 g/hp-hr | 10 | CO - Carbon Monoxide | PP | NA | Y
2015 | 531 | 0661005027 | E2 Appalachian LLC - Batesville | 58380 St John Rd | Quaker City | 43773 |  | Noble | P002 | 1,680 Hp. Waukesha (L7044GSI) natural gas-fired, rich burn, turbocharged, with oxidation catalyst, compressor engine | 2015-01-26 | C2701C(Catalytic Converter): Engine Catalyst | E2 Energy Services | 1680 hp | 2.0 g/hp-hr | 1361 hp | 0.16 g/hp-hr | 6348 03 | CO - Carbon Monoxide | PP | NA | Y
2015 | 533 | 0634005069 | Gulfport Energy - Arrowhead II - Darla | 65800 Mt. Olivett Road | Flushing | 43977 |  | Harrison | P002 | One or multiple stationary natural gas-fired spark ignition (SI) internal combustion engines (ICE) with a combined total horsepower (HP) of no more than 1,800 HP for the site.* Includes 2007 and later model year engines manufactured after the applicable effective date identified in 40 CFR 60.4230(a)(3) and engines manufactured before the NSPS effective date where compliance with the Part 60 Subpart JJJJ emissions standards for the same size engine can be demonstrated through stack testing. | 2015-03-19 | NSCR | Great Plains Analytical | 118 hp | 2.0 g/hp-hr | 99 hp | 0.161 g/hp-hr | 6348 03 | CO - Carbon Monoxide | PP | NA | Y
2015 | 534 | 0661005027 | E2 Appalachian LLC - Batesville | 58380 St John Rd | Quaker City | 43773 |  | Noble | P007 | 1,680 Hp. Waukesha (L7044GSI) natural gas-fired, rich burn, turbocharged, with oxidation catalyst, compressor engine | 2015-02-19 | C2707C(Catalytic Converter): Engine Catalyst | E2 Energy Services | 1,680 hp | 2.0 g/hp-hr | 1,512 hp | 0.18 g/hp-hr | 6348 03 | CO - Carbon Monoxide | PP | NA | Y
2015 | 535 | 0607015003 | Gulfport Energy- Shugert 12 Well Pad | 65800 Mt. Olivett Road | Barnesville | 43713 |  | Belmont | P002 | One or multiple stationary natural gas-fired spark ignition (SI) internal combustion engines (ICE) with a combined total horsepower (HP) of no more than 1,800 HP for the site. | 2015-06-25 | none | Great Plains Services | 118 hp | 4.0 g/hp-hr | 91 hp | 0.185 g/hp-hr | 6348 03 | CO - Carbon Monoxide | PP | NA | Y
2015 | 536 | 0607005016 | Barnesville West Compressor Station | Hwy 801 | Warren Twp. | 43713 |  | Belmont | P009 | Compressor Engine #4 - Natural gas-fired four-stroke lean burn (4SLB) internal combustion engine rated at an operating capacity of 2,370 horsepower (hp) and equipped with an oxidation catalyst | 2015-03-26 | CC004(Catalytic Converter): Compressor Engine #4 Catalytic Converter | Air Hygiene International, Inc | 2,370 hp | 0.14 g/hp-hr | 2,188 hp | 0.2 g/hp-hr | 10 | CO - Carbon Monoxide | PP | NA | Y
2015 | 554 | 0210012002 | Utica Gas Services, LLC-Carrollton Compressor Facility | 2098 Panda Road SE | Carrollton | 44615 |  | Carroll | P010 | 1,775 HP natural gas-fired Caterpillar G3606 engine #7 equipped with an oxidation catalyst | 2015-01-20 | Oxid. Cat.(Catalytic Converter): Oxidative Catalyst | Alliance Source Testing | 1775 HP | 1.18lbs/hr, 2.0g/hp-hr | 1636 HP | 0.21 lb/hr, 0.10 g/hp-hr | 10 | CO - Carbon Monoxide | PP | NA | Y | Our facility descriptions have the engines numbered incorrectly, however the Manufacture dates correspond across both the report and permit. P013 is engine 3 onsite (10 in the permit), P006-P012 onsite are C4-C10, but in the permit 3-9. However if you follow only ***(EU P###)*** everything is accurate.
2015 | 584 | 0210012002 | Utica Gas Services, LLC-Carrollton Compressor Facility | 2098 Panda Road SE | Carrollton | 44615 |  | Carroll | P010 | 1,775 HP natural gas-fired Caterpillar G3606 engine #7 equipped with an oxidation catalyst | 2015-01-21 | Oxid. Cat.(Catalytic Converter): Oxidative Catalyst | Alliance Source Testing | 1775 HP | 1.18lbs/hr, 2.0g/hp-hr | 1636 HP | 0.21 lb/hr, 0.10 g/hp-hr | 10 | CO - Carbon Monoxide | PP | NA | Y | Our facility descriptions have the engines numbered incorrectly, however the Manufacture dates correspond across both the report and permit. P013 is engine 3 onsite (10 in the permit), P006-P012 onsite are C4-C10, but in the permit 3-9. However if you follow only ***(EU P###)*** everything is accurate.
2015 | 586 | 0210012002 | Utica Gas Services, LLC-Carrollton Compressor Facility | 2098 Panda Road SE | Carrollton | 44615 |  | Carroll | P010 | 1,775 HP natural gas-fired Caterpillar G3606 engine #7 equipped with an oxidation catalyst | 2015-01-22 | Oxid. Cat.(Catalytic Converter): Oxidative Catalyst | Alliance Source Testing | 1775 HP | 1.18lbs/hr, 2.0g/hp-hr | 1636 HP | 0.21 lb/hr, 0.10 g/hp-hr | 10 | CO - Carbon Monoxide | PP | NA | Y | Our facility descriptions have the engines numbered incorrectly, however the Manufacture dates correspond across both the report and permit. P013 is engine 3 onsite (10 in the permit), P006-P012 onsite are C4-C10, but in the permit 3-9. However if you follow only ***(EU P###)*** everything is accurate.
2015 | 694 | 0634005090 | E2 Ohio Compression LLC - Mizer | 84500 Addy Rd | Cadiz | 43907 |  | Harrison | P002 | One or multiple stationary natural gas-fired spark ignition (SI) internal combustion engines (ICE) with a combined total horsepower (HP) of no more than 1,800 HP for the site. Includes 2007 and later model year engines manufactured after the applicable effective date identified in 40 CFR 60.4230(a)(3) and engines manufactured before the NSPS effective date where compliance with the Part 60 Subpart JJJJ emission standards for the same size engine can be demonstrated through stack testing | 2015-02-12 | Cat01(Catalytic Converter): Oxidation Catalyst for 4SLB RICE | E2 Energy Services | 680 hp | 4.0 g/hp-hr | 675 hp | 0.22 g/hp-hr | 6348 03 | CO - Carbon Monoxide | PP | NA | Y
2015 | 697 | 0661005027 | E2 Appalachian LLC - Batesville | 58380 St John Rd | Quaker City | 43773 |  | Noble | P008 | 1,680 Hp. Waukesha (L7044GSI) natural gas-fired, rich burn, turbocharged, with oxidation catalyst, compressor engine | 2015-02-19 | C2708C(Catalytic Converter): Engine Catalyst | E2 Energy Services | 1,680 hp | 2.0 g/hp-hr | 1,512 hp | 0.24 g/hp-hr | 6348 03 | CO - Carbon Monoxide | PP | NA | Y
2015 | 698 | 0661005027 | E2 Appalachian LLC - Batesville | 58380 St John Rd | Quaker City | 43773 |  | Noble | P005 | 1,680 Hp. Waukesha (L7044GSI) natural gas-fired, rich burn, turbocharged, with oxidation catalyst, compressor engine | 2015-02-27 | C2705C(Catalytic Converter): Engine Catalyst | E2 Energy Services | 1,680 hp | 2.0 g/hp-hr | 1,295 hp | 0.30 g/hp-hr | 6348 03 | CO - Carbon Monoxide | PP | NA | Y
2015 | 701 | 0210012002 | Utica Gas Services, LLC-Carrollton Compressor Facility | 2098 Panda Road SE | Carrollton | 44615 |  | Carroll | P007 | 1,775 HP natural gas-fired Caterpillar G3606 engine #4 equipped with an oxidation catalyst | 2015-01-20 | Oxid. Cat.(Catalytic Converter): Oxidative Catalyst | Alliance Source Testing | 1775 HP | 1.18lbs/hr, 2.0g/hp-hr | 1599 HP | 0.30 lb/hr, 0.10 g/hp-hr | 10 | CO - Carbon Monoxide | PP | NA | Y | Our facility descriptions have the engines numbered incorrectly, however the Manufacture dates correspond across both the report and permit. P013 is engine 3 onsite (10 in the permit), P006-P012 onsite are C4-C10, but in the permit 3-9. However if you follow only ***(EU P###)*** everything is accurate.
2015 | 706 | 0210012002 | Utica Gas Services, LLC-Carrollton Compressor Facility | 2098 Panda Road SE | Carrollton | 44615 |  | Carroll | P007 | 1,775 HP natural gas-fired Caterpillar G3606 engine #4 equipped with an oxidation catalyst | 2015-01-21 | Oxid. Cat.(Catalytic Converter): Oxidative Catalyst | Alliance Source Testing | 1775 HP | 1.18lbs/hr, 2.0g/hp-hr | 1599 HP | 0.30 lb/hr, 0.10 g/hp-hr | 10 | CO - Carbon Monoxide | PP | NA | Y | Our facility descriptions have the engines numbered incorrectly, however the Manufacture dates correspond across both the report and permit. P013 is engine 3 onsite (10 in the permit), P006-P012 onsite are C4-C10, but in the permit 3-9. However if you follow only ***(EU P###)*** everything is accurate.
2015 | 707 | 0210012002 | Utica Gas Services, LLC-Carrollton Compressor Facility | 2098 Panda Road SE | Carrollton | 44615 |  | Carroll | P007 | 1,775 HP natural gas-fired Caterpillar G3606 engine #4 equipped with an oxidation catalyst | 2015-01-22 | Oxid. Cat.(Catalytic Converter): Oxidative Catalyst | Alliance Source Testing | 1775 HP | 1.18lbs/hr, 2.0g/hp-hr | 1599 HP | 0.30 lb/hr, 0.10 g/hp-hr | 10 | CO - Carbon Monoxide | PP | NA | Y | Our facility descriptions have the engines numbered incorrectly, however the Manufacture dates correspond across both the report and permit. P013 is engine 3 onsite (10 in the permit), P006-P012 onsite are C4-C10, but in the permit 3-9. However if you follow only ***(EU P###)*** everything is accurate.
2015 | 712 | 0630005042 | Gulfport Energy - Miller Well Pad | Jasper Rd | Londonderry Twp. | 43973 |  | Guernsey | P002 | One 50-hp Zenith ZPP416 and one 203-hp Caterpillar G3306B NA natural gas-fired engines for compressors. One or multiple stationary natural gas-fired spark ignition (SI) internal combustion engines (ICE) wiht a combined total horsepower (HP) or no more than 1,800 HP for the site. | 2015-06-27 | catalyst | Great Plains Analytical Services | 118 hp | 4.0 g/hp-hr | 85 hp | 0.334 g/hp-hr | 6348 03 | CO - Carbon Monoxide | PP | NA | N | test date was actually 6-26-2015. To input data for engines that share a P002 number you have to change date or something. If I use 6-26-2015 information will not be accepted because these two engine both are P002 unit numbers-tow engines with hp of less than 1800 hp for site
2015 | 715 | 0634005103 | Gulfport Energy - Davidson | Possom Hollow Rd | Freeport | 43977 |  | Harrison | P002 | One or multiple stationary natural gas-fired spark ignition (SI) internal combustion engines (ICE) with a combined total horsepower (HP) of no more than 1,000 HP for the site.* Includes 2007 and later model year engines manufactured after the applicable effective date identified in 40 CFR 60.4230(a)(3); and engines manufactured before the effective date of the NSPS, where compliance with the Part 60 Subpart JJJJ emissions standards for the same size engine can be met by retrofitting the engine with a control device and demonstrated through stack testing. | 2015-03-19 | NSCR | Great Plains Analytical Service | 118 hp | 2.0 g/hp-hr | 101 hp | 0.339 g/hp-hr | 6348 03 | CO - Carbon Monoxide | PP | NA | Y
2015 | 717 | 0634005101 | Chesapeake Exploration LLC - Trushell 8-13-6 Pad | OH-151E Scio Bowerston Rd | Scio | 43988 |  | Harrison | P002 | One or multiple stationary natural gas-fired spark ignition (SI) internal combustion engines (ICE) with a combined total horsepower (HP) of no more than 1,800 HP for the site.* Includes 2007 and later model year engines manufactured after the applicable effective date identified in 40 CFR 60.4230(a)(3); and engines manufactured before the effective date of the NSPS, where compliance with the Part 60 Subpart JJJJ emissions standards for the same size engine can be met by retrofitting the engine with a control device and demonstrated through stack testing. | 2015-04-29 | NSCR | Alliance Source Testing | 211 hp | 4.0 g/hp-hr | 192 hp | 0.38 g/hp-hr | 10 | CO - Carbon Monoxide | PP | NA | Y
2015 | 719 | 0210012002 | Utica Gas Services, LLC-Carrollton Compressor Facility | 2098 Panda Road SE | Carrollton | 44615 |  | Carroll | P009 | 1,775 HP natural gas-fired Caterpillar G3606 engine #6 equipped with an oxidation catalyst | 2015-01-20 | Oxid. Cat.(Catalytic Converter): Oxidative Catalyst | Alliance Source Testing | 1775 HP | 1.18lbs/hr, 2.0g/hp-hr | 1656 HP | 0.44 lb/hr, 0.10 g/hp-hr | 10 | CO - Carbon Monoxide | PP | NA | Y | Our facility descriptions have the engines numbered incorrectly, however the Manufacture dates correspond across both the report and permit. P013 is engine 3 onsite (10 in the permit), P006-P012 onsite are C4-C10, but in the permit 3-9. However if you follow only ***(EU P###)*** everything is accurate.
2015 | 739 | 0210012002 | Utica Gas Services, LLC-Carrollton Compressor Facility | 2098 Panda Road SE | Carrollton | 44615 |  | Carroll | P009 | 1,775 HP natural gas-fired Caterpillar G3606 engine #6 equipped with an oxidation catalyst | 2015-01-21 | Oxid. Cat.(Catalytic Converter): Oxidative Catalyst | Alliance Source Testing | 1775 HP | 1.18lbs/hr, 2.0g/hp-hr | 1656 HP | 0.44 lb/hr, 0.10 g/hp-hr | 10 | CO - Carbon Monoxide | PP | NA | Y | Our facility descriptions have the engines numbered incorrectly, however the Manufacture dates correspond across both the report and permit. P013 is engine 3 onsite (10 in the permit), P006-P012 onsite are C4-C10, but in the permit 3-9. However if you follow only ***(EU P###)*** everything is accurate.
2015 | 742 | 0210012002 | Utica Gas Services, LLC-Carrollton Compressor Facility | 2098 Panda Road SE | Carrollton | 44615 |  | Carroll | P009 | 1,775 HP natural gas-fired Caterpillar G3606 engine #6 equipped with an oxidation catalyst | 2015-01-22 | Oxid. Cat.(Catalytic Converter): Oxidative Catalyst | Alliance Source Testing | 1775 HP | 1.18lbs/hr, 2.0g/hp-hr | 1656 HP | 0.44 lb/hr, 0.10 g/hp-hr | 10 | CO - Carbon Monoxide | PP | NA | Y | Our facility descriptions have the engines numbered incorrectly, however the Manufacture dates correspond across both the report and permit. P013 is engine 3 onsite (10 in the permit), P006-P012 onsite are C4-C10, but in the permit 3-9. However if you follow only ***(EU P###)*** everything is accurate.
2015 | 747 | 0210012002 | Utica Gas Services, LLC-Carrollton Compressor Facility | 2098 Panda Road SE | Carrollton | 44615 |  | Carroll | P008 | 1,775 HP natural gas-fired Caterpillar G3606 engine #5 equipped with an oxidation catalyst | 2015-01-20 | Oxid. Cat.(Catalytic Converter): Oxidative Catalyst | Alliance Source Testing | 1775 HP | 1.18lbs/hr, 2.0g/hp-hr | 1602 HP | 0.48 lb/hr, 0.10 g/hp-hr | 10 | CO - Carbon Monoxide | PP | NA | Y | Our facility descriptions have the engines numbered incorrectly, however the Manufacture dates correspond across both the report and permit. P013 is engine 3 onsite (10 in the permit), P006-P012 onsite are C4-C10, but in the permit 3-9. However if you follow only ***(EU P###)*** everything is accurate.
2015 | 754 | 0210012002 | Utica Gas Services, LLC-Carrollton Compressor Facility | 2098 Panda Road SE | Carrollton | 44615 |  | Carroll | P008 | 1,775 HP natural gas-fired Caterpillar G3606 engine #5 equipped with an oxidation catalyst | 2015-01-21 | Oxid. Cat.(Catalytic Converter): Oxidative Catalyst | Alliance Source Testing | 1775 HP | 1.18lbs/hr, 2.0g/hp-hr | 1602 HP | 0.48 lb/hr, 0.10 g/hp-hr | 10 | CO - Carbon Monoxide | PP | NA | Y | Our facility descriptions have the engines numbered incorrectly, however the Manufacture dates correspond across both the report and permit. P013 is engine 3 onsite (10 in the permit), P006-P012 onsite are C4-C10, but in the permit 3-9. However if you follow only ***(EU P###)*** everything is accurate.
2015 | 757 | 0210012002 | Utica Gas Services, LLC-Carrollton Compressor Facility | 2098 Panda Road SE | Carrollton | 44615 |  | Carroll | P008 | 1,775 HP natural gas-fired Caterpillar G3606 engine #5 equipped with an oxidation catalyst | 2015-01-22 | Oxid. Cat.(Catalytic Converter): Oxidative Catalyst | Alliance Source Testing | 1775 HP | 1.18lbs/hr, 2.0g/hp-hr | 1602 HP | 0.48 lb/hr, 0.10 g/hp-hr | 10 | CO - Carbon Monoxide | PP | NA | Y | Our facility descriptions have the engines numbered incorrectly, however the Manufacture dates correspond across both the report and permit. P013 is engine 3 onsite (10 in the permit), P006-P012 onsite are C4-C10, but in the permit 3-9. However if you follow only ***(EU P###)*** everything is accurate.
2015 | 761 | 0210002071 | Chesapeake Exploration LLC - Kennedy 14-13-5 Pad | OH-9 - Germano Rd | Harlem Springs | 43903 |  | Carroll | P002 | One or multiple stationary natural gas-fired spark ignition (SI) internal combustion engines (ICE) with a combined total horsepower (HP) of no more than 1,800 HP for the site.* Includes 2007 and later model year engines manufactured after the applicable effective date identified in 40 CFR 60.4230(a)(3); and engines manufactured before the effective date of the NSPS, where compliance with the Part 60 Subpart JJJJ emissions standards for the same size engine can be met by retrofitting the engine with a control device and demonstrated through stack testing. | 2015-08-11 | Catalyst | Alliance Source Testing | 630 HP | 540 ppmvd @ 15% O2 | 422 Hp | 0.5 ppmvd @ 15% O2 | 10 | CO - Carbon Monoxide | PP | NA | Y
2015 | 765 | 0634005071 | Gulfport Energy - County Line - Puskarich | 76015 Moorefield Hill Rd | Flushing | 43977 |  | Harrison | P002 | One or multiple stationary natural gas-fired spark ignition (SI) internal combustion engines (ICE) with a combined total horsepower (HP) of no more than 1,000 HP for the site.* Includes 2007 and later model year engines manufactured after the applicable effective date identified in 40 CFR 60.4230(a)(3); and engines manufactured before the effective date of the NSPS, where compliance with the Part 60 Subpart JJJJ emissions standards for the same size engine can be met by retrofitting the engine with a control device and demonstrated through stack testing. | 2015-03-17 | NSCR | Great Plains Analytical Services | 118 hp | 2.0 g/hp-hr | 103 hp | 0.50 g/hp-hr | 6348 03 | CO - Carbon Monoxide | PP | NA | Y
2015 | 766 | 0634005070 | Gulfport Energy - County Line II - Gustina-Bear | 34011 Cadiz-Piedmont Rd | Flushing | 43977 |  | Harrison | P002 | One or multiple stationary natural gas-fired spark ignition (SI) internal combustion engines (ICE) wiht a combined total horsepower (HP) of no more than 1,800 HP for the site. | 2015-03-18 | NSCR | Great Plains Analytical Services | 118 hp | 2.0 g/hp-hr | 57 hp | 0.521 g/hp-hr | 6348 03 | CO - Carbon Monoxide | PP | NA | N
2015 | 802 | 0250000911 | East Ohio Gas Company - Austintown | 9686 NEW ROAD | Austintown Twp. | 44451 | 9708 | Mahoning | B001 | Natural gas fired reciprocating internal combustion engine rated at 1265 HP (9.55 mmBtu/hr)-Caterpillar Model G3516LE, 4 stroke lean burn (4SLB) spark ignition (SI) internal combustion engine (ICE) with a Miratech catalytic converter; complying with emission limitations in 40 CFR 63, Subpart ZZZZ Table 2d #9; and installed before 6/12/06. | 2015-04-06 | Oxidative Catalyst 1(Other): B001 Catalytic Oxidizer; Oxidative Catalyst 2(Other): B002 Catalytic oxidizer | Environmental Quality Management | 1,265 Hp | 47 ppm @ 15% O2 | 1122.3 or 88.7% | 11.15 ppm @ 15% O2 | 10 | CO - Carbon Monoxide | PP | NA | Y
2015 | 805 | 0210012046 | Chesapeake Exploration LLC - Bauer 14-14-6 Pad | Autumn Road SW | Carrollton | 44615 |  | Carroll | P002 | Natural Gas Engines | 2015-04-28 | Catalyst | Alliance Source Testing, Inc. | 211 Hp | 270 ppmvd@ 15 % O2 | 194 Hp 91.9% | 13.1 ppmvd@ 15 % O2 | 10 | CO - Carbon Monoxide | PP | NA | Y
2015 | 807 | 0285000366 | East Ohio Gas - Chippewa Station | 17045 Galehouse Road | Doylestown | 44230 |  | Wayne | B010 | 2,370 hp 4SLB SI ICE; CAT G3608 | 2015-05-19 | Engine 5 Converter(Catalytic Converter): Engine #5; Cat B010(Catalytic Converter): Catalytic Converter for B010, engine #6; Catalytic(Catalytic Converter): Engine 7 Catalytic converter | Environmental Quality Management | 2370 Hp | 540 ppm @ 15% O2 or 4.0 g/bhp-hr 93%DE | 2225 Hp | 13.60 ppm @ 15% O2 or 0.11 g/bhp-hr 94.5%DE | 10 | CO - Carbon Monoxide | PP | NA | Y | B009-2.5 Catalyst Pressure and 880 degF Catalyst temp, B010-3.0 Catalyst Pressure and 880 degF Catalyst temp, B014-1.0 Catalyst Pressure and 870 degF Catalyst Temperature
2015 | 810 | 0285000366 | East Ohio Gas - Chippewa Station | 17045 Galehouse Road | Doylestown | 44230 |  | Wayne | B010 | 2,370 hp 4SLB SI ICE; CAT G3608 | 2015-05-20 | Engine 5 Converter(Catalytic Converter): Engine #5; Cat B010(Catalytic Converter): Catalytic Converter for B010, engine #6; Catalytic(Catalytic Converter): Engine 7 Catalytic converter | Environmental Quality Management | 2370 Hp | 540 ppm @ 15% O2 or 4.0 g/bhp-hr 93%DE | 2225 Hp | 13.60 ppm @ 15% O2 or 0.11 g/bhp-hr 94.5%DE | 10 | CO - Carbon Monoxide | PP | NA | Y | B009-2.5 Catalyst Pressure and 880 degF Catalyst temp, B010-3.0 Catalyst Pressure and 880 degF Catalyst temp, B014-1.0 Catalyst Pressure and 870 degF Catalyst Temperature
2015 | 813 | 0285000366 | East Ohio Gas - Chippewa Station | 17045 Galehouse Road | Doylestown | 44230 |  | Wayne | B010 | 2,370 hp 4SLB SI ICE; CAT G3608 | 2015-06-16 | Engine 5 Converter(Catalytic Converter): Engine #5; Cat B010(Catalytic Converter): Catalytic Converter for B010, engine #6; Catalytic(Catalytic Converter): Engine 7 Catalytic converter | Environmental Quality Management | 2370 Hp | 540 ppm @ 15% O2 or 4.0 g/bhp-hr 93%DE | 2225 Hp | 13.60 ppm @ 15% O2 or 0.11 g/bhp-hr 94.5%DE | 10 | CO - Carbon Monoxide | PP | NA | Y | B009-2.5 Catalyst Pressure and 880 degF Catalyst temp, B010-3.0 Catalyst Pressure and 880 degF Catalyst temp, B014-1.0 Catalyst Pressure and 870 degF Catalyst Temperature
2015 | 817 | 0250000911 | East Ohio Gas Company - Austintown | 9686 NEW ROAD | Austintown Twp. | 44451 | 9708 | Mahoning | B002 | Natural gas fired reciprocating internal combustion engine rated at 1265 HP (9.55 mmBtu/hr)-Caterpillar Model G3516LE, 4 stroke lean burn (4SLB) spark ignition (SI) internal combustion engine (ICE) with a Miratech catalytic converter; complying with emission limitations in 40 CFR 63, Subpart ZZZZ Table 2d #9; and installed before 6/12/06. | 2015-04-06 | Oxidative Catalyst 1(Other): B001 Catalytic Oxidizer; Oxidative Catalyst 2(Other): B002 Catalytic oxidizer | Environmental Quality Management | 1,265 Hp | 47 ppm @ 15% O2 | 1133 or 89.5% | 14.31 ppm @ 15% O2 | 10 | CO - Carbon Monoxide | PP | NA | Y
2015 | 894 | 0285000366 | East Ohio Gas - Chippewa Station | 17045 Galehouse Road | Doylestown | 44230 |  | Wayne | B014 | 2,370 hp 4SLB SI ICE: CAT 3608 w/catalyst | 2015-05-19 | Engine 5 Converter(Catalytic Converter): Engine #5; Cat B010(Catalytic Converter): Catalytic Converter for B010, engine #6; Catalytic(Catalytic Converter): Engine 7 Catalytic converter | Environmental Quality Management | 2370 Hp | 270 ppm @ 15% O2 or 2.0 g/bhp-hr 93%DE | 2241 Hp | 4.3 ppm @ 15% O2 or 0.03 g/bhp-hr 98.4% DE | 10 | CO - Carbon Monoxide | PP | NA | Y | B009-2.5 Catalyst Pressure and 880 degF Catalyst temp, B010-3.0 Catalyst Pressure and 880 degF Catalyst temp, B014-1.0 Catalyst Pressure and 870 degF Catalyst Temperature
2015 | 895 | 0285000366 | East Ohio Gas - Chippewa Station | 17045 Galehouse Road | Doylestown | 44230 |  | Wayne | B014 | 2,370 hp 4SLB SI ICE: CAT 3608 w/catalyst | 2015-05-20 | Engine 5 Converter(Catalytic Converter): Engine #5; Cat B010(Catalytic Converter): Catalytic Converter for B010, engine #6; Catalytic(Catalytic Converter): Engine 7 Catalytic converter | Environmental Quality Management | 2370 Hp | 270 ppm @ 15% O2 or 2.0 g/bhp-hr 93%DE | 2241 Hp | 4.3 ppm @ 15% O2 or 0.03 g/bhp-hr 98.4% DE | 10 | CO - Carbon Monoxide | PP | NA | Y | B009-2.5 Catalyst Pressure and 880 degF Catalyst temp, B010-3.0 Catalyst Pressure and 880 degF Catalyst temp, B014-1.0 Catalyst Pressure and 870 degF Catalyst Temperature
2015 | 900 | 0285000366 | East Ohio Gas - Chippewa Station | 17045 Galehouse Road | Doylestown | 44230 |  | Wayne | B014 | 2,370 hp 4SLB SI ICE: CAT 3608 w/catalyst | 2015-06-16 | Engine 5 Converter(Catalytic Converter): Engine #5; Cat B010(Catalytic Converter): Catalytic Converter for B010, engine #6; Catalytic(Catalytic Converter): Engine 7 Catalytic converter | Environmental Quality Management | 2370 Hp | 270 ppm @ 15% O2 or 2.0 g/bhp-hr 93%DE | 2241 Hp | 4.3 ppm @ 15% O2 or 0.03 g/bhp-hr 98.4% DE | 10 | CO - Carbon Monoxide | PP | NA | Y | B009-2.5 Catalyst Pressure and 880 degF Catalyst temp, B010-3.0 Catalyst Pressure and 880 degF Catalyst temp, B014-1.0 Catalyst Pressure and 870 degF Catalyst Temperature
2015 | 909 | 0285000366 | East Ohio Gas - Chippewa Station | 17045 Galehouse Road | Doylestown | 44230 |  | Wayne | B009 | 2,370 hp SI ICE pipeline compressor w/catalyst: CAT G3608-LE-TA | 2015-05-19 | Engine 5 Converter(Catalytic Converter): Engine #5; Cat B010(Catalytic Converter): Catalytic Converter for B010, engine #6; Catalytic(Catalytic Converter): Engine 7 Catalytic converter | Environmental Quality Management | 2370 Hp | 93% Destruction Efficiency | 2196.5 Hp | 97.5% Destruction | 10 | CO - Carbon Monoxide | PP | NA | Y | B009-2.5 Catalyst Pressure and 880 degF Catalyst temp, B010-3.0 Catalyst Pressure and 880 degF Catalyst temp, B014-1.0 Catalyst Pressure and 870 degF Catalyst Temperature
2015 | 911 | 0285000366 | East Ohio Gas - Chippewa Station | 17045 Galehouse Road | Doylestown | 44230 |  | Wayne | B009 | 2,370 hp SI ICE pipeline compressor w/catalyst: CAT G3608-LE-TA | 2015-05-20 | Engine 5 Converter(Catalytic Converter): Engine #5; Cat B010(Catalytic Converter): Catalytic Converter for B010, engine #6; Catalytic(Catalytic Converter): Engine 7 Catalytic converter | Environmental Quality Management | 2370 Hp | 93% Destruction Efficiency | 2196.5 Hp | 97.5% Destruction | 10 | CO - Carbon Monoxide | PP | NA | Y | B009-2.5 Catalyst Pressure and 880 degF Catalyst temp, B010-3.0 Catalyst Pressure and 880 degF Catalyst temp, B014-1.0 Catalyst Pressure and 870 degF Catalyst Temperature
2015 | 914 | 0285000366 | East Ohio Gas - Chippewa Station | 17045 Galehouse Road | Doylestown | 44230 |  | Wayne | B009 | 2,370 hp SI ICE pipeline compressor w/catalyst: CAT G3608-LE-TA | 2015-06-16 | Engine 5 Converter(Catalytic Converter): Engine #5; Cat B010(Catalytic Converter): Catalytic Converter for B010, engine #6; Catalytic(Catalytic Converter): Engine 7 Catalytic converter | Environmental Quality Management | 2370 Hp | 93% Destruction Efficiency | 2196.5 Hp | 97.5% Destruction | 10 | CO - Carbon Monoxide | PP | NA | Y | B009-2.5 Catalyst Pressure and 880 degF Catalyst temp, B010-3.0 Catalyst Pressure and 880 degF Catalyst temp, B014-1.0 Catalyst Pressure and 870 degF Catalyst Temperature
2016 | 290 | 0210002039 | Kilgore Compressor Station-Utica Gas Services, LLC | Pontiff Rd | Kilgore | 43988 |  | Carroll | P008 | 1,775 hp NG-fired 4SLB Stationary ICE equipped w/catalyst Caterpillar G3606: Serial Number: 4ZS01808 | 2016-12-02 | CC001(Catalytic Converter): Compressor Engine #1 - Oxidation Catalyst; CC002(Catalytic Converter): Compressor Engine #2 - Oxidation Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - Oxidation Catalyst; CC004(Catalytic Converter): Compressor Eng | Technical Compliance Solutions LLC | 1775 HP | 2.0g/hp-hr & 1.18lbs/hr | 1667 | 0..11 g/hp-hr & 0.399 lb/hr | 10 | CO - Carbon Monoxide | PP | Y | NA
2016 | 356 | 0607015007 | Humphreys Compressor Station | Johnson Ridge Rd | Barnesville | 43713 |  | Belmont | P003 | Compressor Engine #1 - Caterpillar G3612TA - natural gas fired four-stroke, lean burn internal combustion engine rated at an operating capacity of 3,550 horsepower equipped with a double oxidation catalyst. | 2016-04-12 | CC001(Catalytic Converter): Compressor Engine #1 - Oxidation Catalyst; CC002(Catalytic Converter): Compressor Engine #2 - Oxidation Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - Oxidation Catalyst | Air Hygiene, Inc | 3550 hp | 0.19 g/hp-hr | 3402 hp | 0.01 g/hp-hr | 10 | CO - Carbon Monoxide | PP | Y | NA
2016 | 363 | 0656005017 | Triad Hunter, LLC, Stalder Pad | 49947 Twp 724 | Sardis | 43946 |  | Monroe | P002 | Natural Gas Engines | 2016-03-04 | C003(Catalytic Converter): Oxidation Catalyst | EcoTest Energy Services | 630 hp | 2.00 g/hp-hr | 590 hp | 0.01 g/hp-hr | 320 | CO - Carbon Monoxide | PP | Y | NA
2016 | 377 | 0656005028 | Miller Compressor Station | 51103 Twp Rd 847 | Seneca Twp. | 43788 |  | Monroe | P004 | Waukesha 1680 bhp Model L7044GSI 4-stroke Natural Gas Rich Burn Gas Compressor Engine Model Year 2014 controlled by a catalyst | 2016-06-22 | C-2701C(Catalytic Converter): Engine Catalyst; C-2702C(Catalytic Converter): Engine Catalyst; C-2703C(Catalytic Converter): Engine Catalyst; C-2704C(Catalytic Converter): Engine Catalyst; C-2705C(Catalytic Converter): Engine Catalyst; C-2706C(Catalytic Co | Alliance Source Testing | 1680 hp | 0.5 g/hp-hr | 1680 hp | 0.01 g/hp-hr | 10 | CO - Carbon Monoxide | PP | N | NA
2016 | 378 | 0656005028 | Miller Compressor Station | 51103 Twp Rd 847 | Seneca Twp. | 43788 |  | Monroe | P008 | Waukesha 1680 bhp Model L7044GSI 4-stroke Natural Gas Rich Burn Gas Compressor Engine Model Year 2014 controlled by a catalyst | 2016-06-22 | C-2701C(Catalytic Converter): Engine Catalyst; C-2702C(Catalytic Converter): Engine Catalyst; C-2703C(Catalytic Converter): Engine Catalyst; C-2704C(Catalytic Converter): Engine Catalyst; C-2705C(Catalytic Converter): Engine Catalyst; C-2706C(Catalytic Co | Alliance Source Testing | 1680 hp | 0.5 g/hp-hr | 1680 hp | 0.01 g/hp-hr | 10 | CO - Carbon Monoxide | PP | N | NA
2016 | 379 | 0661005052 | Long Compressor Station | 55135 Batesville Rd | Quaker City | 43773 |  | Noble | P005 | 1,680 hp Waukesha 7044GSI NG Fired-rich burn-4stroke compressor engine | 2016-01-28 | C-01(Catalytic Converter): Non-selective catalyst reduction device for C-2000; C-02(Catalytic Converter): Non-selective catalyst reduction device for C-2100; C-03(Catalytic Converter): Non-selective catalyst reduction device for C-2200; C-04(Catalytic Con | Technical Compliance Solutions | 1680 hp | 2.00 g/hp-hr | 1628 hp | 0.01 g/hp-hr | 320 | CO - Carbon Monoxide | PP | Y | NA
2016 | 403 | 0661005052 | Long Compressor Station | 55135 Batesville Rd | Quaker City | 43773 |  | Noble | P007 | 1,680 hp Waukesha 7044GSI NG Fired-rich burn-4stroke compressor engine | 2016-01-28 | C-01(Catalytic Converter): Non-selective catalyst reduction device for C-2000; C-02(Catalytic Converter): Non-selective catalyst reduction device for C-2100; C-03(Catalytic Converter): Non-selective catalyst reduction device for C-2200; C-04(Catalytic Con | Technical Compliance Solutions | 1680 hp | 2.00 g/hp-hr | 1616 hp | 0.01 g/hp-hr | 320 | CO - Carbon Monoxide | PP | Y | NA
2016 | 405 | 0210012002 | Utica Gas Services, LLC-Carrollton Compressor Facility | 2098 Panda Road SE | Carrollton | 44615 |  | Carroll | P005 | 1,775 HP natural gas-fired Caterpillar G3606 engine #2 equipped with an oxidation catalyst | 2016-01-07 | Oxid. Cat.(Catalytic Converter): Oxidative Catalyst | Alliance Source Testing | 1775 HP | 1.18lbs/hr, 4.0g/hp-hr | 1737 HP | 0.010 lb/hr, 0.003 g/hp-hr | 10 | CO - Carbon Monoxide | PP | Y | NA
2016 | 406 | 0607005016 | Barnesville West Compressor Station | Hwy 801 | Warren Twp. | 43713 |  | Belmont | P009 | Compressor Engine #4 - Natural gas-fired four-stroke lean burn (4SLB) internal combustion engine rated at an operating capacity of 2,370 horsepower (hp) and equipped with an oxidation catalyst | 2016-03-22 | CC005(Catalytic Converter): Compressor Engine #5 Catalytic Converter; CC004(Catalytic Converter): Compressor Engine #4 Catalytic Converter; CC006(Catalytic Converter): Compressor Engine #6 Catalytic Converter | Air Hygiene, Inc. | 2370 hp | 0.14 g/hp-hr | 2198 hp | 0.02 g/hp-hr | 10 | CO - Carbon Monoxide | PP | Y | NA
2016 | 407 | 0607005016 | Barnesville West Compressor Station | Hwy 801 | Warren Twp. | 43713 |  | Belmont | P010 | Compressor Engine #5 - Natural gas-fired four-stroke lean burn (4SLB) internal combustion engine rated at an operating capacity of 2,370 horsepower (hp) and equipped with an oxidation catalyst | 2016-03-22 | CC005(Catalytic Converter): Compressor Engine #5 Catalytic Converter; CC004(Catalytic Converter): Compressor Engine #4 Catalytic Converter; CC006(Catalytic Converter): Compressor Engine #6 Catalytic Converter | Air Hygiene, Inc. | 2370 hp | 0.14 g/hp-hr | 2277 hp | 0.02 g/hp-hr | 10 | CO - Carbon Monoxide | PP | Y | NA
2016 | 408 | 0607005016 | Barnesville West Compressor Station | Hwy 801 | Warren Twp. | 43713 |  | Belmont | P011 | Compressor Engine #6 - Natural gas-fired four-stroke lean burn (4SLB) internal combustion engine rated at an operating capacity of 2,370 horsepower (hp) and equipped with an oxidation catalyst | 2016-03-22 | CC005(Catalytic Converter): Compressor Engine #5 Catalytic Converter; CC004(Catalytic Converter): Compressor Engine #4 Catalytic Converter; CC006(Catalytic Converter): Compressor Engine #6 Catalytic Converter | Air Hygiene, Inc. | 2370 hp | 0.14 g/hp-hr | 2281 hp | 0.02 g/hp-hr | 10 | CO - Carbon Monoxide | PP | Y | NA
2016 | 409 | 0607015007 | Humphreys Compressor Station | Johnson Ridge Rd | Barnesville | 43713 |  | Belmont | P001 | Compressor Engine #1 - Caterpillar G3612TA - natural gas fired four-stroke, lean burn internal combustion engine rated at an operating capacity of 3,550 horsepower equipped with a double oxidation catalyst. | 2016-04-12 | CC001(Catalytic Converter): Compressor Engine #1 - Oxidation Catalyst; CC002(Catalytic Converter): Compressor Engine #2 - Oxidation Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - Oxidation Catalyst | Air Hygiene, Inc | 3550 hp | 0.19 g/hp-hr | 3345 hp | 0.02 g/hp-hr | 10 | CO - Carbon Monoxide | PP | Y | NA
2016 | 410 | 0656005011 | Ormet Production Facility | 43879 St Rte 7 | Hannibal | 43931 |  | Monroe | P006 | CAT 3508BLE SI combustion engine 690 bhp | 2016-07-28 | catalyst | EcoTest Energy Services | 690 hp | 0.20 g/hp-hr | 670 hp | 0.02 g/hp-hr | 320 | CO - Carbon Monoxide | PP | Y | NA
2016 | 411 | 0656005011 | Ormet Production Facility | 43879 St Rte 7 | Hannibal | 43931 |  | Monroe | P001 | CAT 3516BLE SI combustion engine 1380 bhp | 2016-06-02 | CD-1(Catalytic Converter): Control Device for Compressor Engine-1 | EcoTest Energy Services | 1380 hp | 2.00 g/hp-hr | 850 hp | 0.02 g/hp-hr | 320 | CO - Carbon Monoxide | PP | Y | NA
2016 | 412 | 0661005052 | Long Compressor Station | 55135 Batesville Rd | Quaker City | 43773 |  | Noble | P003 | 1,680 hp Waukesha 7044GSI NG Fired-rich burn-4stroke compressor engine | 2016-01-28 | C-01(Catalytic Converter): Non-selective catalyst reduction device for C-2000; C-02(Catalytic Converter): Non-selective catalyst reduction device for C-2100; C-03(Catalytic Converter): Non-selective catalyst reduction device for C-2200; C-04(Catalytic Con | Technical Compliance Solutions | 1680 hp | 2.00 g/hp-hr | 1606 hp | 0.02 g/hp-hr | 320 | CO - Carbon Monoxide | PP | Y | NA
2016 | 413 | 0661005052 | Long Compressor Station | 55135 Batesville Rd | Quaker City | 43773 |  | Noble | P006 | 1,680 hp Waukesha 7044GSI NG Fired-rich burn-4stroke compressor engine | 2016-01-28 | C-01(Catalytic Converter): Non-selective catalyst reduction device for C-2000; C-02(Catalytic Converter): Non-selective catalyst reduction device for C-2100; C-03(Catalytic Converter): Non-selective catalyst reduction device for C-2200; C-04(Catalytic Con | Technical Compliance Solutions | 1680 hp | 2.00 g/hp-hr | 1623 hp | 0.02 g/hp-hr | 320 | CO - Carbon Monoxide | PP | Y | NA
2016 | 418 | 0210002039 | Kilgore Compressor Station-Utica Gas Services, LLC | Pontiff Rd | Kilgore | 43988 |  | Carroll | P002 | 1,775 hp NG-fired 4SLB Stationary ICE equipped w/catalyst Caterpillar G3606: Serial Number: 4ZS01796 | 2016-12-02 | CC001(Catalytic Converter): Compressor Engine #1 - Oxidation Catalyst; CC002(Catalytic Converter): Compressor Engine #2 - Oxidation Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - Oxidation Catalyst; CC004(Catalytic Converter): Compressor Eng | Technical Compliance Solutions LLC | 1775 HP | 2.0g/hp-hr & 1.18lbs/hr | 1664 | 0.047 g/hp-hr & 0.173 lb/hr | 10 | CO - Carbon Monoxide | PP | Y | NA
2016 | 423 | 0210002039 | Kilgore Compressor Station-Utica Gas Services, LLC | Pontiff Rd | Kilgore | 43988 |  | Carroll | P006 | 1,775 hp NG-fired 4SLB Stationary ICE equipped w/catalyst Caterpillar G3606: Serial Number: 4ZS01805 | 2016-12-02 | CC001(Catalytic Converter): Compressor Engine #1 - Oxidation Catalyst; CC002(Catalytic Converter): Compressor Engine #2 - Oxidation Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - Oxidation Catalyst; CC004(Catalytic Converter): Compressor Eng | Technical Compliance Solutions LLC | 1775 HP | 2.0g/hp-hr & 1.18lbs/hr | 1615 | 0.048 g/hp-hr & 0.169 lb/hr | 10 | CO - Carbon Monoxide | PP | Y | NA
2016 | 424 | 0607075002 | Ascent Resources - Utica, LLC - CHC Dutton (Wheeling) | 43125 Dutton Drive | Flushing | 43977 |  | Belmont | P007 | Natural Gas Compression engine | 2016-06-28 | Comp Engine(Catalytic Converter): Natural Gas Compressor Engine Catalytic Converter | EcoTest Energy Resources | 211 hp | 0.5 g/hp-hr | 139 hp | 0.05 g/hp-hr | 320 | CO - Carbon Monoxide | PP | Y | NA
2016 | 437 | 0656105005 | E2 Appalachian Compression LLC - Reusser | Twp Hwy 68 and Twp Hwy 66 | Woodsfield | 43793 |  | Monroe | P006 | 1680 Hp. natural gas rich burn compressor engine - Waukesha L7044GSI | 2016-07-14 | C-1(Catalytic Converter): Engine Catalyst; C-2(Catalytic Converter): Engine Catalyst; C-3(Catalytic Converter): Engine #3 Catalyst; C-4(Catalytic Converter): Engine #4 Catalyst; C-5(Catalytic Converter): Engine #5 Catalyst; C-6(Catalytic Converter): Engin | Alliance Source Testing | 1680 hp | 0.94 lb/hr | 1646 hp | 0.02 lb/hr | 10 | CO - Carbon Monoxide | PP | Y | NA
2016 | 480 | 0210012002 | Utica Gas Services, LLC-Carrollton Compressor Facility | 2098 Panda Road SE | Carrollton | 44615 |  | Carroll | P004 | 1,775 HP natural gas-fired Caterpillar G3606 engine #1 equipped with an oxidation catalyst. | 2016-01-07 | Oxid. Cat.(Catalytic Converter): Oxidative Catalyst | Alliance Source Testing | 1775 HP | 1.18lbs/hr, 4.0g/hp-hr | 1644 HP | 0.02 lb/hr, 0..01 g/hp-hr | 10 | CO - Carbon Monoxide | PP | Y | NA
2016 | 481 | 0210012002 | Utica Gas Services, LLC-Carrollton Compressor Facility | 2098 Panda Road SE | Carrollton | 44615 |  | Carroll | P010 | 1,775 HP natural gas-fired Caterpillar G3606 engine #7 equipped with an oxidation catalyst | 2016-01-07 | Oxid. Cat.(Catalytic Converter): Oxidative Catalyst | Alliance Source Testing | 1775 HP | 1.18lbs/hr, 2.0g/hp-hr | 1636 HP | 0.02 lb/hr, 0.09 g/hp-hr | 10 | CO - Carbon Monoxide | PP | Y | NA
2016 | 482 | 0607005016 | Barnesville West Compressor Station | Hwy 801 | Warren Twp. | 43713 |  | Belmont | P006 | Compressor Engine #1 - Natural gas-fired four-stroke lean burn (4SLB) internal combustion engine rated at an operating capacity of 2,370 horsepower (hp) and equipped with an oxidation catalyst | 2016-03-21 | CC001(Catalytic Converter): Compressor Engine #1 Catalytic Converter; CC002(Catalytic Converter): Compressor Engine #2 Catalytic Converter; CC003(Catalytic Converter): Compressor Engine #3 Catalytic Converter | Air Hygiene, Inc. | 2370 hp | 0.14 g/hp-hr | 2270 hp | 0.03 g/hp-hr | 10 | CO - Carbon Monoxide | PP | Y | NA
2016 | 483 | 0607015007 | Humphreys Compressor Station | Johnson Ridge Rd | Barnesville | 43713 |  | Belmont | P002 | Compressor Engine #1 - Caterpillar G3612TA - natural gas fired four-stroke, lean burn internal combustion engine rated at an operating capacity of 3,550 horsepower equipped with a double oxidation catalyst. | 2016-04-12 | CC001(Catalytic Converter): Compressor Engine #1 - Oxidation Catalyst; CC002(Catalytic Converter): Compressor Engine #2 - Oxidation Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - Oxidation Catalyst | Air Hygiene, Inc | 3550 hp | 0.19 g/hp-hr | 3318 hp | 0.03 g/hp-hr | 10 | CO - Carbon Monoxide | PP | Y | NA
2016 | 484 | 0634005027 | Arrowhead Compressor Station | E of Clements Rd and S of Jockey Hollow | Athens Twp. | 43977 |  | Harrison | P010 | Compressor Engine #7 - Caterpillar G3608 - natural gas fired four-stroke, lean burn internal combustion engine rated at an operating capacity of 2,370 horsepower equipped with a catalytic convertor | 2016-11-01 | CC07(Catalytic Converter): Compressor Engine #7 Catalytic Convertor; CC008(Catalytic Converter): Compressor Engine #8 Catalytic Convertor | Air Hygiene International Inc. | 2,370 hp | 2.00 g/hp-hr | 2,210 hp | 0.03 g/hp-hr | 10 | CO - Carbon Monoxide | PP | Y | NA
2016 | 485 | 0656025008 | Gulfport Energy - Howell | Twp Hwy 145 | Beallsville | 43716 |  | Monroe | P002 | One or multiple stationary natural gas-fired spark ignition (SI) internal combustion engines (ICE) with a combined total horsepower (HP) of no more than 1,800 HP for the site.* Includes 2007 and later model year engines manufactured after the applicable | 2016-09-27 | catalyst | Ecotest | 1,775 hp | 3.0 g/hp-hr | 1,500 hp | 0.03 g/hp-hr | 10 | CO - Carbon Monoxide | PP | Y | NA
2016 | 486 | 0661005052 | Long Compressor Station | 55135 Batesville Rd | Quaker City | 43773 |  | Noble | P008 | 1,680 hp Waukesha 7044GSI NG Fired-rich burn-4stroke compressor engine | 2016-01-28 | C-01(Catalytic Converter): Non-selective catalyst reduction device for C-2000; C-02(Catalytic Converter): Non-selective catalyst reduction device for C-2100; C-03(Catalytic Converter): Non-selective catalyst reduction device for C-2200; C-04(Catalytic Con | Technical Compliance Solutions | 1680 hp | 2.00 g/hp-hr | 1544 hp | 0.03 g/hp-hr | 320 | CO - Carbon Monoxide | PP | Y | NA
2016 | 487 | 0607005016 | Barnesville West Compressor Station | Hwy 801 | Warren Twp. | 43713 |  | Belmont | P007 | Compressor Engine #1 - Natural gas-fired four-stroke lean burn (4SLB) internal combustion engine rated at an operating capacity of 2,370 horsepower (hp) and equipped with an oxidation catalyst | 2016-03-21 | CC001(Catalytic Converter): Compressor Engine #1 Catalytic Converter; CC002(Catalytic Converter): Compressor Engine #2 Catalytic Converter; CC003(Catalytic Converter): Compressor Engine #3 Catalytic Converter | Air Hygiene, Inc. | 2370 hp | 0.14 g/hp-hr | 2264 hp | 0.04 g/hp-hr | 10 | CO - Carbon Monoxide | PP | Y | NA
2016 | 488 | 0607005016 | Barnesville West Compressor Station | Hwy 801 | Warren Twp. | 43713 |  | Belmont | P008 | Compressor Engine #3 - Natural gas-fired four-stroke lean burn (4SLB) internal combustion engine rated at an operating capacity of 2,370 horsepower (hp) and equipped with an oxidation catalyst | 2016-03-21 | CC001(Catalytic Converter): Compressor Engine #1 Catalytic Converter; CC002(Catalytic Converter): Compressor Engine #2 Catalytic Converter; CC003(Catalytic Converter): Compressor Engine #3 Catalytic Converter | Air Hygiene, Inc. | 2370 hp | 0.14 g/hp-hr | 2329 hp | 0.04 g/hp-hr | 10 | CO - Carbon Monoxide | PP | Y | NA
2016 | 489 | 0607015001 | Tri-County Compressor Station (MarkWest / Ohio Oil Gath | N of intersection of Hwy 379 and Town | Barnesville | 43713 |  | Belmont | P008 | Compressor Engine #8 - 1980 HP (15.43 MMBtu/hr) Waukesha P9390 - natural gas-fired four-stroke rich burn internal combustion engine equipped with a three-way oxidation catalyst controlling CH2O, CO, NOx, & VOCs by 80, 97, 98.5 & 66 percent respectively | 2016-08-17 | CC002(Catalytic Converter): Compressor Engine #2 - 3-way Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - 3-way Catalyst; CC004(Catalytic Converter): Compressor Engine #4 - 3-way Catalyst; CC005(Catalytic Converter): Compressor Engine #5 - 3-w | Air Hygiene Internatinal, Inc | 1,980 hp | 2.00 g/hp-hr | 1,757 hp | 0.04 g/hp-hr | 10 | CO - Carbon Monoxide | PP | Y | NA
2016 | 491 | 0634005027 | Arrowhead Compressor Station | E of Clements Rd and S of Jockey Hollow | Athens Twp. | 43977 |  | Harrison | P011 | Compressor Engine #8 - Caterpillar G3608 - natural gas fired four-stroke, lean burn internal combustion engine rated at an operating capacity of 2,370 horsepower equipped with a catalytic convertor | 2016-11-01 | CC07(Catalytic Converter): Compressor Engine #7 Catalytic Convertor; CC008(Catalytic Converter): Compressor Engine #8 Catalytic Convertor | Air Hygiene International Inc. | 2,370 hp | 2.00 g/hp-hr | 2,194 hp | 0.04 g/hp-hr | 10 | CO - Carbon Monoxide | PP | Y | NA
2016 | 492 | 0634005033 | Harrison West Compressor Station | Possum Hollow Road | Freeport | 43973 |  | Harrison | P007 | Compressor Engine #7 - 1980 HP (15.43 MMBtu/hr) Waukesha P9390 - natural gas-fired four-stroke rich burn internal combustion engine equipped with a three-way oxidation catalyst controlling CH2O, CO, NOx, & VOCs by 80, 97, 98.5 & 66 percent respectively | 2016-05-13 | CC005(Catalytic Converter): Compressor Engine #5 - 3-way Catalyst; CC006(Catalytic Converter): Compressor Engine #6 - 3-way Catalyst; CC007(Catalytic Converter): Compressor Engine #7 - 3-way Catalyst | Air Hygiene International | 1980 hp | 2.0 g/hp-hr | 1613 hp | 0.04 g/hp-hr | 10 | CO - Carbon Monoxide | PP | Y | NA
2016 | 493 | 0634005048 | Gulfport Energy - Boy Scout Well Pad | 79900 Adams Rd | Tippecanoe | 44699 |  | Harrison | P002 | One 630 hp Caterpillar 630 and one 118 hp Cummins G8.3C natural gas-fired engines for compressors. | 2016-08-24 | catalyst | Ecotest Inc. | 630 hp | 2.00 g/hp-hr | 455 hp | 0.04 g/hp-hr | 6348 03 | CO - Carbon Monoxide | PP | Y | NA
2016 | 494 | 0634005056 | Scio Compressor Station | 37650 Bower Rd | Scio | 43988 |  | Harrison | P002 | Compressor Engine #2 - 1,775 HP Caterpillar G3606 (4S-LB) - natural gas-fired four-cycle lean burn internal combustion engine equipped with an oxidation catalyst controlling CO & VOC emissions | 2016-06-06 | CC002(Catalytic Converter): Compressor Engine #2 - Oxidation Catalyst | EcoTest Energy Services | 1775 hp | 2.00 g/hp-hr | 1695 hp | 0.04 g/hp-hr | 320 | CO - Carbon Monoxide | PP | Y | NA
2016 | 495 | 0634005056 | Scio Compressor Station | 37650 Bower Rd | Scio | 43988 |  | Harrison | P007 | Compressor Engine #7 - 1,775 HP Caterpillar G3606 (4S-LB) - natural gas-fired four-cycle lean burn internal combustion engine equipped with an oxidation catalyst controlling CO & VOC emissions | 2016-06-07 | CC007(Catalytic Converter): Compressor Engine #7 - Oxidation Catalyst | EcoTest Energy Services | 1775 hp | 2.00 g/hp-hr | 1700 hp | 0.04 g/hp-hr | 320 | CO - Carbon Monoxide | PP | Y | NA
2016 | 496 | 0634005056 | Scio Compressor Station | 37650 Bower Rd | Scio | 43988 |  | Harrison | P009 | Compressor Engine #9 - 1,775 HP Caterpillar G3606 (4S-LB) - natural gas-fired four-cycle lean burn internal combustion engine equipped with an oxidation catalyst controlling CO & VOC emissions | 2016-06-07 | CC009(Catalytic Converter): Compressor Engine #9 - Oxidation Catalyst | EcoTest Energy Services | 1775 hp | 2.00 g/hp-hr | 1760 hp | 0.04 g/hp-hr | 320 | CO - Carbon Monoxide | PP | Y | NA
2016 | 497 | 0656025005 | Gulfport Energy - Campbell | Seal Road | Beallsville | 43716 |  | Monroe | P002 | One or multiple stationary natural gas-fired spark ignition (SI) internal combustion engines (ICE) with a combined total horsepower (HP) of no more than 1,800 HP for the site.* Includes 2007 and later model year engines manufactured after the applicable | 2016-09-27 | catalyst | Ecotest | 1,775 hp | 3.0 g/hp-hr | 1,500 hp | 0.04 g/hp-hr | 10 | CO - Carbon Monoxide | PP | Y | NA
2016 | 498 | 0661005052 | Long Compressor Station | 55135 Batesville Rd | Quaker City | 43773 |  | Noble | P009 | 1,680 hp Waukesha 7044GSI NG Fired-rich burn-4stroke compressor engine | 2016-01-28 | C-09(Catalytic Converter): Non-selective catalyst reduction device for C-2800 | Technical Compliance Solutions | 1680 hp | 2.0 g/hp-hr | 1617 hp | 0.04 g/hp-hr | 320 | CO - Carbon Monoxide | PP | Y | NA
2016 | 499 | 0210002039 | Kilgore Compressor Station-Utica Gas Services, LLC | Pontiff Rd | Kilgore | 43988 |  | Carroll | P003 | 1,775 hp NG-fired 4SLB Stationary ICE equipped w/catalyst Caterpillar G3606: Serial Number: 4ZS01797 | 2016-12-02 | CC001(Catalytic Converter): Compressor Engine #1 - Oxidation Catalyst; CC002(Catalytic Converter): Compressor Engine #2 - Oxidation Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - Oxidation Catalyst; CC004(Catalytic Converter): Compressor Eng | Technical Compliance Solutions LLC | 1775 HP | 2.0g/hp-hr & 1.18lbs/hr | 1629 | 0.042 g/hp-hr & 0.152lb/hr | 10 | CO - Carbon Monoxide | PP | Y | NA
2016 | 500 | 0210002039 | Kilgore Compressor Station-Utica Gas Services, LLC | Pontiff Rd | Kilgore | 43988 |  | Carroll | P004 | 1,775 hp NG-fired 4SLB Stationary ICE equipped w/catalyst Caterpillar G3606: Serial Number: 4ZS01800 | 2016-12-02 | CC001(Catalytic Converter): Compressor Engine #1 - Oxidation Catalyst; CC002(Catalytic Converter): Compressor Engine #2 - Oxidation Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - Oxidation Catalyst; CC004(Catalytic Converter): Compressor Eng | Technical Compliance Solutions LLC | 1775 HP | 2.0g/hp-hr & 1.18lbs/hr | 1626 | 0.043 g/hp-hr & 0.153 lb/hr | 10 | CO - Carbon Monoxide | PP | Y | NA
2016 | 530 | 0634005027 | Arrowhead Compressor Station | E of Clements Rd and S of Jockey Hollow | Athens Twp. | 43977 |  | Harrison | P008 | Compressor Engine #5 - Caterpillar G3608 - natural gas fired four-stroke, lean burn internal combustion engine rated at an operating capacity of 2,370 horsepower equipped with a catalytic convertor | 2016-10-31 | CC005(Catalytic Converter): Compressor Engine #5 Catalytic Convertor; CC006(Catalytic Converter): Compressor Engine #6 Catalytic Convertor | Air Hygiene International Inc. | 2,370 hp | 2.00 g/hp-hr | 2,264 hp | 0.05 g/hp-hr | 10 | CO - Carbon Monoxide | PP | Y | NA
2016 | 531 | 0634005027 | Arrowhead Compressor Station | E of Clements Rd and S of Jockey Hollow | Athens Twp. | 43977 |  | Harrison | P009 | Compressor Engine #6 - Caterpillar G3608 - natural gas fired four-stroke, lean burn internal combustion engine rated at an operating capacity of 2,370 horsepower equipped with a catalytic convertor | 2016-10-31 | CC005(Catalytic Converter): Compressor Engine #5 Catalytic Convertor; CC006(Catalytic Converter): Compressor Engine #6 Catalytic Convertor | Air Hygiene International Inc. | 2,370 hp | 2.00 g/hp-hr | 2,202 hr | 0.05 g/hp-hr | 10 | CO - Carbon Monoxide | PP | Y | NA
2016 | 532 | 0656005028 | Miller Compressor Station | 51103 Twp Rd 847 | Seneca Twp. | 43788 |  | Monroe | P007 | Waukesha 1680 bhp Model L7044GSI 4-stroke Natural Gas Rich Burn Gas Compressor Engine Model Year 2014 controlled by a catalyst | 2016-06-22 | C-2701C(Catalytic Converter): Engine Catalyst; C-2702C(Catalytic Converter): Engine Catalyst; C-2703C(Catalytic Converter): Engine Catalyst; C-2704C(Catalytic Converter): Engine Catalyst; C-2705C(Catalytic Converter): Engine Catalyst; C-2706C(Catalytic Co | Alliance Source Testing | 1680 hp | 0.5 g/hp-hr | 1680 hp | 0.05 g/hp-hr | 10 | CO - Carbon Monoxide | PP | N | NA
2016 | 533 | 0661005040 | Crum Compressor Station | 52934 Town Highway 192 | Seneca Twp. | 43780 |  | Noble | P004 | One (1) Waukesha 7044GSI 1,680 hp compressor engine fitted with a 5-element non-selective catalytic reduction catalyst. | 2016-08-31 | C-1(Catalytic Converter): 5-element NSCR for compressor engine C-100; C-2(Catalytic Converter): 5-element NSCR for compressor engine C-200; C-3(Catalytic Converter): 5-element NSCR for compressor engine C-300; C-4(Catalytic Converter): 5-element NSCR for | Alliance Source Testing | 1680 hp | 2.0 g/hp-hr | 1564 hp | 0.05 g/hp-hr | 10 | CO - Carbon Monoxide | PP | Y | NA
2016 | 534 | 0210012004 | Augusta Compressor Facility- Utica Gas Services, L.L.C. | 8034 Bane Rd NE | East Twp. | 44427 |  | Carroll | P012 | 1,775-hp Caterpillar G3606 Compressor Engine w/ Oxidation Catalyst | 2016-09-08 | Oxid. Cat. 3(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 4(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 5(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 6(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 7(Catalytic Converter): | EcoTest Energy Services | 1775 Hp | 1.18 lbs/hr, 2.0 g/hp/hr, 270ppmvd@15%O2 | 1600 Hp or 90.1% of Max | 0.05 lbs/hr, 0.02 g/hp/hr, 2 ppmvd@15%O2 | 10 | CO - Carbon Monoxide | PP | Y | NA
2016 | 579 | 0210002039 | Kilgore Compressor Station-Utica Gas Services, LLC | Pontiff Rd | Kilgore | 43988 |  | Carroll | P001 | 1,775 hp NG-fired 4SLB Stationary ICE equipped w/catalyst Caterpillar G3606 Serial Number: 4ZS01713 | 2016-12-02 | CC001(Catalytic Converter): Compressor Engine #1 - Oxidation Catalyst; CC002(Catalytic Converter): Compressor Engine #2 - Oxidation Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - Oxidation Catalyst; CC004(Catalytic Converter): Compressor Eng | Technical Compliance Solutions LLC | 1775 HP | 2.0g/hp-hr & 1.18lbs/hr | 1703 | 0.057 g/hp-hr & 0.215 lb/hr | 10 | CO - Carbon Monoxide | PP | Y | NA
2016 | 580 | 0630005037 | Blue Racer Midstream LLC - Guernsey Co Field Station #1 | East of I-70E and US 40E | Fairview | 43736 |  | Guernsey | P011 | Compressor engine 1875 HP Cat 3606 4 stroke lean burn oxidation catalyst | 2016-10-18 | CC-2(Catalytic Converter): Catalytic Converter 2; CC-3(Catalytic Converter): Catalytic Converter 3 | Great Plains Analytical Services | 1,875 hp | 1.5 g/hp-hr | 1,822 hp | 0.058 g/hp-hr | 6348 03 | CO - Carbon Monoxide | PP | N | NA
2016 | 581 | 0634005056 | Scio Compressor Station | 37650 Bower Rd | Scio | 43988 |  | Harrison | P003 | Compressor Engine #3 - 1,775 HP Caterpillar G3606 (4S-LB) - natural gas-fired four-cycle lean burn internal combustion engine equipped with an oxidation catalyst controlling CO & VOC emissions | 2016-06-06 | CC003(Catalytic Converter): Compressor Engine #3 - Oxidation Catalyst | EcoTest Energy Services | 1775 hp | 2.00 g/hp-hr | 1680 hp | 0.06 g/hp-hr | 320 | CO - Carbon Monoxide | PP | Y | NA
2016 | 582 | 0634005056 | Scio Compressor Station | 37650 Bower Rd | Scio | 43988 |  | Harrison | P005 | Compressor Engine #5 - 1,775 HP Caterpillar G3606 (4S-LB) - natural gas-fired four-cycle lean burn internal combustion engine equipped with an oxidation catalyst controlling CO & VOC emissions | 2016-06-06 | CC005(Catalytic Converter): Compressor Engine #5 - Oxidation Catalyst | EcoTest Energy Services | 1775 hp | 2.00 g/hp-hr | 1720 hp | 0.06 g/hp-hr | 320 | CO - Carbon Monoxide | PP | Y | NA
2016 | 590 | 0656005010 | Dominion East Ohio - Switzerland Compressor Station | German Ridge Road | Switzerland Twp. | 43942 |  | Monroe | P001 | 3550 Hp Natural gas-fired (4SLB) Caterpillar model 3612 LE DM5309-06 compressor engines equipped with catalytic reduction (three-way). | 2016-09-22 | catalyst | Environmental Quality management | 3,550 hp | 2.0 g/hp-hr | 3,307 hp | 0.06 g/hp-hr | 10 | CO - Carbon Monoxide | PP | Y | NA
2016 | 591 | 0656005010 | Dominion East Ohio - Switzerland Compressor Station | German Ridge Road | Switzerland Twp. | 43942 |  | Monroe | P002 | 3550 Hp Natural gas-fired (4SLB) Caterpillar model 3612 LE DM5309-06 compressor engines equipped with catalytic reduction (three-way). | 2016-09-22 | catalyst | Environmental Quality management | 3,550 hp | 2.0 g/hp-hr | 3,343 hp | 0.06 g/hp-hr | 10 | CO - Carbon Monoxide | PP | Y | NA
2016 | 592 | 0656005010 | Dominion East Ohio - Switzerland Compressor Station | German Ridge Road | Switzerland Twp. | 43942 |  | Monroe | P003 | 3550 Hp Natural gas-fired (4SLB) Caterpillar model 3612 LE DM5309-06 compressor engines equipped with catalytic reduction (three-way). | 2016-09-22 | catalyst | Environmental Quality management | 3,550 hp | 2.0 g/hp-hr | 3,361 hp | 0.06 g/hp-hr | 10 | CO - Carbon Monoxide | PP | Y | NA
2016 | 593 | 0634005123 | Yoder Compressor Station | 79300 Cassville Rd | Cadiz | 43907 |  | Harrison | P001 | Natural gas-fired four-stroke lean burn (4SLB) internal combustion engine rated at an operating capacity of 2,370 horsepower (hp) and equipped with an oxidation catalyst. | 2016-05-19 | CC001(Catalytic Converter): Compressor Engine #1 Catalytic Converter; CC002(Catalytic Converter): Compressor Engine #2 Catalytic Converter; CC003(Catalytic Converter): Compressor Engine #3 Catalytic Converter | Air Hygiene International | 2370 hp | 0.73 lb/hr | 2889 hp | 0.06 lb/hr | 10 | CO - Carbon Monoxide | PP | Y | NA
2016 | 594 | 0210012002 | Utica Gas Services, LLC-Carrollton Compressor Facility | 2098 Panda Road SE | Carrollton | 44615 |  | Carroll | P012 | 1,775 HP natural gas-fired Caterpillar G3606 engine #9 equipped with an oxidation catalyst | 2016-01-07 | Oxid. Cat.(Catalytic Converter): Oxidative Catalyst | Alliance Source Testing | 1775 HP | 1.18lbs/hr, 2.0g/hp-hr | 1716 HP | 0.06 lb/hr, 0.02 g/hp-hr | 10 | CO - Carbon Monoxide | PP | Y | NA
2016 | 595 | 0210012004 | Augusta Compressor Facility- Utica Gas Services, L.L.C. | 8034 Bane Rd NE | East Twp. | 44427 |  | Carroll | P013 | 1,775-hp Caterpillar G3606 Compressor Engine w/ Oxidation Catalyst | 2016-09-08 | Oxid. Cat. 3(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 4(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 5(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 6(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 7(Catalytic Converter): | EcoTest Energy Services | 1775 Hp | 1.18 lbs/hr, 2.0 g/hp/hr, 270ppmvd@15%O2 | 1600 Hp or 90.1% of Max | 0.06 lbs/hr, 0.02 g/hp/hr, 2 ppmvd@15%O2 | 10 | CO - Carbon Monoxide | PP | Y | NA
2016 | 596 | 0634005033 | Harrison West Compressor Station | Possum Hollow Road | Freeport | 43973 |  | Harrison | P006 | Compressor Engine #6 - 1980 HP (15.43 MMBtu/hr) Waukesha P9390 - natural gas-fired four-stroke rich burn internal combustion engine equipped with a three-way oxidation catalyst controlling CH2O, CO, NOx, & VOCs by 80, 97, 98.5 & 66 percent respectively | 2016-05-13 | CC005(Catalytic Converter): Compressor Engine #5 - 3-way Catalyst; CC006(Catalytic Converter): Compressor Engine #6 - 3-way Catalyst; CC007(Catalytic Converter): Compressor Engine #7 - 3-way Catalyst | Air Hygiene International | 1980 hp | 2.0 g/hp-hr | 1638 hp | 0.07 g/hp-hr | 10 | CO - Carbon Monoxide | PP | Y | NA
2016 | 608 | 0634005034 | Lake Compressor Station | County Highway 21 | Freeport | 43973 |  | Harrison | P005 | Compressor Engine #5 - 1980 HP (15.43 MMBtu/hr) Waukesha P9390 - natural gas-fired four-stroke rich burn internal combustion engine equipped with a three-way oxidation catalyst controlling CH2O, CO, NOx, & VOCs by 80, 97, 98.5 & 66 percent respectively | 2016-04-14 | CC004(Catalytic Converter): Compressor Engine #4 - 3-way Catalyst; CC005(Catalytic Converter): Compressor Engine #5 - 3-way Catalyst; CC011(Catalytic Converter): Compressor Engine #9 - 3-way Catalyst | Air Hygiene, Inc | 1980 hp | 2.0 g/hp-hr | 1642 hp | 0.07 g/hp-hr | 10 | CO - Carbon Monoxide | PP | N | NA | test did conform to test method-document locked
2016 | 609 | 0634005056 | Scio Compressor Station | 37650 Bower Rd | Scio | 43988 |  | Harrison | P001 | Compressor Engine #1 - 1,775 HP Caterpillar G3606 (4S-LB) - natural gas-fired four-cycle lean burn internal combustion engine equipped with an oxidation catalyst controlling CO & VOC emissions. | 2016-06-06 | CC001(Catalytic Converter): Compressor Engine #1 - Oxidation Catalyst | EcoTest Energy Services | 1775 hp | 2.00 g/hp-hr | 1700 hp | 0.07 g/hp-hr | 320 | CO - Carbon Monoxide | PP | Y | NA
2016 | 610 | 0634005056 | Scio Compressor Station | 37650 Bower Rd | Scio | 43988 |  | Harrison | P004 | Compressor Engine #4 - 1,775 HP Caterpillar G3606 (4S-LB) - natural gas-fired four-cycle lean burn internal combustion engine equipped with an oxidation catalyst controlling CO & VOC emissions | 2016-06-06 | CC004(Catalytic Converter): Compressor Engine #4 - Oxidation Catalyst | EcoTest Energy Services | 1775 hp | 2.00 g/hp-hr | 1750 hp | 0.07 g/hp-hr | 320 | CO - Carbon Monoxide | PP | Y | NA
2016 | 611 | 0634005056 | Scio Compressor Station | 37650 Bower Rd | Scio | 43988 |  | Harrison | P006 | Compressor Engine #6 - 1,775 HP Caterpillar G3606 (4S-LB) - natural gas-fired four-cycle lean burn internal combustion engine equipped with an oxidation catalyst controlling CO & VOC emissions | 2016-06-06 | CC006(Catalytic Converter): Compressor Engine #6 - Oxidation Catalyst | EcoTest Energy Services | 1775 hp | 2.00 g/hp-hr | 1720 hp | 0.07 g/hp-hr | 320 | CO - Carbon Monoxide | PP | Y | NA
2016 | 612 | 0634005056 | Scio Compressor Station | 37650 Bower Rd | Scio | 43988 |  | Harrison | P010 | Compressor Engine #10 - 1,775 HP Caterpillar G3606 (4S-LB) - natural gas-fired four-cycle lean burn internal combustion engine equipped with an oxidation catalyst controlling CO & VOC emissions | 2016-06-07 | CC010(Catalytic Converter): Compressor Engine #10 - Oxidation Catalyst | EcoTest Energy Services | 1775 hp | 2.00 g/hp-hr | 1725 hp | 0.07 g/hp-hr | 320 | CO - Carbon Monoxide | PP | Y | NA
2016 | 613 | 0656005028 | Miller Compressor Station | 51103 Twp Rd 847 | Seneca Twp. | 43788 |  | Monroe | P006 | Waukesha 1680 bhp Model L7044GSI 4-stroke Natural Gas Rich Burn Gas Compressor Engine Model Year 2014 controlled by a catalyst | 2016-01-29 | C-2706C(Catalytic Converter): Engine Catalyst | E2 Energy Services | 1680 hp | 0.50 g/hp-hr | 1545 hp | 0.07 g/hp-hr | 6348 03 | CO - Carbon Monoxide | PP | Y | NA
2016 | 614 | 0656025012 | Goliath Compressor Station | 48208 St Rte 556 | Beallsville | 43716 |  | Monroe | P005 | Compressor #5 - driven by Caterpillar G3608 engine | 2016-01-13 | C305Catalyst(Other): null | Technical Compliance Solutions | 2370 hp | 1.1 lbs/hr | 1497 hp | 0.07 lb/hr | 320 | CO - Carbon Monoxide | PP | Y | NA
2016 | 630 | 0210012004 | Augusta Compressor Facility- Utica Gas Services, L.L.C. | 8034 Bane Rd NE | East Twp. | 44427 |  | Carroll | P007 | 1,775-hp Caterpillar G3606 Compressor Engine w/ Oxidation Catalyst | 2016-09-08 | Oxid. Cat. 3(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 4(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 5(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 6(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 7(Catalytic Converter): | EcoTest Energy Services | 1775 Hp | 1.18 lbs/hr, 2.0 g/hp/hr, 270ppmvd@15%O2 | 1600 Hp or 90.1% of Max | 0.07 lb/hr, 0.02 g/hp/hr, 3 ppmvd@15%O2 | 10 | CO - Carbon Monoxide | PP | Y | NA
2016 | 639 | 0630005037 | Blue Racer Midstream LLC - Guernsey Co Field Station #1 | East of I-70E and US 40E | Fairview | 43736 |  | Guernsey | P012 | Compressor engine 1875 HP Cat 3606 4 stroke lean burn oxidation catalyst | 2016-10-18 | CC-2(Catalytic Converter): Catalytic Converter 2; CC-3(Catalytic Converter): Catalytic Converter 3 | Great Plains Analytical Services | 1,875 hp | 1.5 g/hp-hr | 1,800 hp | 0.075 g/hp-hr | 6348 03 | CO - Carbon Monoxide | PP | N | NA
2016 | 640 | 0210002039 | Kilgore Compressor Station-Utica Gas Services, LLC | Pontiff Rd | Kilgore | 43988 |  | Carroll | P005 | 1,775 hp NG-fired 4SLB Stationary ICE equipped w/catalyst Caterpillar G3606: Serial Number: 4ZS01804 | 2016-12-02 | CC001(Catalytic Converter): Compressor Engine #1 - Oxidation Catalyst; CC002(Catalytic Converter): Compressor Engine #2 - Oxidation Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - Oxidation Catalyst; CC004(Catalytic Converter): Compressor Eng | Technical Compliance Solutions LLC | 1775 HP | 2.0g/hp-hr & 1.18lbs/hr | 1671 | 0.077 g/hp-hr & 0.285 lb/hr | 10 | CO - Carbon Monoxide | PP | Y | NA
2016 | 641 | 0607015001 | Tri-County Compressor Station (MarkWest / Ohio Oil Gath | N of intersection of Hwy 379 and Town | Barnesville | 43713 |  | Belmont | P005 | Compressor Engine #5 - 1980 HP (15.43 MMBtu/hr) Waukesha P9390 - natural gas-fired four-stroke rich burn internal combustion engine equipped with a three-way oxidation catalyst controlling CH2O, CO, NOx, & VOCs by 80, 97, 98.5 & 66 percent respectively | 2016-08-17 | CC002(Catalytic Converter): Compressor Engine #2 - 3-way Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - 3-way Catalyst; CC004(Catalytic Converter): Compressor Engine #4 - 3-way Catalyst; CC005(Catalytic Converter): Compressor Engine #5 - 3-w | Air Hygiene Internatinal, Inc | 1,980 hp | 2.00 g/hp-hr | 1,733 hp | 0.08 g/hp-hr | 10 | CO - Carbon Monoxide | PP | Y | NA
2016 | 642 | 0634005033 | Harrison West Compressor Station | Possum Hollow Road | Freeport | 43973 |  | Harrison | P005 | Compressor Engine #5 - 1980 HP (15.43 MMBtu/hr) Waukesha P9390 - natural gas-fired four-stroke rich burn internal combustion engine equipped with a three-way oxidation catalyst controlling CH2O, CO, NOx, & VOCs by 80, 97, 98.5 & 66 percent respectively | 2016-05-13 | CC005(Catalytic Converter): Compressor Engine #5 - 3-way Catalyst; CC006(Catalytic Converter): Compressor Engine #6 - 3-way Catalyst; CC007(Catalytic Converter): Compressor Engine #7 - 3-way Catalyst | Air Hygiene International | 1980 hp | 2.0 g/hp-hr | 1612 hp | 0.08 g/hp-hr | 10 | CO - Carbon Monoxide | PP | Y | NA
2016 | 643 | 0634005033 | Harrison West Compressor Station | Possum Hollow Road | Freeport | 43973 |  | Harrison | P001 | Compressor Engine #1 - 1480 HP (11.39 MMBtu/hr) Waukesha L7042 - natural gas-fired four-stroke rich burn internal combustion engine equipped with a three-way oxidation catalyst controlling CH2O, CO, NOx, & VOCs by 80, 97, 98.5 & 66 percent respectively | 2016-04-28 | CC001(Catalytic Converter): Compressor Engine #1 - 3-way Catalyst; CC002(Catalytic Converter): Compressor Engine #2 - 3-way Catalyst; CC004(Catalytic Converter): Compressor Engine #4 - 3-way Catalyst | Air Hygiene, Inc | 1480 hp | 2 g/hp-hr | 1181 hp | 0.08 g/hp-hr | 10 | CO - Carbon Monoxide | PP | Y | NA
2016 | 655 | 0634005056 | Scio Compressor Station | 37650 Bower Rd | Scio | 43988 |  | Harrison | P008 | Compressor Engine #8 - 1,775 HP Caterpillar G3606 (4S-LB) - natural gas-fired four-cycle lean burn internal combustion engine equipped with an oxidation catalyst controlling CO & VOC emissions | 2016-06-07 | CC008(Catalytic Converter): Compressor Engine #8 - Oxidation Catalyst | EcoTest Energy Services | 1775 hp | 2.00 g/hp-hr | 1707 hp | 0.08 g/hp-hr | 320 | CO - Carbon Monoxide | PP | Y | NA
2016 | 656 | 0656005028 | Miller Compressor Station | 51103 Twp Rd 847 | Seneca Twp. | 43788 |  | Monroe | P003 | Waukesha 1680 bhp Model L7044GSI 4-stroke Natural Gas Rich Burn Gas Compressor Engine Model Year 2014 controlled by a catalyst | 2016-06-22 | C-2701C(Catalytic Converter): Engine Catalyst; C-2702C(Catalytic Converter): Engine Catalyst; C-2703C(Catalytic Converter): Engine Catalyst; C-2704C(Catalytic Converter): Engine Catalyst; C-2705C(Catalytic Converter): Engine Catalyst; C-2706C(Catalytic Co | Alliance Source Testing | 1680 hp | 0.5 g/hp-hr | 1680 hp | 0.08 g/hp-hr | 10 | CO - Carbon Monoxide | PP | N | NA
2016 | 660 | 0656025012 | Goliath Compressor Station | 48208 St Rte 556 | Beallsville | 43716 |  | Monroe | P001 | Compressor #1 - driven by Caterpillar G3608 engine | 2016-01-13 | C301Catalyst(Other): null | Technical Compliance Solutions | 2370 hp | 1.1 lbs/hr | 1497 hp | 0.08 lb/hr | 320 | CO - Carbon Monoxide | PP | Y | NA
2016 | 661 | 0210002039 | Kilgore Compressor Station-Utica Gas Services, LLC | Pontiff Rd | Kilgore | 43988 |  | Carroll | P010 | 1,775 hp NG-fired 4SLB Stationary ICE equipped w/catalyst Caterpillar G3606: Serial Number: 4ZS01814 | 2016-12-02 | CC001(Catalytic Converter): Compressor Engine #1 - Oxidation Catalyst; CC002(Catalytic Converter): Compressor Engine #2 - Oxidation Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - Oxidation Catalyst; CC004(Catalytic Converter): Compressor Eng | Technical Compliance Solutions LLC | 1775 HP | 2.0g/hp-hr & 1.18lbs/hr | 1740 | 0.089 g/hp-hr & 0.34 lb/hr | 10 | CO - Carbon Monoxide | PP | Y | NA
2016 | 717 | 0607015001 | Tri-County Compressor Station (MarkWest / Ohio Oil Gath | N of intersection of Hwy 379 and Town | Barnesville | 43713 |  | Belmont | P004 | Compressor Engine #4 - 1980 HP (15.43 MMBtu/hr) Waukesha P9390 - natural gas-fired four-stroke rich burn internal combustion engine equipped with a three-way oxidation catalyst controlling CH2O, CO, NOx, & VOCs by 80, 97, 98.5 & 66 percent respectively | 2016-08-17 | CC002(Catalytic Converter): Compressor Engine #2 - 3-way Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - 3-way Catalyst; CC004(Catalytic Converter): Compressor Engine #4 - 3-way Catalyst; CC005(Catalytic Converter): Compressor Engine #5 - 3-w | Air Hygiene Internatinal, Inc | 1,980 hp | 2.00 g/hp-hr | 1,668 hp | 0.09 g/hp-hr | 10 | CO - Carbon Monoxide | PP | Y | NA
2016 | 719 | 0661005027 | E2 Appalachian LLC - Batesville | 58380 St John Rd | Quaker City | 43773 |  | Noble | P007 | 1,680 Hp. Waukesha (L7044GSI) natural gas-fired, rich burn, turbocharged, with oxidation catalyst, compressor engine | 2016-07-11 | C2701C(Catalytic Converter): Engine Catalyst; C2707C(Catalytic Converter): Engine Catalyst; C2708C(Catalytic Converter): Engine Catalyst | Alliance Source Testing | 1,680 hp | 2.0 g/hp-hr | 1,607 hp | 0.098 g/hp-hr | 10 | CO - Carbon Monoxide | PP | Y | NA
2016 | 724 | 0634005034 | Lake Compressor Station | County Highway 21 | Freeport | 43973 |  | Harrison | P004 | Compressor Engine #4 - 1980 HP (15.43 MMBtu/hr) Waukesha P9390 - natural gas-fired four-stroke rich burn internal combustion engine equipped with a three-way oxidation catalyst controlling CH2O, CO, NOx, & VOCs by 80, 97, 98.5 & 66 percent respectively | 2016-04-14 | CC004(Catalytic Converter): Compressor Engine #4 - 3-way Catalyst; CC005(Catalytic Converter): Compressor Engine #5 - 3-way Catalyst; CC011(Catalytic Converter): Compressor Engine #9 - 3-way Catalyst | Air Hygiene, Inc | 1980 hp | 2.0 g/hp-hr | 1647 hp | 0.10 b/hp-hr | 10 | CO - Carbon Monoxide | PP | N | NA | test did conform to test method-document locked
2016 | 1134 | 0607015001 | Tri-County Compressor Station (MarkWest / Ohio Oil Gath | N of intersection of Hwy 379 and Town | Barnesville | 43713 |  | Belmont | P006 | Compressor Engine #6 - 1980 HP (15.43 MMBtu/hr) Waukesha P9390 - natural gas-fired four-stroke rich burn internal combustion engine equipped with a three-way oxidation catalyst controlling CH2O, CO, NOx, & VOCs by 80, 97, 98.5 & 66 percent respectively | 2016-08-17 | CC002(Catalytic Converter): Compressor Engine #2 - 3-way Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - 3-way Catalyst; CC004(Catalytic Converter): Compressor Engine #4 - 3-way Catalyst; CC005(Catalytic Converter): Compressor Engine #5 - 3-w | Air Hygiene Internatinal, Inc | 1,980 hp | 2.00 g/hp-hr | 1,709 hp | 0.10 g/hp-hr | 10 | CO - Carbon Monoxide | PP | Y | NA
2016 | 1136 | 0634005033 | Harrison West Compressor Station | Possum Hollow Road | Freeport | 43973 |  | Harrison | P002 | Compressor Engine #2 - 1480 HP (11.39 MMBtu/hr) Waukesha L7042 - natural gas-fired four-stroke rich burn internal combustion engine equipped with a three-way oxidation catalyst controlling CH2O, CO, NOx, & VOCs by 80, 97, 98.5 & 66 percent respectively | 2016-04-28 | CC001(Catalytic Converter): Compressor Engine #1 - 3-way Catalyst; CC002(Catalytic Converter): Compressor Engine #2 - 3-way Catalyst; CC004(Catalytic Converter): Compressor Engine #4 - 3-way Catalyst | Air Hygiene, Inc | 1480 hp | 1 g/hp-hr | 1611 hp | 0.10 g/hp-hr | 10 | CO - Carbon Monoxide | PP | Y | NA
2016 | 1139 | 0634005034 | Lake Compressor Station | County Highway 21 | Freeport | 43973 |  | Harrison | P001 | Compressor Engine #1 - 1480 HP (11.39 MMBtu/hr) Waukesha L7042 - natural gas-fired four-stroke rich burn internal combustion engine equipped with a three-way oxidation catalyst controlling CH2O, CO, NOx, & VOCs by 80, 97, 98.5 & 66 percent respectively | 2016-03-28 | CC001(Catalytic Converter): Compressor Engine #1 - 3-way Catalyst; CC002(Catalytic Converter): Compressor Engine #2 - 3-way Catalyst | Air Hygiene, Inc. | 1480 hp | 0.25 g/hp-hr | 1233 hp | 0.10 g/hp-hr | 10 | CO - Carbon Monoxide | PP | Y | NA
2016 | 1140 | 0656005028 | Miller Compressor Station | 51103 Twp Rd 847 | Seneca Twp. | 43788 |  | Monroe | P006 | Waukesha 1680 bhp Model L7044GSI 4-stroke Natural Gas Rich Burn Gas Compressor Engine Model Year 2014 controlled by a catalyst | 2016-06-22 | C-2701C(Catalytic Converter): Engine Catalyst; C-2702C(Catalytic Converter): Engine Catalyst; C-2703C(Catalytic Converter): Engine Catalyst; C-2704C(Catalytic Converter): Engine Catalyst; C-2705C(Catalytic Converter): Engine Catalyst; C-2706C(Catalytic Co | Alliance Source Testing | 1680 hp | 0.5 g/hp-hr | 1680 hp | 0.10 g/hp-hr | 10 | CO - Carbon Monoxide | PP | N | NA
2016 | 1141 | 0661005008 | Seneca Gas Plant | Zep Road | Summerfield | 43788 |  | Noble | P001 | Compressor Engine #1 - Natural gas-fired four-stroke lean burn (4SLB) internal combustion engine rated at an operating capacity of 4,735 horsepower (hp) and equipped with an oxidation catalyst. | 2016-03-17 | CC001(Catalytic Converter): Compressor Engine #1 - Catalyic Convertor; CC002(Catalytic Converter): Compressor Engine #2 - Catalytic Convertor | Air Hygiene International, Inc | 4735 ph | 0.14 g/hp-hr | 4182 hp | 0.10 g/hp-hr | 10 | CO - Carbon Monoxide | PP | Y | NA
2016 | 1142 | 0661005052 | Long Compressor Station | 55135 Batesville Rd | Quaker City | 43773 |  | Noble | P002 | 1,680 hp Waukesha 7044GSI NG Fired-rich burn-4stroke compressor engine | 2016-01-28 | C-01(Catalytic Converter): Non-selective catalyst reduction device for C-2000; C-02(Catalytic Converter): Non-selective catalyst reduction device for C-2100; C-03(Catalytic Converter): Non-selective catalyst reduction device for C-2200; C-04(Catalytic Con | Technical Compliance Solutions | 1680 hp | 2.00 g/hp-hr | 1610 hp | 0.10 g/hp-hr | 320 | CO - Carbon Monoxide | PP | Y | NA
2016 | 1143 | 0210002039 | Kilgore Compressor Station-Utica Gas Services, LLC | Pontiff Rd | Kilgore | 43988 |  | Carroll | P009 | 1,775 hp NG-fired 4SLB Stationary ICE equipped w/catalyst Caterpillar G3606: Serial Number: 4ZS01776 | 2016-12-02 | CC001(Catalytic Converter): Compressor Engine #1 - Oxidation Catalyst; CC002(Catalytic Converter): Compressor Engine #2 - Oxidation Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - Oxidation Catalyst; CC004(Catalytic Converter): Compressor Eng | Technical Compliance Solutions LLC | 1775 HP | 2.0g/hp-hr & 1.18lbs/hr | 1679 | 0.10 g/hp-hr & 0.374 lb/hr | 10 | CO - Carbon Monoxide | PP | Y | NA
2016 | 1150 | 0656025012 | Goliath Compressor Station | 48208 St Rte 556 | Beallsville | 43716 |  | Monroe | P002 | Compressor #2 - driven by Caterpillar G3608 engine | 2016-01-13 | C302Catalyst(Other): null | Technical Compliance Solutions | 2370 hp | 1.1 lbs/hr | 1501 hp | 0.10 lb/hr | 320 | CO - Carbon Monoxide | PP | Y | NA
2016 | 1151 | 0656025012 | Goliath Compressor Station | 48208 St Rte 556 | Beallsville | 43716 |  | Monroe | P003 | Compressor #3 - driven by Caterpillar G3608 engine | 2016-01-14 | C303Catalyst(Other): | Technical Compliance Solutions | 2370 hp | 1.1 lbs/hr | 1537 hp | 0.10 lb/hr | 320 | CO - Carbon Monoxide | PP | Y | NA
2016 | 1152 | 0210002039 | Kilgore Compressor Station-Utica Gas Services, LLC | Pontiff Rd | Kilgore | 43988 |  | Carroll | P007 | 1,775 hp NG-fired 4SLB Stationary ICE equipped w/catalyst Caterpillar G3606: Serial Number: 4ZS01807 | 2016-12-02 | CC001(Catalytic Converter): Compressor Engine #1 - Oxidation Catalyst; CC002(Catalytic Converter): Compressor Engine #2 - Oxidation Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - Oxidation Catalyst; CC004(Catalytic Converter): Compressor Eng | Technical Compliance Solutions LLC | 1775 HP | 2.0g/hp-hr & 1.18lbs/hr | 1654 | 0.102 g/hp-hr & 0.372 lb/hr | 10 | CO - Carbon Monoxide | PP | Y | NA
2016 | 1159 | 0661005027 | E2 Appalachian LLC - Batesville | 58380 St John Rd | Quaker City | 43773 |  | Noble | P008 | 1,680 Hp. Waukesha (L7044GSI) natural gas-fired, rich burn, turbocharged, with oxidation catalyst, compressor engine | 2016-07-11 | C2701C(Catalytic Converter): Engine Catalyst; C2707C(Catalytic Converter): Engine Catalyst; C2708C(Catalytic Converter): Engine Catalyst | Alliance Source Testing | 1,680 hp | 2.0 g/hp-hr | 1,568 hp | 0.105 g/hp-hr | 10 | CO - Carbon Monoxide | PP | Y | NA
2016 | 1160 | 0634005033 | Harrison West Compressor Station | Possum Hollow Road | Freeport | 43973 |  | Harrison | P004 | Compressor Engine #4 - 1980 HP (15.43 MMBtu/hr) Waukesha P9390 - natural gas-fired four-stroke rich burn internal combustion engine equipped with a three-way oxidation catalyst controlling CH2O, CO, NOx, & VOCs by 80, 97, 98.5 & 66 percent respectively | 2016-04-28 | CC001(Catalytic Converter): Compressor Engine #1 - 3-way Catalyst; CC002(Catalytic Converter): Compressor Engine #2 - 3-way Catalyst; CC004(Catalytic Converter): Compressor Engine #4 - 3-way Catalyst | Air Hygiene, Inc | 1980 hp | 0.7 g/hp-hr | 1589 hp | 0.11 g/hp-hr | 10 | CO - Carbon Monoxide | PP | Y | NA
2016 | 1161 | 0661005040 | Crum Compressor Station | 52934 Town Highway 192 | Seneca Twp. | 43780 |  | Noble | P007 | One (1) Waukesha 7044GSI 1,680 hp compressor engine fitted with a 5-element non-selective catalytic reduction catalyst. | 2016-08-31 | C-1(Catalytic Converter): 5-element NSCR for compressor engine C-100; C-2(Catalytic Converter): 5-element NSCR for compressor engine C-200; C-3(Catalytic Converter): 5-element NSCR for compressor engine C-300; C-4(Catalytic Converter): 5-element NSCR for | Alliance Source Testing | 1680 hp | 2.0 g/hp-hr | 1330 hp | 0.11 g/hp-hr | 10 | CO - Carbon Monoxide | PP | Y | NA
2016 | 1171 | 0661005052 | Long Compressor Station | 55135 Batesville Rd | Quaker City | 43773 |  | Noble | P001 | 1,680 hp Waukesha 7044GSI NG Fired-rich burn-4stroke compressor engine | 2016-01-28 | C-01(Catalytic Converter): Non-selective catalyst reduction device for C-2000; C-02(Catalytic Converter): Non-selective catalyst reduction device for C-2100; C-03(Catalytic Converter): Non-selective catalyst reduction device for C-2200; C-04(Catalytic Con | Technical Compliance Solutions | 1680 hp | 2.00 g/hp-hr | 1628 hp | 0.11 g/hp-hr | 320 | CO - Carbon Monoxide | PP | Y | NA
2016 | 1172 | 0634005123 | Yoder Compressor Station | 79300 Cassville Rd | Cadiz | 43907 |  | Harrison | P003 | Natural gas-fired four-stroke lean burn (4SLB) internal combustion engine rated at an operating capacity of 2,370 horsepower (hp) and equipped with an oxidation catalyst. | 2016-05-19 | CC001(Catalytic Converter): Compressor Engine #1 Catalytic Converter; CC002(Catalytic Converter): Compressor Engine #2 Catalytic Converter; CC003(Catalytic Converter): Compressor Engine #3 Catalytic Converter | Air Hygiene International | 2370 hp | 0.73 lb/hr | 2185 hp | 0.11 lb/hr | 10 | CO - Carbon Monoxide | PP | Y | NA
2016 | 1173 | 0656025012 | Goliath Compressor Station | 48208 St Rte 556 | Beallsville | 43716 |  | Monroe | P004 | Compressor #4 - driven by Caterpillar G3608 engine | 2016-01-13 | C304Catalyst(Other): null | Technical Compliance Solutions | 2370 hp | 1.1 lbs/hr | 1501 hp | 0.11 lb/hr | 320 | CO - Carbon Monoxide | PP | Y | NA
2016 | 1174 | 0656005025 | REX Booster Station | Twp Rd 964 | Switzerland Twp. | 43915 |  | Monroe | P001 | Caterpillar 3616 Compressor Engine. This is a natural gas fired engine associated with the Compressor Unit | 2016-05-04 | C001(Catalytic Converter): Oxidation Catalysts; C002(Catalytic Converter): Oxidation Catalysts; C003(Catalytic Converter): Oxidation Catalysts | Alliance Source Testing | 4725 hp | 2.0 lbs/hr 93% control | 4451 hp | 0.11 lb/hr 99% control | 10 | CO - Carbon Monoxide | PP | Y | NA
2016 | 1175 | 0210012002 | Utica Gas Services, LLC-Carrollton Compressor Facility | 2098 Panda Road SE | Carrollton | 44615 |  | Carroll | P011 | 1,775 HP natural gas-fired Caterpillar G3606 engine #8 equipped with an oxidation catalyst | 2016-01-07 | Oxid. Cat.(Catalytic Converter): Oxidative Catalyst | Alliance Source Testing | 1775 HP | 1.18lbs/hr, 2.0g/hp-hr | 1657 HP | 0.11 lb/hr, 0.03 g/hp-hr | 10 | CO - Carbon Monoxide | PP | Y | NA
2016 | 1186 | 0661005027 | E2 Appalachian LLC - Batesville | 58380 St John Rd | Quaker City | 43773 |  | Noble | P006 | 1,680 Hp. Waukesha (L7044GSI) natural gas-fired, rich burn, turbocharged, with oxidation catalyst, compressor engine | 2016-07-12 | C2706C(Catalytic Converter): Engine Catalyst | Alliance Source Testing | 1,680 hp | 0.254 g/hp-hr | 1,490 hp | 0.116 g/hp-hr | 10 | CO - Carbon Monoxide | PP | Y | NA
2016 | 1187 | 0630005041 | E2 Energy Services - Borton | 65483 Lydick Rd | Quaker City | 43773 |  | Guernsey | P002 | 1,680 Hp. Waukesha (L7044GSI) natural gas-fired, rich burn, turbocharged, with oxidation catalyst, compressor engine (Model Year 2014) | 2016-03-02 | C-2701C(Catalytic Converter): Engine Catalyst | E2 Energy Services | 1680 hp | 0.174 g/hp-hr | 1519 hp | 0.12 g/hp-hr | 6348 03 | CO - Carbon Monoxide | PP | N | NA
2016 | 1188 | 0634005034 | Lake Compressor Station | County Highway 21 | Freeport | 43973 |  | Harrison | P011 | Compressor Engine #9 - Waukesha L7042 - natural gas fired four-stroke, rich burn internal combustion engine rated at an operating capacity of 1,480 horsepower equipped with a three-way oxidation catalyst. | 2016-04-14 | CC004(Catalytic Converter): Compressor Engine #4 - 3-way Catalyst; CC005(Catalytic Converter): Compressor Engine #5 - 3-way Catalyst; CC011(Catalytic Converter): Compressor Engine #9 - 3-way Catalyst | Air Hygiene, Inc | 1980 hp | 2.0 g/hp-hr | 1079 hp | 0.12 g/hp-hr | 10 | CO - Carbon Monoxide | PP | N | NA | test did conform to test method-document locked
2016 | 1200 | 0634005090 | E2 Ohio Compression LLC - Mizer | 84500 Addy Rd | Cadiz | 43907 |  | Harrison | P010 | One stationary natural gas-fired spark ignition (SI) internal combustion engine (ICE) with a total horsepower (HP) of 1680 HP. Includes a 2007 and later model year engine manufactured after the applicable effective date identified in 40 CFR 60.4230(a)(3) | 2016-02-25 | Cat03(Catalytic Converter): 3-Way NSCR for 4SRB RICE | E2 Energy Services | 1680 hp | 0.22 g/hp-hr | 1534 hp | 0.12 g/hp-hr | 6348 03 | CO - Carbon Monoxide | PP | Y | NA
2016 | 1238 | 0634005090 | E2 Ohio Compression LLC - Mizer | 84500 Addy Rd | Cadiz | 43907 |  | Harrison | P011 | One stationary natural gas-fired spark ignition (SI) internal combustion engine (ICE) with a total horsepower (HP) of 1680 HP. Includes a 2007 and later model year engine manufactured after the applicable effective date identified in 40 CFR 60.4230(a)(3) | 2016-02-26 | Cat04(Catalytic Converter): 3-Way NSCR for 4SLB Rice | E2 Energy Services | 1680 hp | 0.22 g/hp-hr | 1431 hp | 0.12 g/hp-hr | 6348 03 | CO - Carbon Monoxide | PP | Y | NA
2016 | 1241 | 0656005014 | StatOil USA Onshore Properties Inc - Dangle PAD | 49675 Dangel Lane | Sardis | 43946 |  | Monroe | P002 | One or multiple stationary natural gas-fired spark ignition (SI) internal combustion engines (ICE) with a combined total horsepower (HP) of no more than 1,800 HP for the site.* Includes 2007 and later model year engines manufactured after the applicable | 2016-02-23 | catalyst | Ecotest Energy Services | 1775 hp | 2.0 g/hp-hr | 1600 hp | 0.12 g/hp-hr | 320 | CO - Carbon Monoxide | PP | Y | NA
2016 | 1244 | 0661005040 | Crum Compressor Station | 52934 Town Highway 192 | Seneca Twp. | 43780 |  | Noble | P009 | One (1) Waukesha 7044GSI 1,680 hp compressor engine fitted with a 5-element non-selective catalytic reduction catalyst. | 2016-08-31 | C-1(Catalytic Converter): 5-element NSCR for compressor engine C-100; C-2(Catalytic Converter): 5-element NSCR for compressor engine C-200; C-3(Catalytic Converter): 5-element NSCR for compressor engine C-300; C-4(Catalytic Converter): 5-element NSCR for | Alliance Source Testing | 1680 hp | 2.0 g/hp-hr | 1430 hp | 0.12 g/hp-hr | 10 | CO - Carbon Monoxide | PP | Y | NA
2016 | 1261 | 0661005052 | Long Compressor Station | 55135 Batesville Rd | Quaker City | 43773 |  | Noble | P004 | 1,680 hp Waukesha 7044GSI NG Fired-rich burn-4stroke compressor engine | 2016-01-28 | C-01(Catalytic Converter): Non-selective catalyst reduction device for C-2000; C-02(Catalytic Converter): Non-selective catalyst reduction device for C-2100; C-03(Catalytic Converter): Non-selective catalyst reduction device for C-2200; C-04(Catalytic Con | Technical Compliance Solutions | 1680 hp | 2.00 g/hp-hr | 1627 hp | 0.12 g/hp-hr | 320 | CO - Carbon Monoxide | PP | Y | NA
2016 | 1263 | 0661005060 | CNX Gas LLC - Noble 36 Well Pad | 45379 Gurewicz Rd | Summerfield | 43788 |  | Noble | P002 | NOT INSTALLED AT PERMIT ISSUANCE TIME One or multiple stationary natural gas-fired spark ignition (SI) internal combustion engines (ICE) with a combined total horsepower (HP) of no more than 1,000 HP for the site.* Includes 2007 and later model year eng | 2016-04-04 | NSCR | EcoTest Energy Services | VRU-68 hp Flash gas-400 hp | 4.0 g/hp-hr | VRU-22 hp Flash gas-100 hp | 0.12 g/hp-hr | 320 | CO - Carbon Monoxide | PP | Y | NA | these two engines combined are permitted as P002
2016 | 1267 | 0210012004 | Augusta Compressor Facility- Utica Gas Services, L.L.C. | 8034 Bane Rd NE | East Twp. | 44427 |  | Carroll | P006 | 1,775-hp Caterpillar G3606 Compressor Engine w/ Oxidation Catalyst | 2016-09-08 | Oxid. Cat. 3(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 4(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 5(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 6(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 7(Catalytic Converter): | EcoTest Energy Services | 1775 Hp | 1.18 lbs/hr, 2.0 g/hp/hr, 270ppmvd@15%O2 | 1600 Hp or 90.1% of Max | 0.12 lb/hr, 0.03 g/hp/hr, 5 ppmvd@15%O2 | 10 | CO - Carbon Monoxide | PP | Y | NA
2016 | 1269 | 0210012002 | Utica Gas Services, LLC-Carrollton Compressor Facility | 2098 Panda Road SE | Carrollton | 44615 |  | Carroll | P006 | 1,775 HP natural gas-fired Caterpillar G3606 engine #4 equipped with an oxidation catalyst | 2016-01-07 | Oxid. Cat.(Catalytic Converter): Oxidative Catalyst | Alliance Source Testing | 1775 HP | 1.18lbs/hr, 2.0g/hp-hr | 1627 HP | 0.12 lb/hr, 0.03 g/hp-hr | 10 | CO - Carbon Monoxide | PP | Y | NA
2016 | 1273 | 0656005028 | Miller Compressor Station | 51103 Twp Rd 847 | Seneca Twp. | 43788 |  | Monroe | P005 | Waukesha 1680 bhp Model L7044GSI 4-stroke Natural Gas Rich Burn Gas Compressor Engine Model Year 2014 controlled by a catalyst | 2016-06-22 | C-2701C(Catalytic Converter): Engine Catalyst; C-2702C(Catalytic Converter): Engine Catalyst; C-2703C(Catalytic Converter): Engine Catalyst; C-2704C(Catalytic Converter): Engine Catalyst; C-2705C(Catalytic Converter): Engine Catalyst; C-2706C(Catalytic Co | Alliance Source Testing | 1680 hp | 0.5 g/hp-hr | 1680 hp | 0.13 g/hp-hr | 10 | CO - Carbon Monoxide | PP | N | NA
2016 | 1276 | 0661005008 | Seneca Gas Plant | Zep Road | Summerfield | 43788 |  | Noble | P002 | Compressor Engine #2 - Natural gas-fired four-stroke lean burn (4SLB) internal combustion engine rated at an operating capacity of 4,735 horsepower (hp) and equipped with an oxidation catalyst. | 2016-03-17 | CC001(Catalytic Converter): Compressor Engine #1 - Catalyic Convertor; CC002(Catalytic Converter): Compressor Engine #2 - Catalytic Convertor | Air Hygiene International, Inc | 4735 hp | 0.14 g/hp-hr | 4187 hp | 0.13 g/hp-hr | 10 | CO - Carbon Monoxide | PP | Y | NA
2016 | 1282 | 0656105005 | E2 Appalachian Compression LLC - Reusser | Twp Hwy 68 and Twp Hwy 66 | Woodsfield | 43793 |  | Monroe | P004 | 1680 Hp. natural gas rich burn compressor engine - Waukesha L7044GSI | 2016-03-09 | C-4(Catalytic Converter): Engine #4 Catalyst | E2 Energy Services | 1680 hp | 0.94 lb/hr | 1481 hp | 0.13 lb/hr | 6348 03 | CO - Carbon Monoxide | PP | Y | NA
2016 | 1287 | 0661005027 | E2 Appalachian LLC - Batesville | 58380 St John Rd | Quaker City | 43773 |  | Noble | P001 | 1,680 Hp. Waukesha (L7044GSI) natural gas-fired, rich burn, turbocharged, with oxidation catalyst, compressor engine | 2016-07-11 | C2701C(Catalytic Converter): Engine Catalyst; C2707C(Catalytic Converter): Engine Catalyst; C2708C(Catalytic Converter): Engine Catalyst | Alliance Source Testing | 1,680 hp | 2.0 g/hp-hr | 1,529 hp | 0.131 g/hp-hr | 10 | CO - Carbon Monoxide | PP | Y | NA
2016 | 1288 | 0634005123 | Yoder Compressor Station | 79300 Cassville Rd | Cadiz | 43907 |  | Harrison | P002 | Natural gas-fired four-stroke lean burn (4SLB) internal combustion engine rated at an operating capacity of 2,370 horsepower (hp) and equipped with an oxidation catalyst. | 2016-05-19 | CC001(Catalytic Converter): Compressor Engine #1 Catalytic Converter; CC002(Catalytic Converter): Compressor Engine #2 Catalytic Converter; CC003(Catalytic Converter): Compressor Engine #3 Catalytic Converter | Air Hygiene International | 2370 hp | 0.73 lb/hr | 2202 hp | 0.14 lb/hr | 10 | CO - Carbon Monoxide | PP | Y | NA
2016 | 1294 | 0661005027 | E2 Appalachian LLC - Batesville | 58380 St John Rd | Quaker City | 43773 |  | Noble | P003 | 1,680 Hp. Waukesha (L7044GSI) natural gas-fired, rich burn, turbocharged, with oxidation catalyst, compressor engine | 2016-03-23 | C2703C(Catalytic Converter): Engine Catalyst | E2 Appalachian | 1680 hp | 2.0 g/hp-hr | 1348 hp | 0.1407 g/hp-hr | 6348 03 | CO - Carbon Monoxide | PP | Y | NA
2016 | 1295 | 0661005010 | E2 Appalachian Compression LLC - Upper Hill | Opossum Run Rd and Town Hwy 120 | Sarahsville | 43779 |  | Noble | P007 | 1,680 Hp. Waukesha (L7044GSI) natural gas-fired, rich burn, turbocharged, with oxidation catalyst, compressor engine. | 2016-03-17 | C-7(Catalytic Converter): Engine Catalyst; C-8(Catalytic Converter): Engine Catalyst | Alliance Source Testing | 1680 hp | 4.0 g/hp-hr | 1464 hp | 0.14g/hp-hr | 10 | CO - Carbon Monoxide | PP | Y | NA
2016 | 1296 | 0656105005 | E2 Appalachian Compression LLC - Reusser | Twp Hwy 68 and Twp Hwy 66 | Woodsfield | 43793 |  | Monroe | P008 | 1680 Hp. natural gas rich burn compressor engine - Waukesha L7044GSI | 2016-07-14 | C-1(Catalytic Converter): Engine Catalyst; C-2(Catalytic Converter): Engine Catalyst; C-3(Catalytic Converter): Engine #3 Catalyst; C-4(Catalytic Converter): Engine #4 Catalyst; C-5(Catalytic Converter): Engine #5 Catalyst; C-6(Catalytic Converter): Engin | Alliance Source Testing | 1680 hp | 0.94 lb/hr | 1680 hp | 0.15 lb/hr | 10 | CO - Carbon Monoxide | PP | Y | NA
2016 | 1303 | 0210012002 | Utica Gas Services, LLC-Carrollton Compressor Facility | 2098 Panda Road SE | Carrollton | 44615 |  | Carroll | P007 | 1,775 HP natural gas-fired Caterpillar G3606 engine #4 equipped with an oxidation catalyst | 2016-01-07 | Oxid. Cat.(Catalytic Converter): Oxidative Catalyst | Alliance Source Testing | 1775 HP | 1.18lbs/hr, 2.0g/hp-hr | 1710 HP | 0.15 lb/hr, 0.04 g/hp-hr | 10 | CO - Carbon Monoxide | PP | Y | NA
2016 | 1305 | 0630005041 | E2 Energy Services - Borton | 65483 Lydick Rd | Quaker City | 43773 |  | Guernsey | P004 | 1,680 Hp. Waukesha (L7044GSI) natural gas-fired, rich burn, turbocharged, with oxidation catalyst, compressor engine (Model Year 2014) | 2016-05-12 | C-2703C(Catalytic Converter): Engine Catalyst | E2 Energy Services | 1680 hp | 0.174 g/hp-hr | 1348 hp | 0.156 g/hp-hr | 6348 03 | CO - Carbon Monoxide | PP | Y | NA
2016 | 1311 | 0661005027 | E2 Appalachian LLC - Batesville | 58380 St John Rd | Quaker City | 43773 |  | Noble | P005 | 1,680 Hp. Waukesha (L7044GSI) natural gas-fired, rich burn, turbocharged, with oxidation catalyst, compressor engine | 2016-03-31 | C2705C(Catalytic Converter): Engine Catalyst | E2 Appalachian | 1680 hp | 2.0 g/hp-hr | 1425 hp | 0.1597 g/hp-hr | 6348 03 | CO - Carbon Monoxide | PP | Y | NA
2016 | 1312 | 0607015001 | Tri-County Compressor Station (MarkWest / Ohio Oil Gath | N of intersection of Hwy 379 and Town | Barnesville | 43713 |  | Belmont | P003 | Compressor Engine #3 - 1980 HP (15.43 MMBtu/hr) Waukesha P9390 - natural gas-fired four-stroke rich burn internal combustion engine equipped with a three-way oxidation catalyst controlling CH2O, CO, NOx, & VOCs by 80, 97, 98.5 & 66 percent respectively | 2016-08-17 | CC002(Catalytic Converter): Compressor Engine #2 - 3-way Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - 3-way Catalyst; CC004(Catalytic Converter): Compressor Engine #4 - 3-way Catalyst; CC005(Catalytic Converter): Compressor Engine #5 - 3-w | Air Hygiene Internatinal, Inc | 1,980 hp | 2.00 g/hp-hr | 1,681 hp | 0.16 g/hp-hr | 10 | CO - Carbon Monoxide | PP | Y | NA
2016 | 1318 | 0656105005 | E2 Appalachian Compression LLC - Reusser | Twp Hwy 68 and Twp Hwy 66 | Woodsfield | 43793 |  | Monroe | P005 | 1680 Hp. natural gas rich burn compressor engine - Waukesha L7044GSI | 2016-03-10 | C-5(Catalytic Converter): Engine #5 Catalyst | E2 Energy Services | 1680 hp | 0.94 lb/hr | 1479 hp | 0.16 lb/hr | 6348 03 | CO - Carbon Monoxide | PP | Y | NA
2016 | 1319 | 0210012004 | Augusta Compressor Facility- Utica Gas Services, L.L.C. | 8034 Bane Rd NE | East Twp. | 44427 |  | Carroll | P011 | 1,775-hp Caterpillar G3606 Compressor Engine w/ Oxidation Catalyst | 2016-09-08 | Oxid. Cat. 3(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 4(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 5(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 6(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 7(Catalytic Converter): | EcoTest Energy Services | 1775 Hp | 1.18 lbs/hr, 2.0 g/hp/hr, 270ppmvd@15%O2 | 1600 Hp or 90.1% of Max | 0.16 lbs/hr, 0.05 g/hp/hr, 7 ppmvd@15%O2 | 10 | CO - Carbon Monoxide | PP | Y | NA
2016 | 1320 | 0634005127 | Chesapeake Exploration LLC - Wright 35-11-5 Pad | Lightner House Rd | Scio | 43988 |  | Harrison | P002 | One or multiple stationary natural gas-fired spark ignition (SI) internal combustion engines (ICE) with a combined total horsepower (HP) of no more than 1,800 HP for the site.* Includes 2007 and later model year engines manufactured after the applicable | 2016-02-12 | catalyst | Alliance Source Testing | 211 hp | 4.0 g/hp-hr | 190 hp | 0.17 g/hp-hr | 10 | CO - Carbon Monoxide | PP | Y | NA
2016 | 1325 | 0656005028 | Miller Compressor Station | 51103 Twp Rd 847 | Seneca Twp. | 43788 |  | Monroe | P001 | Waukesha 1680 bhp Model L7044GSI 4-stroke Natural Gas Rich Burn Gas Compressor Engine Model Year 2014 controlled by a catalyst | 2016-06-22 | C-2701C(Catalytic Converter): Engine Catalyst; C-2702C(Catalytic Converter): Engine Catalyst; C-2703C(Catalytic Converter): Engine Catalyst; C-2704C(Catalytic Converter): Engine Catalyst; C-2705C(Catalytic Converter): Engine Catalyst; C-2706C(Catalytic Co | Alliance Source Testing | 1680 hp | 0.5 g/hp-hr | 1680 hp | 0.17 g/hp-hr | 10 | CO - Carbon Monoxide | PP | N | NA
2016 | 1327 | 0210012002 | Utica Gas Services, LLC-Carrollton Compressor Facility | 2098 Panda Road SE | Carrollton | 44615 |  | Carroll | P008 | 1,775 HP natural gas-fired Caterpillar G3606 engine #5 equipped with an oxidation catalyst | 2016-01-07 | Oxid. Cat.(Catalytic Converter): Oxidative Catalyst | Alliance Source Testing | 1775 HP | 1.18lbs/hr, 2.0g/hp-hr | 1710 HP | 0.17 lb/hr, 0.05 g/hp-hr | 10 | CO - Carbon Monoxide | PP | Y | NA
2016 | 1332 | 0607015001 | Tri-County Compressor Station (MarkWest / Ohio Oil Gath | N of intersection of Hwy 379 and Town | Barnesville | 43713 |  | Belmont | P007 | Compressor Engine #7 - 1980 HP (15.43 MMBtu/hr) Waukesha P9390 - natural gas-fired four-stroke rich burn internal combustion engine equipped with a three-way oxidation catalyst controlling CH2O, CO, NOx, & VOCs by 80, 97, 98.5 & 66 percent respectively | 2016-08-17 | CC002(Catalytic Converter): Compressor Engine #2 - 3-way Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - 3-way Catalyst; CC004(Catalytic Converter): Compressor Engine #4 - 3-way Catalyst; CC005(Catalytic Converter): Compressor Engine #5 - 3-w | Air Hygiene Internatinal, Inc | 1,980 hp | 2.00 g/hp-hr | 1,568 hp | 0.18 g/hp-hr | 10 | CO - Carbon Monoxide | PP | Y | NA
2016 | 1335 | 0656005028 | Miller Compressor Station | 51103 Twp Rd 847 | Seneca Twp. | 43788 |  | Monroe | P005 | Waukesha 1680 bhp Model L7044GSI 4-stroke Natural Gas Rich Burn Gas Compressor Engine Model Year 2014 controlled by a catalyst | 2016-02-05 | C-2705C(Catalytic Converter): Engine Catalyst | E2 Energy Services | 1680 hp | 0.5 g/hp-hr | 1542 hp | 0.18 g/hp-hr | 6348 03 | CO - Carbon Monoxide | PP | Y | NA
2016 | 1338 | 0656005028 | Miller Compressor Station | 51103 Twp Rd 847 | Seneca Twp. | 43788 |  | Monroe | P002 | Waukesha 1680 bhp Model L7044GSI 4-stroke Natural Gas Rich Burn Gas Compressor Engine Model Year 2014 controlled by a catalyst | 2016-06-22 | C-2701C(Catalytic Converter): Engine Catalyst; C-2702C(Catalytic Converter): Engine Catalyst; C-2703C(Catalytic Converter): Engine Catalyst; C-2704C(Catalytic Converter): Engine Catalyst; C-2705C(Catalytic Converter): Engine Catalyst; C-2706C(Catalytic Co | Alliance Source Testing | 1680 hp | 0.5 g/hp-hr | 1680 hp | 0.18 g/hp-hr | 10 | CO - Carbon Monoxide | PP | N | NA
2016 | 1341 | 0210012002 | Utica Gas Services, LLC-Carrollton Compressor Facility | 2098 Panda Road SE | Carrollton | 44615 |  | Carroll | P013 | 1,775 HP natural gas-fired Caterpillar G3606 engine #10equipped with an oxidation catalyst | 2016-01-07 | Oxid. Cat.(Catalytic Converter): Oxidative Catalyst | Alliance Source Testing | 1775 HP | 1.18lbs/hr, 2.0g/hp-hr | 1662 HP | 0.18 lb/hr, 0.1 g/hp-hr | 10 | CO - Carbon Monoxide | PP | Y | NA
2016 | 1343 | 0210012004 | Augusta Compressor Facility- Utica Gas Services, L.L.C. | 8034 Bane Rd NE | East Twp. | 44427 |  | Carroll | P010 | 1,775-hp Caterpillar G3606 Compressor Engine w/ Oxidation Catalyst | 2016-09-08 | Oxid. Cat. 3(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 4(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 5(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 6(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 7(Catalytic Converter): | EcoTest Energy Services | 1775 Hp | 1.18 lbs/hr, 2.0 g/hp/hr, 270ppmvd@15%O2 | 1600 Hp or 90.1% of Max | 0.18 lbs/hr, 0.06g/hp/hr, 7 ppmvd@15%O2 | 10 | CO - Carbon Monoxide | PP | Y | NA
2016 | 1347 | 0630005055 | Ascent Resources - Utica LLC - Eggleston Wellpad | 17146 Easton Rd | Salesville | 43778 |  | Guernsey | P002 | One or multiple stationary natural gas-fired spark ignition (SI) internal combustion engines (ICE) with a combined total horsepower (HP) of no more than 1,800 HP for the site. Includes 2007 and later model year engines manufactured after the applicable e | 2016-06-28 | catalyst | EcoTest Energy Resources | 211 hp | 2.0 g/hp-hr | 80 hp | 0.19 g/hp-hr | 320 | CO - Carbon Monoxide | PP | Y | NA
2016 | 1350 | 0634005090 | E2 Ohio Compression LLC - Mizer | 84500 Addy Rd | Cadiz | 43907 |  | Harrison | P009 | One stationary natural gas-fired spark ignition (SI) internal combustion engine (ICE) with a total horsepower (HP) of 1680 HP. Includes a 2007 and later model year engine manufactured after the applicable effective date identified in 40 CFR 60.4230(a)(3) | 2016-02-24 | Cat02(Catalytic Converter): 3-Way NSCR for 4SRB RICE | E2 Energy Services | 1680 hp | 0.22 g/hp-hr | 1563 hp | 0.19 g/hp-hr | 6348 03 | CO - Carbon Monoxide | PP | Y | NA
2016 | 1353 | 0656005028 | Miller Compressor Station | 51103 Twp Rd 847 | Seneca Twp. | 43788 |  | Monroe | P009 | Waukesha 1680 bhp Model L7044GSI 4-stroke Natural Gas Rich Burn Gas Compressor Engine Model Year 2014 controlled by a catalyst | 2016-06-22 | C-2701C(Catalytic Converter): Engine Catalyst; C-2702C(Catalytic Converter): Engine Catalyst; C-2703C(Catalytic Converter): Engine Catalyst; C-2704C(Catalytic Converter): Engine Catalyst; C-2705C(Catalytic Converter): Engine Catalyst; C-2706C(Catalytic Co | Alliance Source Testing | 1680 hp | 0.5 g/hp-hr | 1680 hp | 0.19 g/hp-hr | 10 | CO - Carbon Monoxide | PP | N | NA
2016 | 1356 | 0661005040 | Crum Compressor Station | 52934 Town Highway 192 | Seneca Twp. | 43780 |  | Noble | P002 | One (1) Waukesha 7044GSI 1,680 hp compressor engine fitted with a 5-element non-selective catalytic reduction catalyst. | 2016-08-31 | C-1(Catalytic Converter): 5-element NSCR for compressor engine C-100; C-2(Catalytic Converter): 5-element NSCR for compressor engine C-200; C-3(Catalytic Converter): 5-element NSCR for compressor engine C-300; C-4(Catalytic Converter): 5-element NSCR for | Alliance Source Testing | 1680 hp | 2.0 g/hp-hr | 1584 hp | 0.19 g/hp-hr | 10 | CO - Carbon Monoxide | PP | Y | NA
2016 | 1357 | 0661005040 | Crum Compressor Station | 52934 Town Highway 192 | Seneca Twp. | 43780 |  | Noble | P008 | One (1) Waukesha 7044GSI 1,680 hp compressor engine fitted with a 5-element non-selective catalytic reduction catalyst. | 2016-08-31 | C-1(Catalytic Converter): 5-element NSCR for compressor engine C-100; C-2(Catalytic Converter): 5-element NSCR for compressor engine C-200; C-3(Catalytic Converter): 5-element NSCR for compressor engine C-300; C-4(Catalytic Converter): 5-element NSCR for | Alliance Source Testing | 1680 hp | 2.0 g/hp-hr | 1451 hp | 0.19 g/hp-hr | 10 | CO - Carbon Monoxide | PP | Y | NA
2016 | 1360 | 0210012004 | Augusta Compressor Facility- Utica Gas Services, L.L.C. | 8034 Bane Rd NE | East Twp. | 44427 |  | Carroll | P009 | 1,775-hp Caterpillar G3606 Compressor Engine w/ Oxidation Catalyst | 2016-09-08 | Oxid. Cat. 3(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 4(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 5(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 6(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 7(Catalytic Converter): | EcoTest Energy Services | 1775 Hp | 1.18 lbs/hr, 2.0 g/hp/hr, 270ppmvd@15%O2 | 1650 Hp or 93% of Max | 0.19 lbs/hr, 0.05 g/hp/hr, 7 ppmvd@15%O2 | 10 | CO - Carbon Monoxide | PP | Y | NA
2016 | 1364 | 0661005027 | E2 Appalachian LLC - Batesville | 58380 St John Rd | Quaker City | 43773 |  | Noble | P001 | 1,680 Hp. Waukesha (L7044GSI) natural gas-fired, rich burn, turbocharged, with oxidation catalyst, compressor engine | 2016-04-13 | C2701C(Catalytic Converter): Engine Catalyst | E2 Appalachian | 1680 hp | 2.0 g/hp-hr | 1539 hp | 0.199 g/hp-hr | 6348 03 | CO - Carbon Monoxide | PP | Y | NA
2016 | 1367 | 0661005040 | Crum Compressor Station | 52934 Town Highway 192 | Seneca Twp. | 43780 |  | Noble | P001 | One (1) Waukesha 7044GSI 1,680 hp compressor engine fitted with a 5-element non-selective catalytic reduction catalyst. | 2016-08-31 | C-1(Catalytic Converter): 5-element NSCR for compressor engine C-100; C-2(Catalytic Converter): 5-element NSCR for compressor engine C-200; C-3(Catalytic Converter): 5-element NSCR for compressor engine C-300; C-4(Catalytic Converter): 5-element NSCR for | Alliance Source Testing | 1680 hp | 2.0 g/hp-hr | 1568 hp | 0.20 g/hp-hr | 10 | CO - Carbon Monoxide | PP | Y | NA
2016 | 1369 | 0634005034 | Lake Compressor Station | County Highway 21 | Freeport | 43973 |  | Harrison | P002 | Compressor Engine #2 - 1480 HP (11.39 MMBtu/hr) Waukesha L7042 - natural gas-fired four-stroke rich burn internal combustion engine equipped with a three-way oxidation catalyst controlling CH2O, CO, NOx, & VOCs by 80, 97, 98.5 & 66 percent respectively | 2016-03-28 | CC001(Catalytic Converter): Compressor Engine #1 - 3-way Catalyst; CC002(Catalytic Converter): Compressor Engine #2 - 3-way Catalyst | Air Hygiene, Inc. | 1480 hp | 0.25 g/hp-hr | 1374 hp | 0.21 g/hp-hr | 10 | CO - Carbon Monoxide | PP | Y | NA
2016 | 1372 | 0661005010 | E2 Appalachian Compression LLC - Upper Hill | Opossum Run Rd and Town Hwy 120 | Sarahsville | 43779 |  | Noble | P009 | 1,680 Hp. Waukesha (L7044GSI) natural gas-fired, rich burn, turbocharged, with oxidation catalyst, compressor engine. | 2016-04-29 | C-3(Catalytic Converter): Engine Catalyst; C-9(Catalytic Converter): Engine Catalyst | Alliance Source Testing | 1680 hp | 4.0 g/hp-hr | 1646 hp | 0.21 g/hp-hr | 10 | CO - Carbon Monoxide | PP | Y | NA
2016 | 1375 | 0661005010 | E2 Appalachian Compression LLC - Upper Hill | Opossum Run Rd and Town Hwy 120 | Sarahsville | 43779 |  | Noble | P009 | 1,680 Hp. Waukesha (L7044GSI) natural gas-fired, rich burn, turbocharged, with oxidation catalyst, compressor engine. | 2016-04-29 | C-3(Catalytic Converter): Engine Catalyst; C-9(Catalytic Converter): Engine Catalyst | Ecotest Energy Services | 1680 hp | 4.0 g/hp-hr | 1646 hp | 0.21 g/hp-hr | 6348 03 | CO - Carbon Monoxide | PP | Y | NA
2016 | 1381 | 0661005040 | Crum Compressor Station | 52934 Town Highway 192 | Seneca Twp. | 43780 |  | Noble | P005 | One (1) Waukesha 7044GSI 1,680 hp compressor engine fitted with a 5-element non-selective catalytic reduction catalyst. | 2016-08-31 | C-1(Catalytic Converter): 5-element NSCR for compressor engine C-100; C-2(Catalytic Converter): 5-element NSCR for compressor engine C-200; C-3(Catalytic Converter): 5-element NSCR for compressor engine C-300; C-4(Catalytic Converter): 5-element NSCR for | Alliance Source Testing | 1680 hp | 2.0 g/hp-hr | 1503 hp | 0.21 g/hp-hr | 10 | CO - Carbon Monoxide | PP | Y | NA
2016 | 1382 | 0210012002 | Utica Gas Services, LLC-Carrollton Compressor Facility | 2098 Panda Road SE | Carrollton | 44615 |  | Carroll | P009 | 1,775 HP natural gas-fired Caterpillar G3606 engine #6 equipped with an oxidation catalyst | 2016-01-07 | Oxid. Cat.(Catalytic Converter): Oxidative Catalyst | Alliance Source Testing | 1775 HP | 1.18lbs/hr, 2.0g/hp-hr | 1656 HP | 0.21 lb/hr, 0.10 g/hp-hr | 10 | CO - Carbon Monoxide | PP | Y | NA
2016 | 1383 | 0210012004 | Augusta Compressor Facility- Utica Gas Services, L.L.C. | 8034 Bane Rd NE | East Twp. | 44427 |  | Carroll | P008 | 1,775-hp Caterpillar G3606 Compressor Engine w/ Oxidation Catalyst | 2016-09-08 | Oxid. Cat. 3(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 4(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 5(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 6(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 7(Catalytic Converter): | EcoTest Energy Services | 1775 Hp | 1.18 lbs/hr, 2.0 g/hp/hr, 270ppmvd@15%O2 | 1628 Hp or 91.7% of Max | 0.21 lbs/hr, 0.6 g/hp/hr, 8 ppmvd@15%O2 | 10 | CO - Carbon Monoxide | PP | Y | NA
2016 | 1388 | 0661005040 | Crum Compressor Station | 52934 Town Highway 192 | Seneca Twp. | 43780 |  | Noble | P006 | One (1) Waukesha 7044GSI 1,680 hp compressor engine fitted with a 5-element non-selective catalytic reduction catalyst. | 2016-08-31 | C-1(Catalytic Converter): 5-element NSCR for compressor engine C-100; C-2(Catalytic Converter): 5-element NSCR for compressor engine C-200; C-3(Catalytic Converter): 5-element NSCR for compressor engine C-300; C-4(Catalytic Converter): 5-element NSCR for | Alliance Source Testing | 1680 hp | 2.0 g/hp-hr | 1533 hp | 0.23 g/hp-hr | 10 | CO - Carbon Monoxide | PP | Y | NA
2016 | 1443 | 0656035009 | Eureka Midstream-Zink Compressor Station | 51213 Krebs Hill Rd | Clarington | 43915 |  | Monroe | P006 | Natural Gas Fueled Lean Burn 4-Stroke Caterpillar G3608TALE Compressor Engine | 2016-04-12 | catalyst | EcoTest Energy Services | 2370 hp | 1.432 lb/hr | 2150 hp | 0.23 lb/hr | 320 | CO - Carbon Monoxide | PP | Y | NA | P006 serial number BEN00694 P007 serial number BEN00693
2016 | 1444 | 0661005010 | E2 Appalachian Compression LLC - Upper Hill | Opossum Run Rd and Town Hwy 120 | Sarahsville | 43779 |  | Noble | P008 | 1,680 Hp. Waukesha (L7044GSI) natural gas-fired, rich burn, turbocharged, with oxidation catalyst, compressor engine. | 2016-03-17 | C-7(Catalytic Converter): Engine Catalyst; C-8(Catalytic Converter): Engine Catalyst | Alliance Source Testing | 1680 hp | 4.0 g/hp-hr | 1406 hp | 0.24 g/hp-hr | 10 | CO - Carbon Monoxide | PP | Y | NA
2016 | 1445 | 0656005025 | REX Booster Station | Twp Rd 964 | Switzerland Twp. | 43915 |  | Monroe | P002 | Caterpillar 3616 Compressor Engine. This is a natural gas fired engine associated with the Compressor Unit | 2016-05-04 | C001(Catalytic Converter): Oxidation Catalysts; C002(Catalytic Converter): Oxidation Catalysts; C003(Catalytic Converter): Oxidation Catalysts | Alliance Source Testing | 4725 hp | 2.0 lbs/hr 93% control | 4451 hp | 0.24 lbs/hr 98% control | 10 | CO - Carbon Monoxide | PP | Y | NA
2016 | 1451 | 0661005027 | E2 Appalachian LLC - Batesville | 58380 St John Rd | Quaker City | 43773 |  | Noble | P002 | 1,680 Hp. Waukesha (L7044GSI) natural gas-fired, rich burn, turbocharged, with oxidation catalyst, compressor engine | 2016-04-28 | C2702C(Catalytic Converter): Engine Catalyst | Alliance Source Testing | 1680 hp | 2.0 g/hp-hr | 1529 hp | 0.242 g/hp-hr | 10 | CO - Carbon Monoxide | PP | N | NA
2016 | 1454 | 0634005070 | Gulfport Energy - County Line II - Gustina-Bear | 34011 Cadiz-Piedmont Rd | Flushing | 43977 |  | Harrison | P002 | One or multiple stationary natural gas-fired spark ignition (SI) internal combustion engines (ICE) wiht a combined total horsepower (HP) of no more than 1,800 HP for the site. | 2016-02-17 | cagalyst | Ecotest Energy Services | 118 hp | 4.0 g/hp-hr | 90 hp | 0.25 g/hp-hr | 6348 03 | CO - Carbon Monoxide | PP | Y | NA
2016 | 1456 | 0656065006 | Antero Resources - Hercher Pad | 39886 Township Rd | Lewisville | 43754 |  | Monroe | P002 | One or multiple stationary natural gas-fired spark ignition (SI) internal combustion engines (ICE) with a combined total horsepower (HP) of no more than 1,800 HP for the site.* Includes 2007 and later model year engines manufactured after the applicable | 2016-02-05 | catalyst | Technical Compliance Solutions | 1,775 hp | 3.0 g/hp-hr | 1,605 hp | 0.25 g/hp-hr | 320 | CO - Carbon Monoxide | PP | Y | NA
2016 | 1459 | 0661005027 | E2 Appalachian LLC - Batesville | 58380 St John Rd | Quaker City | 43773 |  | Noble | P006 | 1,680 Hp. Waukesha (L7044GSI) natural gas-fired, rich burn, turbocharged, with oxidation catalyst, compressor engine | 2016-04-01 | C2705C(Catalytic Converter): Engine Catalyst | E2 Appalachian | 1680 hp | 0.254 g/hp-hr | 1551 hp | 0.2585 g/hp-hr | 6348 03 | CO - Carbon Monoxide | FF | Y | NA
2016 | 1465 | 0656005028 | Miller Compressor Station | 51103 Twp Rd 847 | Seneca Twp. | 43788 |  | Monroe | P007 | Waukesha 1680 bhp Model L7044GSI 4-stroke Natural Gas Rich Burn Gas Compressor Engine Model Year 2014 controlled by a catalyst | 2016-01-27 | C-2707C(Catalytic Converter): Engine Catalyst | E2 Energy Services | 1680 hp | 0.5 g/hp-hr | 1542 hp | 0.26 g/hp-hr | 6348 03 | CO - Carbon Monoxide | PP | Y | NA
2016 | 1466 | 0656035009 | Eureka Midstream-Zink Compressor Station | 51213 Krebs Hill Rd | Clarington | 43915 |  | Monroe | P007 | Natural Gas Fueled Lean Burn 4-Stroke Caterpillar G3608TALE Compressor Engine | 2016-04-12 | catalyst | EcoTest Energy Services | 2370 hp | 1.432 lb/hr | 2150 hp | 0.26 lb/hr | 320 | CO - Carbon Monoxide | PP | Y | NA | P006 serial number BEN00694 P007 serial number BEN00693
2016 | 1467 | 0661005040 | Crum Compressor Station | 52934 Town Highway 192 | Seneca Twp. | 43780 |  | Noble | P003 | One (1) Waukesha 7044GSI 1,680 hp compressor engine fitted with a 5-element non-selective catalytic reduction catalyst. | 2016-08-31 | C-1(Catalytic Converter): 5-element NSCR for compressor engine C-100; C-2(Catalytic Converter): 5-element NSCR for compressor engine C-200; C-3(Catalytic Converter): 5-element NSCR for compressor engine C-300; C-4(Catalytic Converter): 5-element NSCR for | Alliance Source Testing | 1680 hp | 2.0 g/hp-hr | 1558 hp | 0.27 g/hp-hr | 10 | CO - Carbon Monoxide | PP | Y | NA
2016 | 1468 | 0661005027 | E2 Appalachian LLC - Batesville | 58380 St John Rd | Quaker City | 43773 |  | Noble | P004 | 1,680 Hp. Waukesha (L7044GSI) natural gas-fired, rich burn, turbocharged, with oxidation catalyst, compressor engine | 2016-03-30 | C2704C(Catalytic Converter): Engine Catalyst | E2 Appalachian | 1680 hp | 2.0 g/hp-hr | 1470 hp | 0.2795 g/hp-hr | 6348 03 | CO - Carbon Monoxide | PP | Y | NA
2016 | 1477 | 0630005054 | Ascent Resources - Utica LLC - J Bar J Wellpad | 25204 Oxford Rd | Quaker City | 43773 |  | Guernsey | P002 | One or multiple stationary natural gas-fired spark ignition (SI) internal combustion engines (ICE) with a combined total horsepower (HP) of no more than 1,800 HP for the site. Includes 2007 and later model year engines manufactured after the applicable e | 2016-03-08 | catalyst | Great Plains Analytical Services, Inc | 211 hp | 2.0 g/hp-hr | 117 hp | 0.306 g/hp-hr | 6348 03 | CO - Carbon Monoxide | PP | Y | NA
2016 | 1480 | 0630005039 | E2 Ohio Compression LLC - Hayes | 21260 Grape Hollow Rd | Salesville | 43778 |  | Guernsey | P032 | Cat G350B 690 HP NG engine | 2016-08-31 | Cat01(Catalytic Converter): Oxidation Catalyst for 4SLB RICE | E2Energy Services | 690 hp | 2.00 g/hp-hr | 345 hp | 0.31 g/hp-hr | 6348 03 | CO - Carbon Monoxide | PP | Y | NA
2016 | 1485 | 0656105005 | E2 Appalachian Compression LLC - Reusser | Twp Hwy 68 and Twp Hwy 66 | Woodsfield | 43793 |  | Monroe | P005 | 1680 Hp. natural gas rich burn compressor engine - Waukesha L7044GSI | 2016-07-14 | C-1(Catalytic Converter): Engine Catalyst; C-2(Catalytic Converter): Engine Catalyst; C-3(Catalytic Converter): Engine #3 Catalyst; C-4(Catalytic Converter): Engine #4 Catalyst; C-5(Catalytic Converter): Engine #5 Catalyst; C-6(Catalytic Converter): Engin | Alliance Source Testing | 1680 hp | 0.94 lb/hr | 1613 hp | 0.31 lb/hr | 10 | CO - Carbon Monoxide | PP | Y | NA
2016 | 1487 | 0656005025 | REX Booster Station | Twp Rd 964 | Switzerland Twp. | 43915 |  | Monroe | P003 | Caterpillar 3616 Compressor Engine. This is a natural gas fired engine associated with the Compressor Unit | 2016-05-04 | C001(Catalytic Converter): Oxidation Catalysts; C002(Catalytic Converter): Oxidation Catalysts; C003(Catalytic Converter): Oxidation Catalysts | Alliance Source Testing | 4725 hp | 2.0 lbs/hr 93% control | 4514 hp | 0.32 lbs/hr 98% control | 10 | CO - Carbon Monoxide | PP | Y | NA
2016 | 1491 | 0546015002 | Bellefontaine Gas Producers, LLC | 2946 US Route 68 North | Bellefontaine | 43311 |  | Logan | P001 | 2275 Hp, 4-stroke lean burn, non-emergency, spark ignition RICE; Ch. 31 modification issued 1/8/2014. | 2016-04-12 | N/A | DTE Energy | 2,275 BHp | 0.6 g/bhp-hr | +> 2047.5 BHp | 0.36 g/bhp-hr | 10B | CO - Carbon Monoxide | PP | Y | Y
2016 | 1501 | 0661005027 | E2 Appalachian LLC - Batesville | 58380 St John Rd | Quaker City | 43773 |  | Noble | P002 | 1,680 Hp. Waukesha (L7044GSI) natural gas-fired, rich burn, turbocharged, with oxidation catalyst, compressor engine | 2016-03-24 | C2702C(Catalytic Converter): Engine Catalyst | E2 Appalachian | 1680 hp | 2.0 g/hp-hr | 1473 hp | 0.384 g/hp-hr | 6348 03 | CO - Carbon Monoxide | PP | Y | NA
2016 | 1502 | 0661005027 | E2 Appalachian LLC - Batesville | 58380 St John Rd | Quaker City | 43773 |  | Noble | P002 | 1,680 Hp. Waukesha (L7044GSI) natural gas-fired, rich burn, turbocharged, with oxidation catalyst, compressor engine | 2016-04-14 | C2702C(Catalytic Converter): Engine Catalyst | E2 Energy Services | 1680 hp | 2.0 g/hp-hr | 1473 hp | 0.384 g/hp-hr | 6348 03 | CO - Carbon Monoxide | PP | N | NA
2016 | 1503 | 0630005035 | Ascent Resources - Utica LLC - Coad 12-9N-7W | 25595 Oxford Rd | Quaker City | 43773 |  | Guernsey | P002 | One or multiple stationary natural gas-fired spark ignition (SI) internal combustion engines (ICE) with a combined total horsepower (HP) of no more than 1,800 HP for the site. Includes 2007 and later model year engines manufactured after the applicable e | 2016-03-08 | catalyst | Great Plains Analytical Services | 211 hp | 2.0 g/hp-hr | 116 hp | 0.386 g/hp-hr | 6348 03 | CO - Carbon Monoxide | PP | Y | NA
2016 | 1504 | 0661005027 | E2 Appalachian LLC - Batesville | 58380 St John Rd | Quaker City | 43773 |  | Noble | P008 | 1,680 Hp. Waukesha (L7044GSI) natural gas-fired, rich burn, turbocharged, with oxidation catalyst, compressor engine | 2016-04-14 | C2708C(Catalytic Converter): Engine Catalyst | E2 Appalachian | 1680 hp | 2.0 g/hp-hr | 1475 hp | 0.4356 g/hp-hr | 6348 03 | CO - Carbon Monoxide | PP | Y | NA
2016 | 1505 | 0656105005 | E2 Appalachian Compression LLC - Reusser | Twp Hwy 68 and Twp Hwy 66 | Woodsfield | 43793 |  | Monroe | P001 | 1680 Hp. natural gas rich burn compressor engine - Waukesha L7044GSI | 2016-07-14 | C-1(Catalytic Converter): Engine Catalyst; C-2(Catalytic Converter): Engine Catalyst; C-3(Catalytic Converter): Engine #3 Catalyst; C-4(Catalytic Converter): Engine #4 Catalyst; C-5(Catalytic Converter): Engine #5 Catalyst; C-6(Catalytic Converter): Engin | Alliance Source Testing | 1680 hp | 0.94 lb/hr | 1646 hp | 0.44 lb/hr | 10 | CO - Carbon Monoxide | PP | Y | NA
2016 | 1506 | 0656105005 | E2 Appalachian Compression LLC - Reusser | Twp Hwy 68 and Twp Hwy 66 | Woodsfield | 43793 |  | Monroe | P009 | 1680 Hp. natural gas rich burn compressor engine - Waukesha L7044GSI | 2016-07-14 | C-1(Catalytic Converter): Engine Catalyst; C-2(Catalytic Converter): Engine Catalyst; C-3(Catalytic Converter): Engine #3 Catalyst; C-4(Catalytic Converter): Engine #4 Catalyst; C-5(Catalytic Converter): Engine #5 Catalyst; C-6(Catalytic Converter): Engin | Alliance Source Testing | 1680 hp | 0.94 lb/hr | 1404 hp | 0.47 lb/hr | 10 | CO - Carbon Monoxide | PP | Y | NA
2016 | 1507 | 0656105005 | E2 Appalachian Compression LLC - Reusser | Twp Hwy 68 and Twp Hwy 66 | Woodsfield | 43793 |  | Monroe | P002 | 1680 Hp. natural gas rich burn compressor engine - Waukesha L7044GSI | 2016-07-14 | C-1(Catalytic Converter): Engine Catalyst; C-2(Catalytic Converter): Engine Catalyst; C-3(Catalytic Converter): Engine #3 Catalyst; C-4(Catalytic Converter): Engine #4 Catalyst; C-5(Catalytic Converter): Engine #5 Catalyst; C-6(Catalytic Converter): Engin | Alliance Source Testing | 1680 hp | 0.94 lb/hr | 1457 hp | 0.53 lb/hr | 10 | CO - Carbon Monoxide | PP | Y | NA
2016 | 1508 | 0656065002 | Antero Resources- Webb Pad | 42006 Sandbar Rd | Lewisville | 43754 |  | Monroe | P002 | One or multiple stationary natural gas-fired spark ignition (SI) internal combustion engines (ICE) with a combined total horsepower (HP) of no more than 1,800 HP for the site.* Includes 2007 and later model year engines manufactured after the applicable | 2016-02-05 | catalyst | Techhical Compliance Solutions | 400 hp | 4.0 g/hp-hr | 379 hp | 0.54 g/hp-hr | 320 | CO - Carbon Monoxide | PP | N | NA
2016 | 1509 | 0656105005 | E2 Appalachian Compression LLC - Reusser | Twp Hwy 68 and Twp Hwy 66 | Woodsfield | 43793 |  | Monroe | P007 | 1680 Hp. natural gas rich burn compressor engine - Waukesha L7044GSI | 2016-07-14 | C-1(Catalytic Converter): Engine Catalyst; C-2(Catalytic Converter): Engine Catalyst; C-3(Catalytic Converter): Engine #3 Catalyst; C-4(Catalytic Converter): Engine #4 Catalyst; C-5(Catalytic Converter): Engine #5 Catalyst; C-6(Catalytic Converter): Engin | Alliance Source Testing | 1680 hp | 0.94 lb/hr | 1646 hp | 0.54 lb/hr | 10 | CO - Carbon Monoxide | PP | Y | NA
2016 | 1520 | 0661005010 | E2 Appalachian Compression LLC - Upper Hill | Opossum Run Rd and Town Hwy 120 | Sarahsville | 43779 |  | Noble | P003 | 1,680 Hp. Waukesha (L7044GSI) natural gas-fired, rich burn, turbocharged, with oxidation catalyst, compressor engine. | 2016-04-29 | C-3(Catalytic Converter): Engine Catalyst; C-9(Catalytic Converter): Engine Catalyst | Alliance Source Testing | 1680 hp | 4.0 g/hp-hr | 1658 hp | 0.57 g/hp-hr | 10 | CO - Carbon Monoxide | PP | Y | NA
2016 | 1523 | 0661005010 | E2 Appalachian Compression LLC - Upper Hill | Opossum Run Rd and Town Hwy 120 | Sarahsville | 43779 |  | Noble | P003 | 1,680 Hp. Waukesha (L7044GSI) natural gas-fired, rich burn, turbocharged, with oxidation catalyst, compressor engine. | 2016-04-29 | C-3(Catalytic Converter): Engine Catalyst; C-9(Catalytic Converter): Engine Catalyst | Ecotest Energy Services | 1680 hp | 4.0 g/hp-hr | 1658 hp | 0.57 g/hp-hr | 6348 03 | CO - Carbon Monoxide | PP | Y | NA
2016 | 1525 | 0656105005 | E2 Appalachian Compression LLC - Reusser | Twp Hwy 68 and Twp Hwy 66 | Woodsfield | 43793 |  | Monroe | P007 | 1680 Hp. natural gas rich burn compressor engine - Waukesha L7044GSI | 2016-03-18 | C-7(Catalytic Converter): Engine #7Catalyst | E2 Energy Services | 1680 hp | 0.94 lb/hr | 1535 hp | 0.65 lb/hr | 6348 03 | CO - Carbon Monoxide | PP | Y | NA
2016 | 1532 | 0656105005 | E2 Appalachian Compression LLC - Reusser | Twp Hwy 68 and Twp Hwy 66 | Woodsfield | 43793 |  | Monroe | P006 | 1680 Hp. natural gas rich burn compressor engine - Waukesha L7044GSI | 2016-03-10 | C-6(Catalytic Converter): Engine #6Catalyst | E2 Energy Services | 1680 hp | 0.94 lb/hr | 1592 hp | 0.66 lb/hr | 6348 03 | CO - Carbon Monoxide | PP | Y | NA
2016 | 1536 | 0656105005 | E2 Appalachian Compression LLC - Reusser | Twp Hwy 68 and Twp Hwy 66 | Woodsfield | 43793 |  | Monroe | P008 | 1680 Hp. natural gas rich burn compressor engine - Waukesha L7044GSI | 2016-03-11 | C-7(Catalytic Converter): Engine #7Catalyst | E2 Energy Services | 1680 hp | 0.94 lb/hr | 1548 hp | 0.75 lb/hr | 6348 03 | CO - Carbon Monoxide | PP | Y | NA
2016 | 1537 | 0656105005 | E2 Appalachian Compression LLC - Reusser | Twp Hwy 68 and Twp Hwy 66 | Woodsfield | 43793 |  | Monroe | P003 | 1680 Hp. natural gas rich burn compressor engine - Waukesha L7044GSI | 2016-07-14 | C-1(Catalytic Converter): Engine Catalyst; C-2(Catalytic Converter): Engine Catalyst; C-3(Catalytic Converter): Engine #3 Catalyst; C-4(Catalytic Converter): Engine #4 Catalyst; C-5(Catalytic Converter): Engine #5 Catalyst; C-6(Catalytic Converter): Engin | Alliance Source Testing | 1680 hp | 0.94 lb/hr | 1658 hp | 0.76 lb/hr | 10 | CO - Carbon Monoxide | PP | Y | NA
2016 | 1543 | 0238000050 | MILEY COMPRESSOR STATION | 7531 State Rte 514 | Ripley Twp. | 44611 |  | Holmes | B004 | White Superior 8G-825, 4-cycle, rich burn, natural gas-fired reciprocating pipeline compressor engine, having a maximum capacity of 780hp, controlled by a Non-Selective Catalytic Reduction. (Compressor #07702 - B004) | 2016-05-19 | TWC | Lemos Labs. | 780 Hp | 270 ppmvd @ 15% O2 | < 90% | 0.9 ppmvd @ 15% O2 | 10 | CO - Carbon Monoxide | PP | Y | NA
2016 | 1545 | 0656105005 | E2 Appalachian Compression LLC - Reusser | Twp Hwy 68 and Twp Hwy 66 | Woodsfield | 43793 |  | Monroe | P004 | 1680 Hp. natural gas rich burn compressor engine - Waukesha L7044GSI | 2016-07-14 | C-1(Catalytic Converter): Engine Catalyst; C-2(Catalytic Converter): Engine Catalyst; C-3(Catalytic Converter): Engine #3 Catalyst; C-4(Catalytic Converter): Engine #4 Catalyst; C-5(Catalytic Converter): Engine #5 Catalyst; C-6(Catalytic Converter): Engin | Alliance Source Testing | 1680 hp | 0.94 lb/hr | 1680 hp | 0.94 lb/hr | 10 | CO - Carbon Monoxide | PP | Y | NA
2016 | 1550 | 0656105005 | E2 Appalachian Compression LLC - Reusser | Twp Hwy 68 and Twp Hwy 66 | Woodsfield | 43793 |  | Monroe | P001 | 1680 Hp. natural gas rich burn compressor engine - Waukesha L7044GSI | 2016-03-18 | C-1(Catalytic Converter): Engine Catalyst | E2 Energy Services | 1680 hp | 0.94 lb/hr | 1538 hp | 0.98 lb/hr | 6348 03 | CO - Carbon Monoxide | FF | Y | NA
2016 | 1553 | 0630005050 | Carrizo Utica LLC- Wagler Production Facility | Deck Rd | Londonderry Twp. | 45647 |  | Guernsey | P002 | One or multiple stationary natural gas-fired spark ignition (SI) internal combustion engines (ICE) with a combined total horsepower of 1,800 HP for the site. Includes 2007 or later model year engines manufactured after the applicable effective date iden | 2016-04-11 | catalyst | Alliance Source Testing | 275 hp | 2.0 g/hp-hr | 263 hp | 1.3 g/hp-hr | 10 | CO - Carbon Monoxide | PP | Y | NA
2016 | 1554 | 0656035012 | CNX Gas LLC - Switz 6 Production Facility | 49498 SR 556 | Clarington | 43915 |  | Monroe | P002 | NOT INSTALLED AT PERMIT ISSUANCE TIME NG engine | 2016-05-16 | catalyst | Ecotest Energy Services | 68 hp, 276 hp 425 hp | 4.0 g/hp-hr | 35 hp, 102 hp, 188 hp | 1.37 g/hp-hr | 320 | CO - Carbon Monoxide | PP | Y | NA | 425 hp engine, 276 hp and 68 hp engine combined allowable for P002
2016 | 1557 | 0656035012 | CNX Gas LLC - Switz 6 Production Facility | 49498 SR 556 | Clarington | 43915 |  | Monroe | P002 | NOT INSTALLED AT PERMIT ISSUANCE TIME NG engine | 2016-06-01 | catalyst | Ecotest Energy Services | 68 hp, 276 hp 425 hp | 4.0 g/hp-hr | 35 hp, 102 hp, 188 hp | 1.37 g/hp-hr | 320 | CO - Carbon Monoxide | PP | Y | NA | 425 hp engine, 276 hp and 68 hp engine combined allowable for P002
2016 | 1565 | 0634005121 | Ascent Resources - Utica LLC - Pettay Well Pad | 3440 Huff Run Rd | Cadiz | 43907 |  | Harrison | P002 | One or multiple stationary natural gas-fired spark ignition (SI) internal combustion engines (ICE) with a combined total horsepower (HP) of no more than 1,800 HP for the site. Includes 2007 and later model year engines manufactured after the applicable e | 2016-05-25 | catalyst | Great Plains Analytical Services | 276 hp 225 hp | 4.0 g/hp-hr | 216 hp 154 hp | 1.62 g/hp-hr | 6348 03 | CO - Carbon Monoxide | PP | N | NA | two engines 276 hp and 225 hp. emissions rates and allowable combined
2016 | 1580 | 0661005042 | CNX Gas LLC., Noble 19 | 51109 Lew Martin Rd | Summerfield | 43778 |  | Noble | P002 | One or multiple stationary natural gas-fired spark ignition (SI) internal combustion engines (ICE) with a combined total horsepower of 1,800 HP for the site. Includes 2007 or later model year engines manufactured after the applicable effective date iden | 2016-05-17 | catalyst | Ecotest Energy Services | 380 hp 84 hp | 4.0 g/hp-hr | 165 hp 55 hp | 1.88 g/hp-hr | 6348 03 | CO - Carbon Monoxide | PP | Y | NA | 380 hp flash gas unit and 84 hp VRU compressor engine-P002 allowable combined and results combined
2016 | 1596 | 0250000911 | East Ohio Gas Company - Austintown | 9686 NEW ROAD | Austintown Twp. | 44451 | 9708 | Mahoning | B001 | Natural gas-fired Caterpillar Model G3516LE, 4 stroke lean burn (4SLB) spark ignition (SI) reciprocating internal combustion engine (RICE) with an oxidation catalyst rated at 1265 HP (9.55 MMBtu/hr); complying with emission limitations in 40 CFR 63, Subpa | 2016-03-22 | Oxidative Catalyst 1(Other): B001 Catalytic Oxidizer; Oxidative Catalyst 2(Other): B002 Catalytic oxidizer | Environmental Quality Management | 1,265 Hp | 47 ppm @ 15% O2 | 1219 or 96.4% | 10.7 ppm @ 15% O2 | 10 | CO - Carbon Monoxide | PP | Y | NA
2016 | 1598 | 0125064019 | Dublin Advanced Energy Partners - Dublin Rec Center | 5600 Post Road | Dublin | 43017 |  | Franklin | B001 | 349 bhp natural gas-fired stationary combustion engine | 2016-03-22 | None | Air Compliance Testing | 349 hp-hr | 2.0 g/hp-hr or 270 ppmvd at 15% O2 | 332.6 hp-hr | 102.0 ppmvd at 15% O2 | 10 | CO - Carbon Monoxide | PP | Y | NA | This testing was performed to satisfy the initial testing requirements of 40 CFR Part 60 Subpart JJJJ - Standards of Performance for Stationary Spark Ignition Internal Combustion Engines.
2016 | 1605 | 0238000050 | MILEY COMPRESSOR STATION | 7531 State Rte 514 | Ripley Twp. | 44611 |  | Holmes | B003 | White Superior 8G-825, 4-cycle, rich burn, natural gas-fired reciprocating pipeline compressor engine, having a maximum capacity of 780hp, controlled by a Non-Selectivie Catalytic Reduction. (Compressor #07701 - B003) | 2016-05-19 | TWC | Lemos Labs. | 780 Hp | 270 ppmvd @ 15% O2 | < 90% | 11.3 ppmvd @ 15% O2 | 10 | CO - Carbon Monoxide | PP | Y | NA
2016 | 1619 | 0285000366 | East Ohio Gas - Chippewa Station | 17045 Galehouse Road | Doylestown | 44230 |  | Wayne | B010 | 2,370 hp 4SLB SI ICE; CAT G3608 | 2016-05-18 | Engine 5 Converter(Catalytic Converter): Engine #5; Cat B010(Catalytic Converter): Catalytic Converter for B010, engine #6; Catalytic(Catalytic Converter): Engine 7 Catalytic converter | Environmental Quality Management | 2370 Hp | 540 ppm @15% O2 or 4.0g/bhp-hr 93%DE 1.0 lb/hr | 2180 Hp | 13.7 ppm @15% O2, .11 g 94.5% DE 0.55 lb/hr | 10 | CO - Carbon Monoxide | PP | Y | NA | B009-3.3Catalyst Pressure and 889 degF Catalyst temp, B010-2.75 Catalyst Pressure and 860 degF Catalyst temp, B014-1.2 Catalyst Pressure and 874 degF Catalyst Temperature
2016 | 1624 | 0228000333 | East Ohio Gas Co. - Chesterland Compressor Station | 1201 E. 55th St. | Cleveland | 44103 |  | Geauga | P001 | A 630 bhp natural gas-fired reciprocating internal combustion 4-stroke lean-burn engine | 2016-09-28 | . | Environmental Quality Management, Inc. | 630 HP | 47 ppm @15%O2 | 604 HP or 95.9% | 15.7 ppm @ 15% O2 | 10 | CO - Carbon Monoxide | PP | Y | NA
2016 | 1652 | 0285000388 | East Ohio Gas Company - Paint | STATE RTE 250 | Wooster | 44624 |  | Wayne | B002 | Natural gas fired Internal Combustion Engine with max input capacity of 11.9 MMBtu/hr - Caterpillar G3516TALE with 1340 HP, 4-stroke, selective catalytic reduction (SCR) | 2016-07-07 | Three way Catalyst; CatOx(Catalytic Converter): Catalytic oxidizer for Engine 2 | Environmental Quality Management | 1340 HP | 540 ppm @ 15% O2 and 4.0 g/hp-hr | 1259 HP or 94% | 2.4 ppm @ 15% O2 and 0.02 g/hp-hr | 10 | CO - Carbon Monoxide | PP | Y | NA
2016 | 1657 | 0238000050 | MILEY COMPRESSOR STATION | 7531 State Rte 514 | Ripley Twp. | 44611 |  | Holmes | B005 | White Superior 12-GTLA, 4-cycle, lean burn, natural gas-fired reciprocating pipeline compressor engine, having a maximum capacity of 1650 hp. (Compressor #07703 - B005) | 2016-05-19 | TWC | Lemos Labs. | 1650 Hp | 47 ppmvd @ 15% O2 | < 90% | 2.4 ppmvd @ 15% O2 | 10 | CO - Carbon Monoxide | PP | Y | NA
2016 | 1659 | 0661005010 | E2 Appalachian Compression LLC - Upper Hill | Opossum Run Rd and Town Hwy 120 | Sarahsville | 43779 |  | Noble | P008 | 1,680 Hp. Waukesha (L7044GSI) natural gas-fired, rich burn, turbocharged, with oxidation catalyst, compressor engine. | 2016-07-13 | C-2(Catalytic Converter): Engine Catalyst; C-8(Catalytic Converter): Engine Catalyst | Alliance Source Testing | 1,680 hp | 540 hp | 1,518 hp | 23.3 ppm | 10 | CO - Carbon Monoxide | PP | Y | NA
2016 | 1677 | 0857103154 | PINNACLE GAS PRODUCERS LLC | 4220 PINNACLE RD | MORAINE | 45439 |  | Montgomery | B003 | Natural Gas Fired Compressor Engine, 12 MMBtu/hour nominal heat input | 2016-02-24 | N/A | DTE Energy | 12 MMBtu/hr heat input | 540 ppm @ 15% O2 | 867RPM | 265 ppm @ 15%O2 | 10 | CO - Carbon Monoxide | PP | Y | NA | Fuel content averaged 984 BTU/scf. Averaged 1503 degrees Fahrenheit.
2016 | 1679 | 0634005086 | Ascent Resources - Utica LLC - Hamilton 19-11N-6W | 34385 Kennedy Ridge Rd | Flushing | 43977 |  | Harrison | P002 | One or multiple stationary natural gas-fired spark ignition (SI) internal combustion engines (ICE) with a combined total horsepower (HP) of no more than 1,800 HP for the site. Includes 2007 and later model year engines manufactured after the applicable e | 2016-05-23 | catalyst | Great Plaines Analytical Services | 400 hp 203 hp | 2.0 g/hp-hr | 338 hp 188 hp | 3.42 g/hp-hr | 6348 03 | CO - Carbon Monoxide | FF | Y | NA | P002 two engines on allowable rate
2016 | 1680 | 0634005086 | Ascent Resources - Utica LLC - Hamilton 19-11N-6W | 34385 Kennedy Ridge Rd | Flushing | 43977 |  | Harrison | P002 | One or multiple stationary natural gas-fired spark ignition (SI) internal combustion engines (ICE) with a combined total horsepower (HP) of no more than 1,800 HP for the site. Includes 2007 and later model year engines manufactured after the applicable e | 2016-05-26 | catalyst | Great Plaines Analytical Services | 400 hp 203 hp | 2.0 g/hp-hr | 338 hp 188 hp | 3.42 g/hp-hr | 6348 03 | CO - Carbon Monoxide | FF | Y | NA | P002 two engines on allowable rate
2016 | 1681 | 0210012030 | Blue Racer Midstream LLC - Carroll Co Field Station #1 | Cobbler Rd NE | Carrollton | 44615 |  | Carroll | P003 | 1,340 HP Caterpillar G3516LE 4SLB Compressor Engine #3 with Oxidation Catalyst | 2016-10-14 | CC-1(Catalytic Converter): Oxidation Catalyst 1; CC-2(Catalytic Converter): Oxidation Catalyst 2; CC-3(Catalytic Converter): Oxidation Catalyst 3 | Montrose Air Quality Services | 1,340 Hp | 270 ppmvd@15% O2 & 0.54 g/bhp-hr | 1,086 HP or 79% | 3.7 ppmvd@15% O2 & 0.033 g/bhp-hr | 320 | CO - Carbon Monoxide | PP | Y | NA
2016 | 1682 | 0210012030 | Blue Racer Midstream LLC - Carroll Co Field Station #1 | Cobbler Rd NE | Carrollton | 44615 |  | Carroll | P001 | 1,340 HP Caterpillar G3516LE 4SLB Compressor Engine #1 with Oxidation Catalyst. Engine model year: 2013. | 2016-10-14 | CC-1(Catalytic Converter): Oxidation Catalyst 1; CC-2(Catalytic Converter): Oxidation Catalyst 2; CC-3(Catalytic Converter): Oxidation Catalyst 3 | Montrose Air Quality Services | 1,340 Hp | 270 ppmvd@15% O2 & 0.54 g/bhp-hr | 1,129 HP or 82% | 3.8 ppmvd@15% O2 & 0.034 g/bhp-hr | 320 | CO - Carbon Monoxide | PP | Y | NA
2016 | 1695 | 0661005010 | E2 Appalachian Compression LLC - Upper Hill | Opossum Run Rd and Town Hwy 120 | Sarahsville | 43779 |  | Noble | P002 | 1,680 Hp. Waukesha (L7044GSI) natural gas-fired, rich burn, turbocharged, with oxidation catalyst, compressor engine. | 2016-07-13 | C-2(Catalytic Converter): Engine Catalyst; C-8(Catalytic Converter): Engine Catalyst | Alliance Source Testing | 1,680 hp | 540 ppm | 1,529 hp | 36.7 ppm | 10 | CO - Carbon Monoxide | PP | Y | NA
2016 | 1699 | 0250000911 | East Ohio Gas Company - Austintown | 9686 NEW ROAD | Austintown Twp. | 44451 | 9708 | Mahoning | B002 | Natural gas-fired Caterpillar Model G3516LE, 4 stroke lean burn (4SLB) spark ignition (SI) reciprocating internal combustion engine (RICE) with an oxidation catalyst rated at 1265 HP (9.55 MMBtu/hr); complying with emission limitations in 40 CFR 63, Subpa | 2016-03-22 | Oxidative Catalyst 1(Other): B001 Catalytic Oxidizer; Oxidative Catalyst 2(Other): B002 Catalytic oxidizer | Environmental Quality Management | 1,265 Hp | 47 ppm @ 15% O2 | 1158 or 91.5% | 4.1 ppm @ 15% O2 | 10 | CO - Carbon Monoxide | PP | Y | NA
2016 | 1702 | 0656005028 | Miller Compressor Station | 51103 Twp Rd 847 | Seneca Twp. | 43788 |  | Monroe | P008 | Waukesha 1680 bhp Model L7044GSI 4-stroke Natural Gas Rich Burn Gas Compressor Engine Model Year 2014 controlled by a catalyst | 2016-01-21 | C-2708C(Catalytic Converter): Engine Catalyst | E2 Energy Services | 1680 hp | 0.5 g/hp-hr | 1510 hp | 4.30 g/hp-hr | 6348 03 | CO - Carbon Monoxide | FF | Y | NA
2016 | 1706 | 0656005028 | Miller Compressor Station | 51103 Twp Rd 847 | Seneca Twp. | 43788 |  | Monroe | P009 | Waukesha 1680 bhp Model L7044GSI 4-stroke Natural Gas Rich Burn Gas Compressor Engine Model Year 2014 controlled by a catalyst | 2016-01-22 | C-2709C(Catalytic Converter): Engine Catalyst | E2 Energy Services | 1680 hp | 0.5 g/hp-hr | 1477 hp | 4.43 g/hp-hr | 6348 03 | CO - Carbon Monoxide | FF | Y | NA
2016 | 1719 | 0285000366 | East Ohio Gas - Chippewa Station | 17045 Galehouse Road | Doylestown | 44230 |  | Wayne | B014 | 2,370 hp 4SLB SI ICE: CAT 3608 w/catalyst | 2016-05-18 | Engine 5 Converter(Catalytic Converter): Engine #5; Cat B010(Catalytic Converter): Catalytic Converter for B010, engine #6; Catalytic(Catalytic Converter): Engine 7 Catalytic converter | Environmental Quality Management | 2370 Hp | 270 ppm @15% O2, 2.0 g/bhp-hr, 93%DE, 0.72 lb/hr | 2228 Hp | 6.4 ppm @15% O2, .05g ,97.3%DE, 0.26 lb/hr | 10 | CO - Carbon Monoxide | PP | Y | NA | B009-3.3Catalyst Pressure and 889 degF Catalyst temp, B010-2.75 Catalyst Pressure and 860 degF Catalyst temp, B014-1.2 Catalyst Pressure and 874 degF Catalyst Temperature
2016 | 1720 | 0210012030 | Blue Racer Midstream LLC - Carroll Co Field Station #1 | Cobbler Rd NE | Carrollton | 44615 |  | Carroll | P002 | 1,340 HP Caterpillar G3516LE 4SLB Compressor Engine #2 with Oxidation Catalyst. Engine model year: 2013. | 2016-10-14 | CC-1(Catalytic Converter): Oxidation Catalyst 1; CC-2(Catalytic Converter): Oxidation Catalyst 2; CC-3(Catalytic Converter): Oxidation Catalyst 3 | Montrose Air Quality Services | 1,340 Hp | 270 ppmvd@15% O2 & 0.54 g/bhp-hr | 1,053 HP or 76% | 7.0 ppmvd@15% O2 & 0.062 g/bhp-hr | 320 | CO - Carbon Monoxide | PP | Y | NA
2016 | 2245 | 0285000366 | East Ohio Gas - Chippewa Station | 17045 Galehouse Road | Doylestown | 44230 |  | Wayne | B009 | 2,370 hp SI ICE pipeline compressor w/catalyst: CAT G3608-LE-TA | 2016-05-18 | Engine 5 Converter(Catalytic Converter): Engine #5; Cat B010(Catalytic Converter): Catalytic Converter for B010, engine #6; Catalytic(Catalytic Converter): Engine 7 Catalytic converter | Environmental Quality Management | 2370 Hp | 93% Destruction Efficiency & 1.0 lb/hr | 2251 Hp | 96.6% Destruction & 0.32 lb/hr | 10 | CO - Carbon Monoxide | PP | Y | NA | B009-3.3Catalyst Pressure and 889 degF Catalyst temp, B010-2.75 Catalyst Pressure and 860 degF Catalyst temp, B014-1.2 Catalyst Pressure and 874 degF Catalyst Temperature
2014 | 1432 | 0546015002 | Bellefontaine Gas Producers, LLC | 2946 US Route 68 North | Bellefontaine | 43311 |  | Logan | P001 | 2275 Hp, 4-stroke lean burn, non-emergency, spark ignition RICE; Ch. 31 modification issued 1/8/2014. | 2014-04-29 | N/A | DTE Energy | 1600 KW | 3.0 g/bhp-hr | 1600 KW | 2.7 g/bhp-hr | 10 | CO - Carbon Monoxide | PASS | NA | Y |  | Yes
2015 | 886 | 0238000187 | Trailway Wood II | 2261 County Rd 168 | Dundee | 44624 |  | Holmes | B004 | 4SLB Stationary RICE Natural Gas Engine #1 | 2015-04-16 | Engineered to meet the standard | Custom Stack Analysis | 452.8 KW | 270 ppm @ 15% O2 | 188.6 KW | 264.52 ppm @ 15% O2 | 10 | CO - Carbon Monoxide | PP | NA | Y | Operated at only 41.78 % of load. Will be limited to this output unless tested otherwise. | Yes
2016 | 1723 | 0238000191 | H W CHAIR, LTD | 6291 COUNTY ROAD 77 | MILLERSBURG | 44654 |  | Holmes | B002 | 738 hp (550 kW) 4SRB natural gas engine controlled by a NSCR and AFR to power facility: Waukesha F3521GSI | 2016-06-01 | CCWEG2(Catalytic Converter): catalyst | Custom Stack Analysis | 550 kw | 270 ppm @ 15% O2 or 2.0 g/hp-hr | 354.83 KW | 84.78 ppm @ 15% O2 or 0.67 g/hp-hr | 10 | CO - Carbon Monoxide | PP | Y | NA |  | Yes
2011 | 777 | 0664000056 | Waste Management of Ohio (Suburban South Recycling) | 3415 Township Road 447 | Glenford | 43739 |  | Perry | P004 | 1148 HP CAT 3516 Reciprocating LFG Engine | 2011-05-24 | NA | Custom Statck Analysis , LLC | 1148 Hp/ 800 Kw | 5.0 grams/hp-hr | 1148 grams/hr-hr/812 Kw | 2.32 grams/hp-hr | 10 | CO - Carbon Monoxide | PASS | NA | Y |  | Yes
2011 | 780 | 0664000056 | Waste Management of Ohio (Suburban South Recycling) | 3415 Township Road 447 | Glenford | 43739 |  | Perry | P006 | 1148 HP CAT 3516 Reciprocating LFG Engine | 2011-05-25 | NA | Custom Statck Analysis , LLC | 1148 Hp/ 800 Kw | 5.0 grams/hp-hr | 1148 grams/hr-hr/815 Kw | 2.27 grams/hp-hr | 10 | CO - Carbon Monoxide | PASS | NA | Y |  | Yes
2011 | 785 | 0664000056 | Waste Management of Ohio (Suburban South Recycling) | 3415 Township Road 447 | Glenford | 43739 |  | Perry | P003 | 1148 HP CAT 3516 Reciprocating LFG Engine | 2011-05-26 | NA | Custom Statck Analysis , LLC | 1148 Hp/ 800 Kw | 5.0 grams/hp-hr | 1148 grams/hr-hr | 2.25 grams/hp-hr | 10 | CO - Carbon Monoxide | PASS | NA | Y |  | Yes
2011 | 789 | 0664000056 | Waste Management of Ohio (Suburban South Recycling) | 3415 Township Road 447 | Glenford | 43739 |  | Perry | P007 | 1148 HP CAT 3516 Reciprocating LFG Engine | 2011-05-26 | NA | Custom Statck Analysis , LLC | 1148 Hp/ 800 Kw | 5.0 grams/hp-hr | 1148 grams/hr-hr/811 Kw | 2.16 grams/hp-hr | 10 | CO - Carbon Monoxide | PASS | NA | Y |  | Yes
2011 | 792 | 0664000056 | Waste Management of Ohio (Suburban South Recycling) | 3415 Township Road 447 | Glenford | 43739 |  | Perry | P008 | 1148 HP CAT 3516 Reciprocating LFG Engine | 2011-05-26 | NA | Custom Statck Analysis , LLC | 1148 Hp/ 800 Kw | 5.0 grams/hp-hr | 1148 grams/hr-hr/810 Kw | 2.28 grams/hp-hr | 10 | CO - Carbon Monoxide | PASS | NA | Y |  | Yes
2011 | 799 | 0664000056 | Waste Management of Ohio (Suburban South Recycling) | 3415 Township Road 447 | Glenford | 43739 |  | Perry | P002 | 1148 HP CAT 3516 Reciprocating LFG Engine | 2011-06-01 | NA | Custom Statck Analysis , LLC | 1148 Hp/ 800 Kw | 5.0 grams/hp-hr | 1148 grams/hr-hr | 2.35 grams/hp-hr | 10 | CO - Carbon Monoxide | PASS | NA | Y |  | Yes
2011 | 803 | 0664000056 | Waste Management of Ohio (Suburban South Recycling) | 3415 Township Road 447 | Glenford | 43739 |  | Perry | P005 | 1148 HP CAT 3516 Reciprocating LFG Engine | 2011-06-01 | NA | Custom Statck Analysis , LLC | 1148 Hp/ 800 Kw | 5.0 grams/hp-hr | 1148 grams/hr-hr/807 Kw | 2.19 grams/hp-hr | 10 | CO - Carbon Monoxide | PASS | NA | Y |  | Yes
2012 | 737 | 0664000056 | Waste Management of Ohio (Suburban South Recycling) | 3415 Township Road 447 | Glenford | 43739 |  | Perry | P008 | 1148 HP CAT 3516 Reciprocating LFG Engine | 2012-04-02 | NA | RMC Environmental, Inc. | 1148 Hp/ 800 Kw | 5.0 grams/hp-hr | 1148 grams/hr-hr/810 Kw | 2.61 grams/hp-hr | 10 | CO - Carbon Monoxide | PASS | NA | Y | emissions limit: 6.84 lbs/hr test results: 6.59 lbs/hr | Yes
2012 | 741 | 0664000056 | Waste Management of Ohio (Suburban South Recycling) | 3415 Township Road 447 | Glenford | 43739 |  | Perry | P005 | 1148 HP CAT 3516 Reciprocating LFG Engine | 2012-04-03 | NA | RMC Environmental, Inc. | 1148 Hp/ 800 Kw | 5.0 grams/hp-hr | 1148 grams/hr-hr/810 Kw | 1.92 grams/hp-hr | 10 | CO - Carbon Monoxide | PASS | NA | Y | emissions limit: 6.84 lbs/hr test results: 4.85 lbs/hr | Yes
2012 | 747 | 0664000056 | Waste Management of Ohio (Suburban South Recycling) | 3415 Township Road 447 | Glenford | 43739 |  | Perry | P006 | 1148 HP CAT 3516 Reciprocating LFG Engine | 2012-04-03 | NA | RMC Environmental, Inc. | 1148 Hp/ 800 Kw | 5.0 grams/hp-hr | 1148 grams/hr-hr/810 Kw | 2.13 grams/hp-hr | 10 | CO - Carbon Monoxide | PASS | NA | Y | emissions limit: 6.84 lbs/hr test results: 5.40 lbs/hr | Yes
2012 | 749 | 0664000056 | Waste Management of Ohio (Suburban South Recycling) | 3415 Township Road 447 | Glenford | 43739 |  | Perry | P007 | 1148 HP CAT 3516 Reciprocating LFG Engine | 2012-04-03 | NA | RMC Environmental, Inc. | 1148 Hp/ 800 Kw | 5.0 grams/hp-hr | 1148 grams/hr-hr/810 Kw | 2.14 grams/hp-hr | 10 | CO - Carbon Monoxide | PASS | NA | Y | emissions limit: 6.84 lbs/hr test results: 5.42 lbs/hr | Yes
2012 | 752 | 0664000056 | Waste Management of Ohio (Suburban South Recycling) | 3415 Township Road 447 | Glenford | 43739 |  | Perry | P003 | 1148 HP CAT 3516 Reciprocating LFG Engine | 2012-04-04 | NA | RMC Environmental, Inc. | 1148 Hp/ 800 Kw | 5.0 grams/hp-hr | 1148 grams/hr-hr/810 Kw | 2.11 grams/hp-hr | 10 | CO - Carbon Monoxide | PASS | NA | Y | emissions limit: 6.84 lbs/hr test results: 5.35 lbs/hr | Yes
2012 | 756 | 0664000056 | Waste Management of Ohio (Suburban South Recycling) | 3415 Township Road 447 | Glenford | 43739 |  | Perry | P004 | 1148 HP CAT 3516 Reciprocating LFG Engine | 2012-04-04 | NA | RMC Environmental, Inc. | 1148 Hp/ 800 Kw | 5.0 grams/hp-hr | 1148 grams/hr-hr/810 Kw | 2.61 grams/hp-hr | 10 | CO - Carbon Monoxide | PASS | NA | Y | emissions limit: 6.84 lbs/hr test results: 6.62 lbs/hr | Yes
2012 | 761 | 0664000056 | Waste Management of Ohio (Suburban South Recycling) | 3415 Township Road 447 | Glenford | 43739 |  | Perry | P002 | 1148 HP CAT 3516 Reciprocating LFG Engine | 2012-04-05 | NA | RMC Environmental, Inc. | 1148 Hp/ 800 Kw | 5.0 grams/hp-hr | 1148 grams/hr-hr/810 Kw | 2.13 grams/hp-hr | 10 | CO - Carbon Monoxide | PASS | NA | Y | emissions limit: 6.84 lbs/hr test results: 5.38 lbs/hr | Yes
2013 | 1257 | 0664000056 | Waste Management of Ohio (Suburban South Recycling) | 3415 Township Road 447 | Glenford | 43739 |  | Perry | P002 | 1148 HP CAT 3516 Reciprocating LFG Engine | 2013-03-26 | oxidative catalyst reduction | RMC Environmental, Inc. | 1148 Hp | 5.0 grams/Hp-hr 6.84 lbs/hr | 1148 Hp | 1.75 grams/Hp-hr 4.42 lbs/hr | 10 | CO - Carbon Monoxide | PASS | NA | Y | Testing occurred March 26 - 28, 2013. Lisa witnessed three different tests.
2013 | 1258 | 0664000056 | Waste Management of Ohio (Suburban South Recycling) | 3415 Township Road 447 | Glenford | 43739 |  | Perry | P003 | 1148 HP CAT 3516 Reciprocating LFG Engine | 2013-03-26 | oxidative catalyst reduction | RMC Environmental, Inc. | 1148 Hp | 5.0 grams/Hp-hr 6.84 lbs/hr | 1148 Hp | 1.79 grams/Hp-hr 4.54 lbs/hr | 10 | CO - Carbon Monoxide | PASS | NA | Y | Testing occurred March 26 - 28, 2013. Lisa witnessed three different tests.
2013 | 1263 | 0664000056 | Waste Management of Ohio (Suburban South Recycling) | 3415 Township Road 447 | Glenford | 43739 |  | Perry | P004 | 1148 HP CAT 3516 Reciprocating LFG Engine | 2013-03-26 | oxidative catalyst reduction | RMC Environmental, Inc. | 1148 Hp | 5.0 grams/Hp-hr 6.84 lbs/hr | 1148 Hp | 2.21 grams/Hp-hr 5.61 lbs/hr | 10 | CO - Carbon Monoxide | PASS | NA | Y | Testing occurred March 26 - 28, 2013. Lisa witnessed three different tests.
2013 | 1266 | 0664000056 | Waste Management of Ohio (Suburban South Recycling) | 3415 Township Road 447 | Glenford | 43739 |  | Perry | P005 | 1148 HP CAT 3516 Reciprocating LFG Engine | 2013-03-26 | oxidative catalyst reduction | RMC Environmental, Inc. | 1148 Hp | 5.0 grams/Hp-hr 6.84 lbs/hr | 1148 Hp | 2.15 grams/Hp-hr 5.45 lbs/hr | 10 | CO - Carbon Monoxide | PASS | NA | Y | Testing occurred March 26 - 28, 2013. Lisa witnessed three different tests.
2013 | 1269 | 0664000056 | Waste Management of Ohio (Suburban South Recycling) | 3415 Township Road 447 | Glenford | 43739 |  | Perry | P006 | 1148 HP CAT 3516 Reciprocating LFG Engine | 2013-03-26 | oxidative catalyst reduction | RMC Environmental, Inc. | 1148 Hp | 5.0 grams/Hp-hr 6.84 lbs/hr | 1148 Hp | 2.20 grams/Hp-hr 5.57 lbs/hr | 10 | CO - Carbon Monoxide | PASS | NA | Y | Testing occurred March 26 - 28, 2013. Lisa witnessed three different tests.
2013 | 1270 | 0664000056 | Waste Management of Ohio (Suburban South Recycling) | 3415 Township Road 447 | Glenford | 43739 |  | Perry | P007 | 1148 HP CAT 3516 Reciprocating LFG Engine | 2013-03-26 | oxidative catalyst reduction | RMC Environmental, Inc. | 1148 Hp | 5.0 grams/Hp-hr 6.84 lbs/hr | 1148 Hp | 1.92 grams/Hp-hr 4.86 lbs/hr | 10 | CO - Carbon Monoxide | PASS | NA | Y | Testing occurred March 26 - 28, 2013. Lisa witnessed three different tests.
2013 | 1273 | 0664000056 | Waste Management of Ohio (Suburban South Recycling) | 3415 Township Road 447 | Glenford | 43739 |  | Perry | P008 | 1148 HP CAT 3516 Reciprocating LFG Engine | 2013-03-26 | oxidative catalyst reduction | RMC Environmental, Inc. | 1148 Hp | 5.0 grams/Hp-hr 6.84 lbs/hr | 1148 Hp | 2.10 grams/Hp-hr 5.31 lbs/hr | 10 | CO - Carbon Monoxide | PASS | NA | Y | Testing occurred March 26 - 28, 2013. Lisa witnessed three different tests.
2014 | 1429 | 0664000056 | Waste Management of Ohio (Suburban South Recycling) | 3415 Township Road 447 | Glenford | 43739 |  | Perry | P002 | 1148 HP CAT 3516 Reciprocating LFG Engine | 2014-04-28 | none | RMC Environmental | 800 MW | 5.0 g/hp-hr | 824 MW | 2.6 g/hp-hr | 10 | CO - Carbon Monoxide | PASS | NA | Y |  | Yes
2014 | 1679 | 0664000056 | Waste Management of Ohio (Suburban South Recycling) | 3415 Township Road 447 | Glenford | 43739 |  | Perry | P006 | 1148 HP CAT 3516 Reciprocating LFG Engine | 2014-04-30 | none | RMC Environmenatl | 800 MW | 5.0 g/hp-hr | 825 MW | 2.3 g/hp-hr | 10 | CO - Carbon Monoxide | PASS | NA | Y |  | Yes
2014 | 1686 | 0664000056 | Waste Management of Ohio (Suburban South Recycling) | 3415 Township Road 447 | Glenford | 43739 |  | Perry | P005 | 1148 HP CAT 3516 Reciprocating LFG Engine | 2014-04-28 | none | RMC Environmental | 800 MW | 5.0 g/hp-hr | 818 MW | 2.4 g/hp-hr | 10 | CO - Carbon Monoxide | PASS | NA | Y |  | Yes
2014 | 1688 | 0664000056 | Waste Management of Ohio (Suburban South Recycling) | 3415 Township Road 447 | Glenford | 43739 |  | Perry | P007 | 1148 HP CAT 3516 Reciprocating LFG Engine | 2014-04-29 | none | RMC Environmental | 800 MW | 5.0 g/hp-hr | 2.4 g/hp-hr | 2.4 g/hp-hr | 10 | CO - Carbon Monoxide | PASS | NA | Y |  | Yes
2014 | 1691 | 0664000056 | Waste Management of Ohio (Suburban South Recycling) | 3415 Township Road 447 | Glenford | 43739 |  | Perry | P008 | 1148 HP CAT 3516 Reciprocating LFG Engine | 2014-04-29 | none | RMC Environmental | 800 MW | 5.0 g/hp-hr | 824 MW | 2.4 g/hp-hr | 10 | CO - Carbon Monoxide | PASS | NA | Y |  | Yes
2014 | 1693 | 0664000056 | Waste Management of Ohio (Suburban South Recycling) | 3415 Township Road 447 | Glenford | 43739 |  | Perry | P004 | 1148 HP CAT 3516 Reciprocating LFG Engine | 2014-04-28 | none | RMC Environmental | 800 MW | 5.0 g/hp-hr | 828 MW | 2.5 g/hp-hr | 10 | CO - Carbon Monoxide | PASS | NA | Y |  | Yes
2014 | 1698 | 0664000056 | Waste Management of Ohio (Suburban South Recycling) | 3415 Township Road 447 | Glenford | 43739 |  | Perry | P003 | 1148 HP CAT 3516 Reciprocating LFG Engine | 2014-04-29 | none | RMC Environmental | 800 MW | 5.0 g/hp-hr | 818 MW | 2.5 g-hp-hr | 10 | CO - Carbon Monoxide | PASS | NA | Y |  | Yes
2015 | 770 | 0664000056 | Waste Management of Ohio (Suburban South Recycling) | 3415 Township Road 447 | Glenford | 43739 |  | Perry | P002 | 1148 HP CAT 3516 Reciprocating LFG Engine | 2015-03-25 | none | RMC Envirnmental, Inc. | 1,148 hp | 5.0 g/hp-hr | 1,228 hp | 1.6 g/hp-hr | 10 | CO - Carbon Monoxide | PP | NA | Y
2015 | 773 | 0664000056 | Waste Management of Ohio (Suburban South Recycling) | 3415 Township Road 447 | Glenford | 43739 |  | Perry | P008 | 1148 HP CAT 3516 Reciprocating LFG Engine | 2015-03-26 | none | RMC Environmental, Inc | 1,148 hp | 5.0 g/hp-hr | 1,268 hp | 1.6 g/hp-hr | 10 | CO - Carbon Monoxide | PP | NA | Y
2015 | 775 | 0664000056 | Waste Management of Ohio (Suburban South Recycling) | 3415 Township Road 447 | Glenford | 43739 |  | Perry | P004 | 1148 HP CAT 3516 Reciprocating LFG Engine | 2015-03-25 | none | RMC Environmental, Inc | 1,148hp | 5.0 g/hp-hr | 1,231 hp | 1.8 g/hp-hr | 10 | CO - Carbon Monoxide | PP | NA | Y
2015 | 831 | 0664000056 | Waste Management of Ohio (Suburban South Recycling) | 3415 Township Road 447 | Glenford | 43739 |  | Perry | P007 | 1148 HP CAT 3516 Reciprocating LFG Engine | 2015-03-26 | none | RMC Environmental, Inc | 1,148 hp | 5.0 g/hp-hr | 1,241 hp | 2.0 g/hp-hr | 10 | CO - Carbon Monoxide | PP | NA | Y
2015 | 832 | 0664000056 | Waste Management of Ohio (Suburban South Recycling) | 3415 Township Road 447 | Glenford | 43739 |  | Perry | P003 | 1148 HP CAT 3516 Reciprocating LFG Engine | 2015-03-24 | none | RMC Envirnmental, Inc. | 1,148 hp | 5.0 g/hp-hr | 1,260 hp | 2.1 g/hp-hr | 10 | CO - Carbon Monoxide | PP | NA | Y
2015 | 849 | 0664000056 | Waste Management of Ohio (Suburban South Recycling) | 3415 Township Road 447 | Glenford | 43739 |  | Perry | P005 | 1148 HP CAT 3516 Reciprocating LFG Engine | 2015-03-24 | none | RMC Environmental, Inc | 1,148 hp | 5.0 g/hp-hr | 1,252 hp | 2.2 g/hp-hr | 10 | CO - Carbon Monoxide | PP | NA | Y
2015 | 883 | 0664000056 | Waste Management of Ohio (Suburban South Recycling) | 3415 Township Road 447 | Glenford | 43739 |  | Perry | P006 | 1148 HP CAT 3516 Reciprocating LFG Engine | 2015-03-25 | none | RMC Environmental, Inc | 1,248 hp | 5.0 g/hp-hr | 1,251 hp | 2.6 g/hp-hr | 10 | CO - Carbon Monoxide | PP | NA | Y
2016 | 1571 | 0664000056 | Waste Management of Ohio (Suburban South Recycling) | 3415 Township Road 447 | Glenford | 43739 |  | Perry | P006 | 1148 HP CAT 3516 Reciprocating LFG Engine | 2016-03-31 | none | RMC Environmental, Inc. | 1148 hp | 5.0 g/hp-hr | 1334 hp | 1.7 g/hp-hr | 10 | CO - Carbon Monoxide | PP | Y | NA
2016 | 1573 | 0664000056 | Waste Management of Ohio (Suburban South Recycling) | 3415 Township Road 447 | Glenford | 43739 |  | Perry | P003 | 1148 HP CAT 3516 Reciprocating LFG Engine | 2016-03-31 | none | RMC Environmental, Inc. | 1148 hp | 5.0 g/hp-hr | 1239 hp | 1.8 g/hp-hr | 10 | CO - Carbon Monoxide | PP | Y | NA
2016 | 1577 | 0664000056 | Waste Management of Ohio (Suburban South Recycling) | 3415 Township Road 447 | Glenford | 43739 |  | Perry | P008 | 1148 HP CAT 3516 Reciprocating LFG Engine | 2016-03-31 | none | RMC Environmental, Inc. | 1148 hp | 5.0 g/hp-hr | 1258 hp | 1.8 g/hp-hr | 10 | CO - Carbon Monoxide | PP | Y | NA
2016 | 1592 | 0664000056 | Waste Management of Ohio (Suburban South Recycling) | 3415 Township Road 447 | Glenford | 43739 |  | Perry | P007 | 1148 HP CAT 3516 Reciprocating LFG Engine | 2016-03-31 | none | RMC Environmental, Inc. | 1148 hp | 5.0 g/hp-hr | 1288 hp | 1.9 g/hp-hr | 10 | CO - Carbon Monoxide | PP | Y | NA
2016 | 1630 | 0664000056 | Waste Management of Ohio (Suburban South Recycling) | 3415 Township Road 447 | Glenford | 43739 |  | Perry | P005 | 1148 HP CAT 3516 Reciprocating LFG Engine | 2016-03-31 | none | RMC Environmental, Inc. | 1148 hp | 5.0 g/hp-hr | 1244 hp | 2.0 g/hp-hr | 10 | CO - Carbon Monoxide | PP | Y | NA
2016 | 1646 | 0664000056 | Waste Management of Ohio (Suburban South Recycling) | 3415 Township Road 447 | Glenford | 43739 |  | Perry | P002 | 1148 HP CAT 3516 Reciprocating LFG Engine | 2016-03-31 | none | RMC Environmental, Inc. | 1148 hp | 5.0 g/hp-hr | 1251 hp | 2.3 g/hp-hr | 10 | CO - Carbon Monoxide | PP | Y | NA
2016 | 1650 | 0664000056 | Waste Management of Ohio (Suburban South Recycling) | 3415 Township Road 447 | Glenford | 43739 |  | Perry | P004 | 1148 HP CAT 3516 Reciprocating LFG Engine | 2016-03-31 | none | RMC Environmental, Inc. | 1148 hp | 5.0 g/hp-hr | 1240 hp | 2.3 g/hp-hr | 10 | CO - Carbon Monoxide | PP | Y | NA
2016 | 1623 | 0247170911 | WELLINGTON MUNICIPAL UTILITIES - WEST STATION | 300 Erie St | Wellington | 44090 |  | Lorain | B001 | G.M.Electromotive Div. Model 8-645-E4, 1525 HP, 1050 KW, No. 2 Diesel-fueled, 2-stroke internal combustion engine driven, electric generator set with a Miratech NSCR. | 2016-04-12 | IQ2-30-20-EL(Catalytic Converter): Miratech NSCR | Grace Consulting, Inc. | 1000 kw | 23 ppmvd @ 15% O2 | 1000 | 14.01 ppmvd @ 15% O2 | 10 | CO - Carbon Monoxide | PP | N | NA |  | Yes
2015 | 891 | 0285032008 | Wooster Renewable Energy, LLC | 1123 Old Columbus Road | Wooster | 44619 |  | Wayne | B001 | Combined Heat and Process Unit consisting of a 1,475 hp/1,800 rpm/1,100 kw, 4SLB, digester gas engine powering a 1.3 MW generator | 2015-04-21 | Oxygen Sensor that will adjust fuel to air ratios. | Custom Stack Analysis | 1475 Hp | 540 ppm @ 15% O2 4.0 g/hp-hr | 1371 Hp | 390.05 ppm @ 15% O2 2.95 g/hp-hr | 10 | CO - Carbon Monoxide | PP | NA | Y |  | Yes
2006 | 1399 | 1431070849 | University of Cincinnati | Clifton Campus | Cincinnati | 45221 |  | Hamilton | P007 | 2 MW Diesel fuel-fired internal combustion engine | 2006-07-16 | CATALYTIC OXIDIZER | EQM | 2 MW | 1.59 LB/HR | 1.8 MW | 0.40 LB/HR | 10 | CO - Carbon Monoxide | PASS | NA | Y |  | Yes
2006 | 1401 | 1431070849 | University of Cincinnati | Clifton Campus | Cincinnati | 45221 |  | Hamilton | P008 | 1.5 MW Diesel fuel-fired internal combustion engine | 2006-08-15 | CATALYTIC OXIDIZER | EQM | 1.5 MW | 1.94 LB/HR, >70%DE | 1.35 MW | 0.89 LB/HR, 87%DE | 10 | CO - Carbon Monoxide | PASS | NA | Y |  | Yes
2006 | 1413 | 1431070849 | University of Cincinnati | Clifton Campus | Cincinnati | 45221 |  | Hamilton | P007 | 2 MW Diesel fuel-fired internal combustion engine | 2006-12-11 | CATALYTIC OXIDIZER | RMC Environmental | 2 MW | 1.59 LB/HR; >70% DRE | 1.8 MW | 0.23 LB/HR; 90.1% DRE | 10 | CO - Carbon Monoxide | PASS | NA | Y |  | Yes
2007 | 1616 | 1431070849 | University of Cincinnati | Clifton Campus | Cincinnati | 45221 |  | Hamilton | P008 | 1.5 MW Diesel fuel-fired internal combustion engine | 2007-01-08 | CATALYTIC OXIDIZER | RMC Environmental | 1.5 MW | 1.91 LB/HR; >70% DRE | 1.35 MW | 0.80 LB/HR; 87.1% DRE | 10 | CO - Carbon Monoxide | PASS | NA | Y |  | Yes
2007 | 1623 | 1431070849 | University of Cincinnati | Clifton Campus | Cincinnati | 45221 |  | Hamilton | P007 | 2 MW Diesel fuel-fired internal combustion engine | 2007-11-14 | CATALYTIC OXIDIZER | RMC Environmental | 2 MW | >70% DRE | 1.86 MW | 89.0% DRE | 10 | CO - Carbon Monoxide | PASS | NA | Y |  | Yes
2007 | 1624 | 1431070849 | University of Cincinnati | Clifton Campus | Cincinnati | 45221 |  | Hamilton | P008 | 1.5 MW Diesel fuel-fired internal combustion engine | 2007-11-14 | CATALYTIC OXIDIZER | RMC Environmental | 1.5 MW | >70% DRE | 1.35 MW | 90.1% DRE | 10 | CO - Carbon Monoxide | PASS | NA | Y |  | Yes
2008 | 1771 | 1431070849 | University of Cincinnati | Clifton Campus | Cincinnati | 45221 |  | Hamilton | P007 | 2 MW Diesel fuel-fired internal combustion engine | 2008-11-18 | CATALYTIC OXIDIZER | RMC Environmental | 2 MW | >70% DRE; 1.59 LB/HR | 1.86 MW | 85.34% DRE; 0.26 LB/HR | 10 | CO - Carbon Monoxide | PASS | NA | Y |  | Yes
2008 | 1772 | 1431070849 | University of Cincinnati | Clifton Campus | Cincinnati | 45221 |  | Hamilton | P008 | 1.5 MW Diesel fuel-fired internal combustion engine | 2008-11-18 | CATALYTIC OXIDIZER | RMC Environmental | 1.5 MW | >70% DRE; 1.91 LB/HR | 1.35 MW | 88.10% DRE; 0.62 LB/HR | 10 | CO - Carbon Monoxide | PASS | NA | Y |  | Yes
2011 | 1088 | 1431070849 | University of Cincinnati | Clifton Campus | Cincinnati | 45221 |  | Hamilton | P007 | 2 MW Diesel fuel-fired internal combustion engine | 2011-03-25 | CATALYTIC OXIDIZER | RMC Environmental | 2 MW | >70% DRE; 1.59 LB/HR | 1.602 MW | 81.32% DRE; 0.22 LB/HR | 10 | CO - Carbon Monoxide | PASS | NA | Y |  | Yes
2011 | 1089 | 1431070849 | University of Cincinnati | Clifton Campus | Cincinnati | 45221 |  | Hamilton | P008 | 1.5 MW Diesel fuel-fired internal combustion engine | 2011-03-25 | CATALYTIC OXIDIZER | RMC Environmental Inc. | 1.5 MW | >70% DRE; 1.91 LB/HR | 1.35 MW | 83.14% DRE; 0.80 LB/HR | 10 | CO - Carbon Monoxide | PASS | NA | Y |  | Yes
2011 | 1093 | 1431070849 | University of Cincinnati | Clifton Campus | Cincinnati | 45221 |  | Hamilton | P007 | 2 MW Diesel fuel-fired internal combustion engine | 2011-12-01 | CATALYTIC OXIDIZER | RMC Environmental | 2 MW | >70% DRE; 1.59 LB/HR | 1.720 MW | 84.75% DRE; 0.27 LB/HR | 10 | CO - Carbon Monoxide | PASS | NA | Y |  | Yes
2011 | 1094 | 1431070849 | University of Cincinnati | Clifton Campus | Cincinnati | 45221 |  | Hamilton | P008 | 1.5 MW Diesel fuel-fired internal combustion engine | 2011-12-01 | CATALYTIC OXIDIZER | RMC Environmental Inc. | 1.5 MW | >70% DRE; 1.91 LB/HR | 1.35 MW | 92.70% DRE; 0.72 LB/HR | 10 | CO - Carbon Monoxide | PASS | NA | Y |  | Yes
2012 | 1321 | 1431070849 | University of Cincinnati | Clifton Campus | Cincinnati | 45221 |  | Hamilton | P005 | 2 MW Diesel fuel-fired internal combustion engine | 2012-12-12 | Catalytic Oxidizer | RMC Environmental | 2 MW | >70% DRE; 1.73 LB/HR | 1.8 MW | 96.72% DRE; 1.52 LB/HR | 10 | CO - Carbon Monoxide | PASS | NA | Y | Test Report: Report ID# 54678 ITT: Report ID# 648362 | Yes
2012 | 1322 | 1431070849 | University of Cincinnati | Clifton Campus | Cincinnati | 45221 |  | Hamilton | B108 | 135.6 MMBTU Spreader Stoker Boiler w/ fabric filter, capable of coal, clean cellulosic biomass and/or pelletized fuel (capacity with CCB is 131 MMBtu/hr; capacity with pelletized fuel 90 MMBtu/hr) [This emissions unit was formerly identified as B008 under facility ID 1431070270 and has been incorporated into this facility ID as emissions unit B108 in accordance with Engineering Guide 58.] | 2012-12-13 | Fabric Filter Baghouse and Over-fire Air System | RMC Environmental, Inc. | 135.6 mmBtu/hr (100,000 lb of steam/hr) | Not Applicable | 76,000 lb of steam/hr | 0.05 lb/mmBtu | 10 | CO - Carbon Monoxide | PASS | NA | Y | Testing was conducted to gather new baseline emissions data for NOx and CO after the installation of a new over-fire air system. 100% coal was used to fire the boiler during the test. NOx emissions were found to be 275 ppmvd @ 3% O2 and 0.38 lb/mmBtu. Test Report: Report ID# 56838 (attachment ID - 676210) ITT: Report ID# 54681 (attachment ID - 648371)
2013 | 1573 | 1431070849 | University of Cincinnati | Clifton Campus | Cincinnati | 45221 |  | Hamilton | P007 | 2 MW Diesel fuel-fired internal combustion engine | 2013-04-02 | CATALYTIC OXIDIZER | RMC Environmental | 2 MW | >70% DRE; 1.59 LB/HR | 1.2 MW | 89.93% DRE; 0.14 LB/HR | 10 | CO - Carbon Monoxide | PASS | NA | Y | Faciltity report located in STARS2 under Report ID 64566 | Yes
2013 | 1574 | 1431070849 | University of Cincinnati | Clifton Campus | Cincinnati | 45221 |  | Hamilton | P008 | 1.5 MW Diesel fuel-fired internal combustion engine | 2013-04-02 | CATALYTIC OXIDIZER | RMC Environmental Inc. | 1.5 MW | >70% DRE; 1.91 LB/HR | 1.2 MW | 85.45% DRE; 0.60 LB/HR | 10 | CO - Carbon Monoxide | PASS | NA | Y | Facility report located in STARS2 under Report ID 64566 | Yes
2013 | 1580 | 1431070849 | University of Cincinnati | Clifton Campus | Cincinnati | 45221 |  | Hamilton | P007 | 2 MW Diesel fuel-fired internal combustion engine | 2013-12-19 | CATALYTIC OXIDIZER | RMC Environmental | 2 MW | >70% DRE; 1.59 LB/HR | 1.2 MW | 87% DRE; 0.20 LB/HR | 10 | CO - Carbon Monoxide | PASS | NA | Y | Faciltity report located in STARS2 under Report ID 73255 | Yes
2013 | 1581 | 1431070849 | University of Cincinnati | Clifton Campus | Cincinnati | 45221 |  | Hamilton | P008 | 1.5 MW Diesel fuel-fired internal combustion engine | 2013-12-19 | CATALYTIC OXIDIZER | RMC Environmental Inc. | 1.5 MW | >70% DRE; 1.91 LB/HR | 1.4 MW | 79% DRE; 0.75 LB/HR | 10 | CO - Carbon Monoxide | PASS | NA | Y | Facility report located in STARS2 under Report ID 73255 | Yes
2014 | 1800 | 1431070849 | University of Cincinnati | Clifton Campus | Cincinnati | 45221 |  | Hamilton | P007 | 2 MW Diesel fuel-fired internal combustion engine | 2014-11-05 | CATALYTIC OXIDIZER | RMC Environmental | 2 MW | >70% DRE; 1.59 LB/HR | 1.2 MW | 74% DRE; 0.32 LB/HR | 10 | CO - Carbon Monoxide | PASS | NA | Y | Faciltity report located in STARS2 under Report ID 90620 | Yes
2014 | 1832 | 1431070849 | University of Cincinnati | Clifton Campus | Cincinnati | 45221 |  | Hamilton | P008 | 1.5 MW Diesel fuel-fired internal combustion engine | 2014-11-05 | CATALYTIC OXIDIZER | RMC Environmental Inc. | 1.5 MW | >70% DRE; 1.91 LB/HR | 1.35 MW | 82% DRE; 0.78 LB/HR | 10 | CO - Carbon Monoxide | PASS | NA | Y | Facility report located in STARS2 under Report ID 90620 | Yes
2016 | 1887 | 1431070849 | University of Cincinnati | Clifton Campus | Cincinnati | 45221 |  | Hamilton | P007 | 2 MW Diesel fuel-fired internal combustion engine | 2016-10-14 | CATS catlst(Catalytic Converter): Controls engine CO and OC emissions; Cumm catlst(Catalytic Converter): Controls engine CO and OC emissions | RMC Environmental, Inc. | 2 MW | >70% DRE; 1.59 lb/hr | 1.2MW | 86.7% DRE; 0.19 lb/hr | 10 | CO - Carbon Monoxide | PP | N | NA |  | Yes
2016 | 1960 | 1431070849 | University of Cincinnati | Clifton Campus | Cincinnati | 45221 |  | Hamilton | P008 | 1.5 MW Diesel fuel-fired internal combustion engine | 2016-10-14 | CATS catlst(Catalytic Converter): Controls engine CO and OC emissions; Cumm catlst(Catalytic Converter): Controls engine CO and OC emissions | RMC Environmental, Inc. | 1.5 MW | >70 DRE; 1.91 lb/hr | 1.35 MW | 91% DRE; 0.46 lb/hr | 10 | CO - Carbon Monoxide | PP | N | NA |  | Yes
2012 | 1545 | 1677011251 | Urban Renewables III, LLC | 2460 Akron Peninsula Rd | Akron | 44313 |  | Summit | B001 | Reciprocating internal combustion engine burning landfill gas to drive an electrical generator. | 2012-11-16 | None | Air Compliance Testing, Inc | 1000 kW | 610 ppmvd @ 15% O2 | 997.98 kW | 230.8 ppmvd @ 15% O2 | 10 | CO - Carbon Monoxide | PASS | NA | Y | Testing to comply with 40 CFR part 60 subpart JJJJ. Emission Standards for Stationary Non-Emergency SI. Stationary SI Landfill/Digester Gas Engines. Table 1 (HP > 500). | Yes
2016 | 1718 | 1677011251 | Urban Renewables III, LLC | 2460 Akron Peninsula Rd | Akron | 44313 |  | Summit | B001 | Reciprocating internal combustion engine burning landfill gas to drive an electrical generator. | 2016-06-01 | n/a | Air Compliance Testing, Inc. | 1137 | 8.7 lbs/hr | 904 | 6.33 lbs/hr | 10 | CO - Carbon Monoxide | PP | Y | Y
2004 | 372 | 0369000025 | PRO-TEC Coating Company | 5500 PRO-TEC Pkwy | Leipsic | 45856 | 9234 | Putnam | P001 | 92.0 MMBtu/hr natural gas-fired continuous annealing furnace, this includes 12 MMBtu/hr auxiliary natural gas-fired burners [the burners are used to maintain the selective catalytic reduction (SCR) control device operating temperature within the recommended range]. With alkaline cleaning, annealing furnace, water quenching and tempering. | 2004-09-16 | selective catalytic reduction unit | AIR COMPLIANCE CONSULTANTS, INC. | 96 mmbtu/hr | 12.4 lbs/hr | 89.2 mmbtu/hr | 4.9 lbs/hr | 10 | CO - Carbon Monoxide | PASS | NA | Y
2006 | 537 | 0369000025 | PRO-TEC Coating Company | 5500 PRO-TEC Pkwy | Leipsic | 45856 | 9234 | Putnam | P001 | 92.0 MMBtu/hr natural gas-fired continuous annealing furnace, this includes 12 MMBtu/hr auxiliary natural gas-fired burners [the burners are used to maintain the selective catalytic reduction (SCR) control device operating temperature within the recommended range]. With alkaline cleaning, annealing furnace, water quenching and tempering. | 2006-05-19 | selective catalytic reducing unit (SCR) | Air Compliance Consultants, Inc. | 96 mmBTU/hr | 12.4 lbs/hr | 87.5 mmBTU/hr | 9.51lbs/hr | 10 | CO - Carbon Monoxide | PASS | NA | Y
2013 | 898 | 0369000025 | PRO-TEC Coating Company | 5500 PRO-TEC Pkwy | Leipsic | 45856 | 9234 | Putnam | P001 | 92.0 MMBtu/hr natural gas-fired continuous annealing furnace, this includes 12 MMBtu/hr auxiliary natural gas-fired burners [the burners are used to maintain the selective catalytic reduction (SCR) control device operating temperature within the recommended range]. With alkaline cleaning, annealing furnace, water quenching and tempering. | 2013-04-18 | CGL1-SCR(NOx Reduction Technology): Urea Injection and Selective Catalytic Reduction | Custom Stack Analysis, LLC | 92 MMBtu/hr | 11.9 lbs/hr | 83.8 MMBtu/hr | 13.07 lbs/hr | 10 | CO - Carbon Monoxide | FAIL | NA | Y | Failure determination made by Carol Norman. The average SCR temperature for the test was 635.7 F. The urea injection rate was 7.0 gal/hr.
2013 | 900 | 0369000025 | PRO-TEC Coating Company | 5500 PRO-TEC Pkwy | Leipsic | 45856 | 9234 | Putnam | P001 | 92.0 MMBtu/hr natural gas-fired continuous annealing furnace, this includes 12 MMBtu/hr auxiliary natural gas-fired burners [the burners are used to maintain the selective catalytic reduction (SCR) control device operating temperature within the recommended range]. With alkaline cleaning, annealing furnace, water quenching and tempering. | 2013-05-29 | CGL1-SCR(NOx Reduction Technology): Urea Injection and Selective Catalytic Reduction | Custom Stack Analysis, LLC | 92 MMBtu/hr | 11.9 lbs/hr | 85.1 MMBtu/hr | 4.1 lbs/hr | 10 | CO - Carbon Monoxide | PASS | NA | Y | The SCR temperature averaged 633.7 F for the test. The urea injection rate was 6.9 gal/hr.
2016 | 1568 | 0656005025 | REX Booster Station | Twp Rd 964 | Switzerland Twp. | 43915 |  | Monroe | P004 | Caterpillar 3516C. This is a natural gas fired engine associated with the Generator Unit | 2016-05-04 | C001(Catalytic Converter): Oxidation Catalysts; C002(Catalytic Converter): Oxidation Catalysts; C003(Catalytic Converter): Oxidation Catalysts | Alliance Source Testing | 2175 hp | 1.94 g/hp-hr | 1958 hp | 1.66 g/hp-hr | 10 | CO - Carbon Monoxide | PP | Y | NA
2014 | 539 | 1409001140 | Rumpke of Ohio Inc. - Scrap Tire Facility | 3851 South St | Hamilton | 45011 |  | Butler | P012 | 536 Horsepower Diesel Fired Engine for Tire Shredder | 2014-01-15 | Catalytic Oxidizer | O'Brien & Gere Engineers | 546 HP (1800 rpm) | 23 ppmvd @ 15% O2 or 70% CO reduction | 546 HP (1800 rpm) | 0.13 ppmvd @ 15% O2 99.8 % CO reduction | 10 | CO - Carbon Monoxide | PASS | NA | Y | CO and O2 measurements were made using ASTM D6522 in accordance with 40CFR Part 63, Subpart ZZZZ appendix A. ASTM D6522 utilizes portable electrochemical cell analyzers.
2007 | 1495 | 1318538151 | MM Cuyahoga Energy LLC | Cochran and Solon Roads | Solon | 44139 |  | Cuyahoga | P003 | 9.06 MMBtu per hour Caterpillar internal combustion engine for the burning of landfill gas | 2007-09-06 | N/A | CK Environmental | 950 KW | 8.30 lb/hr | 850 KW | 7.70 lb/hr | 10 | CO - Carbon Monoxide | PASS | NA | Y |  | Yes
2007 | 1498 | 1318538151 | MM Cuyahoga Energy LLC | Cochran and Solon Roads | Solon | 44139 |  | Cuyahoga | P004 | 9.06 MMBtu per hour Caterpillar internal combustion engine for the burning of landfill gas | 2007-09-06 | N/A | CK Environmental | 950 KW | 8.30 lb/hr | 850 KW | 6.72 lb/hr | 10 | CO - Carbon Monoxide | PASS | NA | Y |  | Yes
2013 | 320 | 0210012004 | Augusta Compressor Facility- Utica Gas Services, L.L.C. | 8034 Bane Rd NE | East Twp. | 44427 |  | Carroll | P014 | 605-hp Baldor IGLC420-2N Engine Driven Emergency Generator | 2013-10-10 | Oxid. Cat. 3(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 4(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 5(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 6(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 7(Catalytic Converter): | Alliance Source Testing | 605 Hp | 2.67 lbs/hr, 4.0 g/hp/hr, 540 ppmvd@15%O2 | 551 Hp or 91% of Max | 0.08 lbs/hr, 0.1 g/hp/hr, 8.1 ppmvd@15%O2 | 10 | CO - Carbon Monoxide | PASS | NA | Y
2013 | 323 | 0210012004 | Augusta Compressor Facility- Utica Gas Services, L.L.C. | 8034 Bane Rd NE | East Twp. | 44427 |  | Carroll | P015 | 605-hp Baldor IGLC420-2N Engine Driven Emergency Generator | 2013-10-10 | Oxid. Cat. 3(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 4(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 5(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 6(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 7(Catalytic Converter): | Alliance Source Testing | 605 Hp | 2.67 lbs/hr, 4.0 g/hp/hr, 540 ppmvd@15%O2 | 551 Hp or 91% of Max | 0.06 lbs/hr, 0.1 g/hp/hr, 5.8 ppmvd@15%O2 | 10 | CO - Carbon Monoxide | PASS | NA | Y
2013 | 290 | 0210012004 | Augusta Compressor Facility- Utica Gas Services, L.L.C. | 8034 Bane Rd NE | East Twp. | 44427 |  | Carroll | P014 | 605-hp Baldor IGLC420-2N Engine Driven Emergency Generator | 2013-10-09 | Oxid. Cat. 3(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 4(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 5(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 6(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 7(Catalytic Converter): | Alliance Source Testing | 605 Hp | 2.67 lbs/hr, 4.0 g/hp/hr, 540 ppmvd@15%O2 | 551 Hp or 91% of Max | 0.08 lbs/hr, 0.1 g/hp/hr, 8.1 ppmvd@15%O2 | 10 | CO - Carbon Monoxide | PASS | NA | Y
2013 | 294 | 0210012004 | Augusta Compressor Facility- Utica Gas Services, L.L.C. | 8034 Bane Rd NE | East Twp. | 44427 |  | Carroll | P015 | 605-hp Baldor IGLC420-2N Engine Driven Emergency Generator | 2013-10-09 | Oxid. Cat. 3(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 4(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 5(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 6(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 7(Catalytic Converter): | Alliance Source Testing | 605 Hp | 2.67 lbs/hr, 4.0 g/hp/hr, 540 ppmvd@15%O2 | 551 Hp or 91% of Max | 0.06 lbs/hr, 0.1 g/hp/hr, 5.8 ppmvd@15%O2 | 10 | CO - Carbon Monoxide | PASS | NA | Y
2013 | 155 | 0210012004 | Augusta Compressor Facility- Utica Gas Services, L.L.C. | 8034 Bane Rd NE | East Twp. | 44427 |  | Carroll | P014 | 605-hp Baldor IGLC420-2N Engine Driven Emergency Generator | 2013-10-08 | Oxid. Cat. 3(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 4(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 5(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 6(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 7(Catalytic Converter): | Alliance Source Testing | 605 Hp | 2.67 lbs/hr, 4.0 g/hp/hr, 540 ppmvd@15%O2 | 551 Hp or 91% of Max | 0.08 lbs/hr, 0.1 g/hp/hr, 8.1 ppmvd@15%O2 | 10 | CO - Carbon Monoxide | PASS | NA | Y
2013 | 157 | 0210012004 | Augusta Compressor Facility- Utica Gas Services, L.L.C. | 8034 Bane Rd NE | East Twp. | 44427 |  | Carroll | P015 | 605-hp Baldor IGLC420-2N Engine Driven Emergency Generator | 2013-10-08 | Oxid. Cat. 3(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 4(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 5(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 6(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 7(Catalytic Converter): | Alliance Source Testing | 605 Hp | 2.67 lbs/hr, 4.0 g/hp/hr, 540 ppmvd@15%O2 | 551 Hp or 91% of Max | 0.06 lbs/hr, 0.1 g/hp/hr, 5.8 ppmvd@15%O2 | 10 | CO - Carbon Monoxide | PASS | NA | Y
2014 | 1025 | 0634005058 | Atlas Noble, LLC - Cramblett Well Pad | Bowers Road | North Twp. | 43988 |  | Harrison | P003 | NA - One or multiple stationary diesel-fired compression ignition (CI) (diesel) internal combustion engines (ICE), certified to meet the Tier 3 emission standards for diesel engines, with a combined total horsepower (HP) of no more than 250 HP for the site . | 2014-03-04 | none | Air Compliance Consultants | 68 hp | 540 ppm | 33 hp | 114 ppm | 10 | CO - Carbon Monoxide | PASS | NA | Y | VRU engine 2- 68 hp caterpillar engine
2015 | 818 | 0322000295 | Bio-Gas Technologies, LTD | 10215 Hoover Road | Milan | 44846 |  | Erie | P001 | 13.9 mmBtu/hr LFG fired IC engine/generator #1 | 2015-01-21 | None | Air Compliance Testing, Inc. | 1600 kW | 14.76 lbs/hr | 1512 kW | 14.71 lbs/hr | 10 | CO - Carbon Monoxide | PP | NA | Y |  | Yes
2015 | 887 | 0322000295 | Bio-Gas Technologies, LTD | 10215 Hoover Road | Milan | 44846 |  | Erie | P001 | 13.9 mmBtu/hr LFG fired IC engine/generator #1 | 2015-01-22 | None | Air Compliance Testing, Inc. | 800 kW | 7.84 lbs/hr | 779 kW | 3.87 lbs/hr | 10 | CO - Carbon Monoxide | PP | NA | Y |  | Yes
2016 | 718 | 0210012004 | Augusta Compressor Facility- Utica Gas Services, L.L.C. | 8034 Bane Rd NE | East Twp. | 44427 |  | Carroll | P015 | 605-hp Baldor IGLC420-2N Engine Driven Emergency Generator | 2016-09-08 | Oxid. Cat. 3(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 4(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 5(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 6(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 7(Catalytic Converter): | EcoTest Energy Services | 605 Hp | 2.67 lbs/hr, 4.0 g/hp/hr, 540 ppmvd@15%O2 | 560 Hp or 92.6% of Max | 0.09 lbs/hr, 0.07 g/hp/hr, 9 ppmvd@15%O2 | 10 | CO - Carbon Monoxide | PP | Y | NA
2016 | 1176 | 0210012004 | Augusta Compressor Facility- Utica Gas Services, L.L.C. | 8034 Bane Rd NE | East Twp. | 44427 |  | Carroll | P014 | 605-hp Baldor IGLC420-2N Engine Driven Emergency Generator | 2016-09-08 | Oxid. Cat. 3(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 4(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 5(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 6(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 7(Catalytic Converter): | EcoTest Energy Services | 605 Hp | 2.67 lbs/hr, 4.0 g/hp/hr, 540 ppmvd@15%O2 | 560 Hp or 92.6% of Max | 0.11 lbs/hr, 0.09 g/hp/hr, 11 ppmvd@15%O2 | 10 | CO - Carbon Monoxide | PP | Y | NA
2004 | 607 | 0374010117 | Autolite | 1600 N. Union Street | Fostoria | 44830 |  | Seneca | P074 | dynamometer spark plug testing engines. | 2004-11-16 | none | CUSTOM STACK ANALYSIS | 41.98 gallons gasoline/hr | 130.14 lbs/hr | 48.43 gallons gasoline/hr | 120.49 lbs/hr | 10 | CO - Carbon Monoxide | PASS | NA | Y
2013 | 963 | 0374010117 | Autolite | 1600 N. Union Street | Fostoria | 44830 |  | Seneca | P074 | dynamometer spark plug testing engines. | 2013-01-10 | None | Air Compliance Testing, Inc. | 51.0 gallons gasoline/hr | 136.17 lbs/hr | 46.2 gallons gasoline/hr | 195.11 lbs/hr | 10 | CO - Carbon Monoxide | FAIL | NA | Y | Failure determination made by Andrea Odendahl.
2012 | 338 | 0250092002 | City of Struthers WWTP | 530 Lowellville Road | Struthers | 44471 |  | Mahoning | P001 | Stationary internal combustion engine | 2012-01-27 | None | Custom Stack Analysis, LLC | 585 HP | 5.0 g/HP-hr, 610 ppmvd at 15% O2 | 247 HP | 1.56 g/HP-hr, 139.71 ppm at 15% O2 | 10 | CO - Carbon Monoxide | PASS | NA | Y
2012 | 342 | 0250092002 | City of Struthers WWTP | 530 Lowellville Road | Struthers | 44471 |  | Mahoning | P002 | Waukesha H24GLD Engine | 2012-01-30 | None | Custom Stack Analysis, LLC | 585 HP | 5.0 g/HP-hr, 610 ppmvd at 15% O2 | 247 HP | 1.51 g/HP-hr, 135.19 ppm at 15% O2 | 10 | CO - Carbon Monoxide | PASS | NA | Y
2015 | 777 | 0250092002 | City of Struthers WWTP | 530 Lowellville Road | Struthers | 44471 |  | Mahoning | P001 | Stationary internal combustion engine | 2015-03-11 | Catalyst | Custom Stack Analysis | 585 HP as permitted | 5.0 g/HP-hr. 610 ppm @15% O2 | 271 | 1.81g & 140.77 ppm | 10 | CO - Carbon Monoxide | PP | NA | Y
2015 | 782 | 0250092002 | City of Struthers WWTP | 530 Lowellville Road | Struthers | 44471 |  | Mahoning | P001 | Stationary internal combustion engine | 2015-03-12 | Catalyst | Custom Stack Analysis | 585 HP as permitted | 5.0 g/HP-hr. 610 ppm @15% O2 | 271 | 1.81g & 140.77 ppm | 10 | CO - Carbon Monoxide | PP | NA | Y
2015 | 784 | 0250092002 | City of Struthers WWTP | 530 Lowellville Road | Struthers | 44471 |  | Mahoning | P002 | Waukesha H24GLD Engine | 2015-03-11 | Catalyst | Custom Stack Analysis | 585 HP as permitted | 5.0 g/HP-hr. 610 ppm @15% O2 | 264 | 1.89 g & 153.95 ppm | 10 | CO - Carbon Monoxide | PP | NA | Y
2015 | 790 | 0250092002 | City of Struthers WWTP | 530 Lowellville Road | Struthers | 44471 |  | Mahoning | P002 | Waukesha H24GLD Engine | 2015-03-12 | Catalyst | Custom Stack Analysis | 585 HP as permitted | 5.0 g/HP-hr. 610 ppm @15% O2 | 264 | 1.89 g & 153.95 ppm | 10 | CO - Carbon Monoxide | PP | NA | Y
2016 | 1658 | 0857043333 | DP&L Tait Generating Station | 2101 Arbor Boulevard | Moraine | 45439 | 1762 | Montgomery | B507 | Stationary internal combustion engine, large bore No.2 fuel oil-fired electric generator (General Motors Model MP45A); 30 MMBTU/hr maximum heat input | 2016-06-21 | Diesel Oxidation Catalyst | Mostardi Platt | 2.7 MW | 23 ppm CO @15% O2 or 70%DE | 2.5 MW | 20 ppm @15% O2, 96% DE | 10 | CO - Carbon Monoxide | PP | Y | NA | Pressure drops: unit 1: 4"H20 & inlet catalyst temperature 769 degree Fahrenheit, unit 2: 2"H20 & inlet catalyst temperature 757 degree Fahrenheit, unit 3: 2"H20 & inlet catalyst temperature 749 degrees Fahrenheit, unit 4: 2"H20 & inlet catalyst temperatu | Yes
2016 | 1683 | 0857043333 | DP&L Tait Generating Station | 2101 Arbor Boulevard | Moraine | 45439 | 1762 | Montgomery | B510 | Stationary internal combustion engine, large bore No.2 fuel oil-fired electric generator (General Motors Model MP45A); 30 MMBTU/hr maximum heat input | 2016-06-21 | Diesel Oxidation Catalyst | Mostardi Platt | 2.7 MW | 23 ppm CO @15% O2 or 70%DE | 2.5 MW | 36 ppm @15% O2, 90% DE | 10 | CO - Carbon Monoxide | PP | Y | NA | Pressure drops: unit 1: 4"H20 & inlet catalyst temperature 769 degree Fahrenheit, unit 2: 2"H20 & inlet catalyst temperature 757 degree Fahrenheit, unit 3: 2"H20 & inlet catalyst temperature 749 degrees Fahrenheit, unit 4: 2"H20 & inlet catalyst temperatu | Yes
2016 | 1710 | 0857043333 | DP&L Tait Generating Station | 2101 Arbor Boulevard | Moraine | 45439 | 1762 | Montgomery | B509 | Stationary internal combustion engine, large bore No.2 fuel oil-fired electric generator (General Motors Model MP45A); 30 MMBTU/hr maximum heat input | 2016-06-21 | Diesel Oxidation Catalyst | Mostardi Platt | 2.7 MW | 23 ppm CO @15% O2 or 70%DE | 2.5 MW | 44 ppm @ 15% O2, 89% DE | 10 | CO - Carbon Monoxide | PP | Y | NA | Pressure drops: unit 1: 4"H20 & inlet catalyst temperature 769 degree Fahrenheit, unit 2: 2"H20 & inlet catalyst temperature 757 degree Fahrenheit, unit 3: 2"H20 & inlet catalyst temperature 749 degrees Fahrenheit, unit 4: 2"H20 & inlet catalyst temperatu | Yes
2016 | 1721 | 0857043333 | DP&L Tait Generating Station | 2101 Arbor Boulevard | Moraine | 45439 | 1762 | Montgomery | B508 | Stationary internal combustion engine, large bore No.2 fuel oil-fired electric generator (General Motors Model MP45A); 30 MMBTU/hr maximum heat input | 2016-06-21 | Diesel Oxidation Catalyst | Mostardi Platt | 2.7 MW | 23 ppm CO @15% O2 or 70%DE | 2.5 MW | 79 ppm @15% O2, 87% DE | 10 | CO - Carbon Monoxide | PP | Y | NA | Pressure drops: unit 1: 4"H20 & inlet catalyst temperature 769 degree Fahrenheit, unit 2: 2"H20 & inlet catalyst temperature 757 degree Fahrenheit, unit 3: 2"H20 & inlet catalyst temperature 749 degrees Fahrenheit, unit 4: 2"H20 & inlet catalyst temperatu | Yes
2013 | 1318 | 0857040926 | DP&L, Monument Substation | 1131 East Monument Avenue | Dayton | 45402 | 1356 | Montgomery | B001 | Stationary compression ignition (CI) internal combustion engine (ICE), large bore No. 2 fuel oil-fired electric generator (General Motors Model MP45B); greater than 600 brake horsepower (bHP); complying with 40 CFR 63, Subpart ZZZZ Table 2d #3; and installed before 6/12/06. | 2013-06-26 | Diesel Oxidation Catalyst | Mostardi Platt | 2.7 MW; 30 MMBTU/hr | 23 ppm CO @15% O2 or 70% DE | 2.55 MW | 22 ppm CO @ 15% O2, 95% DE | 10 | CO - Carbon Monoxide | PASS | NA | Y |  | Yes
2013 | 1319 | 0857040926 | DP&L, Monument Substation | 1131 East Monument Avenue | Dayton | 45402 | 1356 | Montgomery | B002 | Stationary compression ignition (CI) internal combustion engine (ICE), large bore No. 2 fuel oil-fired electric generator (General Motors Model MP45B); greater than 600 brake horsepower (bHP); complying with 40 CFR 63, Subpart ZZZZ Table 2d #3; and installed before 6/12/06. | 2013-06-26 | Diesel Oxidation Catalyst | Mostardi Platt | 2.7 MW; 30 MMBTU/hr | 23 ppm CO @15% O2 or 70% DE | 2.5 MW | 22 ppm CO @ 15% O2, 94% DE | 10 | CO - Carbon Monoxide | PASS | NA | Y |  | Yes
2013 | 1320 | 0857040926 | DP&L, Monument Substation | 1131 East Monument Avenue | Dayton | 45402 | 1356 | Montgomery | B003 | Stationary compression ignition (CI) internal combustion engine (ICE), large bore No. 2 fuel oil-fired electric generator (General Motors Model MP45B); greater than 600 brake horsepower (bHP); complying with 40 CFR 63, Subpart ZZZZ Table 2d #3; and installed before 6/12/06. | 2013-06-26 | Diesel Oxidation Catalyst | Mostardi Platt | 2.7 MW; 30 MMBTU/hr | 23 ppm CO @15% O2 or 70% DE | 2.5 MW | 15 ppm CO @ 15% O2, 95% DE | 10 | CO - Carbon Monoxide | PASS | NA | Y |  | Yes
2013 | 1321 | 0857040926 | DP&L, Monument Substation | 1131 East Monument Avenue | Dayton | 45402 | 1356 | Montgomery | B004 | Stationary compression ignition (CI) internal combustion engine (ICE), large bore No. 2 fuel oil-fired electric generator (General Motors Model MP45B); greater than 600 brake horsepower (bHP); complying with 40 CFR 63, Subpart ZZZZ Table 2d #3; and installed before 6/12/06. | 2013-06-26 | Diesel Oxidation Catalyst | Mostardi Platt | 2.7 MW; 30 MMBTU/hr | 23 ppm CO @15% O2 or 70% DE | 2.5 MW | 23 ppm CO @ 15% O2, 91% DE | 10 | CO - Carbon Monoxide | PASS | NA | Y |  | Yes
2013 | 1322 | 0857040926 | DP&L, Monument Substation | 1131 East Monument Avenue | Dayton | 45402 | 1356 | Montgomery | B005 | Stationary compression ignition (CI) internal combustion engine (ICE), large bore No. 2 fuel oil-fired electric generator (General Motors Model MP45B); greater than 600 brake horsepower (bHP); complying with 40 CFR 63, Subpart ZZZZ Table 2d #3; and installed before 6/12/06. | 2013-06-26 | Diesel Oxidation Catalyst | Mostardi Platt | 2.7 MW; 30 MMBTU/hr | 23 ppm CO @15% O2 or 70% DE | 2.5 MW | 13 ppm CO @15% O2, 95% DE | 10 | CO - Carbon Monoxide | PASS | NA | Y |  | Yes
2016 | 1664 | 0857040926 | DP&L, Monument Substation | 1131 East Monument Avenue | Dayton | 45402 | 1356 | Montgomery | B004 | Stationary compression ignition (CI) internal combustion engine (ICE), large bore No. 2 fuel oil-fired electric generator (General Motors Model MP45B); greater than 600 brake horsepower (bHP); complying with 40 CFR 63, Subpart ZZZZ Table 2d #3; and instal | 2016-06-22 | Diesel Oxidation Catalyst | Mostardi Platt | 2.7 MW; 30 MMBTU/hr | 23 ppm CO @15% O2 or 70% DE | 2.5 MW | 24 ppm CO @ 15% O2, 89% DE | 10 | CO - Carbon Monoxide | PP | Y | NA | B001 Pressure drop: 1" H2O & catalyst inlet temp 716 B002 Pressure drop: 4" H2O & catalyst inlet temp 640 B003 Pressure drop: 1" H20 & catalyst inlet temp 655 B004 Pressure drop: 0" H2O & catalyst inlet temp 799 B005 Pressure drop: 0" H2O & catalyst inle | Yes
2016 | 1675 | 0857040926 | DP&L, Monument Substation | 1131 East Monument Avenue | Dayton | 45402 | 1356 | Montgomery | B002 | Stationary compression ignition (CI) internal combustion engine (ICE), large bore No. 2 fuel oil-fired electric generator (General Motors Model MP45B); greater than 600 brake horsepower (bHP); complying with 40 CFR 63, Subpart ZZZZ Table 2d #3; and instal | 2016-06-22 | Diesel Oxidation Catalyst | Mostardi Platt | 2.7 MW; 30 MMBTU/hr | 23 ppm CO @15% O2 or 70% DE | 2.5 MW | 26 ppm CO @ 15% O2, 90% DE | 10 | CO - Carbon Monoxide | PP | Y | NA | B001 Pressure drop: 1" H2O & catalyst inlet temp 716 B002 Pressure drop: 4" H2O & catalyst inlet temp 640 B003 Pressure drop: 1" H20 & catalyst inlet temp 655 B004 Pressure drop: 0" H2O & catalyst inlet temp 799 B005 Pressure drop: 0" H2O & catalyst inle | Yes
2016 | 1676 | 0857040926 | DP&L, Monument Substation | 1131 East Monument Avenue | Dayton | 45402 | 1356 | Montgomery | B005 | Stationary compression ignition (CI) internal combustion engine (ICE), large bore No. 2 fuel oil-fired electric generator (General Motors Model MP45B); greater than 600 brake horsepower (bHP); complying with 40 CFR 63, Subpart ZZZZ Table 2d #3; and instal | 2016-06-22 | Diesel Oxidation Catalyst | Mostardi Platt | 2.7 MW; 30 MMBTU/hr | 23 ppm CO @15% O2 or 70% DE | 2.5 MW | 26.7 ppm CO @15% O2, 92% DE | 10 | CO - Carbon Monoxide | PP | Y | NA | B001 Pressure drop: 1" H2O & catalyst inlet temp 716 B002 Pressure drop: 4" H2O & catalyst inlet temp 640 B003 Pressure drop: 1" H20 & catalyst inlet temp 655 B004 Pressure drop: 0" H2O & catalyst inlet temp 799 B005 Pressure drop: 0" H2O & catalyst inle | Yes
2016 | 1678 | 0857040926 | DP&L, Monument Substation | 1131 East Monument Avenue | Dayton | 45402 | 1356 | Montgomery | B003 | Stationary compression ignition (CI) internal combustion engine (ICE), large bore No. 2 fuel oil-fired electric generator (General Motors Model MP45B); greater than 600 brake horsepower (bHP); complying with 40 CFR 63, Subpart ZZZZ Table 2d #3; and instal | 2016-06-22 | Diesel Oxidation Catalyst | Mostardi Platt | 2.7 MW; 30 MMBTU/hr | 23 ppm CO @15% O2 or 70% DE | 2.5 MW | 28 ppm CO @ 15% O2, 92% DE | 10 | CO - Carbon Monoxide | PP | Y | NA | B001 Pressure drop: 1" H2O & catalyst inlet temp 716 B002 Pressure drop: 4" H2O & catalyst inlet temp 640 B003 Pressure drop: 1" H20 & catalyst inlet temp 655 B004 Pressure drop: 0" H2O & catalyst inlet temp 799 B005 Pressure drop: 0" H2O & catalyst inle | Yes
2016 | 1698 | 0857040926 | DP&L, Monument Substation | 1131 East Monument Avenue | Dayton | 45402 | 1356 | Montgomery | B001 | Stationary compression ignition (CI) internal combustion engine (ICE), large bore No. 2 fuel oil-fired electric generator (General Motors Model MP45B); greater than 600 brake horsepower (bHP); complying with 40 CFR 63, Subpart ZZZZ Table 2d #3; and instal | 2016-06-22 | Diesel Oxidation Catalyst | Mostardi Platt | 2.7 MW; 30 MMBTU/hr | 23 ppm CO @15% O2 or 70% DE | 2.5 MW | 39 ppm CO @ 15% O2, 89% DE | 10 | CO - Carbon Monoxide | PP | Y | NA | B001 Pressure drop: 1" H2O & catalyst inlet temp 716 B002 Pressure drop: 4" H2O & catalyst inlet temp 640 B003 Pressure drop: 1" H20 & catalyst inlet temp 655 B004 Pressure drop: 0" H2O & catalyst inlet temp 799 B005 Pressure drop: 0" H2O & catalyst inle | Yes
2016 | 1724 | 0575010008 | DP&L, Sidney Generating Station | 2385 Campbell Road | Sidney | 45365 | 8838 | Shelby | B001 | Stationary internal combustion engine, large bore No. 2 fuel oil-fired electric generator (General Motors Model MP45A); 30 MMBtu/h maximum heat input | 2016-06-16 | catalytic converter | Mostardi/Platt | 2.5 MW | 70 % DRE | 2.5 MW | 86.5 % DRE | 10 | CO - Carbon Monoxide | PP | Y | NA |  | Yes
2016 | 1888 | 0575010008 | DP&L, Sidney Generating Station | 2385 Campbell Road | Sidney | 45365 | 8838 | Shelby | B002 | Stationary internal combustion engine, large bore No. 2 fuel oil-fired electric generator (General Motors Model MP45B); 30 MMBtu/h maximum heat input | 2016-06-16 | catalytic converter | Mostardi/Platt | 2.5 MW | 70 % DRE | 2.5 MW | 87.3 5 DRE | 10 | CO - Carbon Monoxide | PP | Y | NA |  | Yes
2016 | 1889 | 0575010008 | DP&L, Sidney Generating Station | 2385 Campbell Road | Sidney | 45365 | 8838 | Shelby | B004 | Stationary internal combustion engine, large bore No. 2 fuel oil-fired electric generator (General Motors Model MP45B); 30 MMBtu/h maximum heat input | 2016-06-16 | catalytic converter | Mostardi/Platt | 2.5 MW | 70 % DRE | 2.5 MW | 88.9 % DRE | 10 | CO - Carbon Monoxide | PP | Y | NA |  | Yes
2016 | 1890 | 0575010008 | DP&L, Sidney Generating Station | 2385 Campbell Road | Sidney | 45365 | 8838 | Shelby | B005 | Stationary internal combustion engine, large bore No. 2 fuel oil-fired electric generator (General Motors Model MP45B); 30 MMBtu/h maximum heat input | 2016-06-16 | catalytic converter | Mostardi/Platt | 2.5 MW | 70 % DRE | 2.5 MW | 88.9 % DRE | 10 | CO - Carbon Monoxide | PP | Y | NA |  | Yes
2016 | 1891 | 0575010008 | DP&L, Sidney Generating Station | 2385 Campbell Road | Sidney | 45365 | 8838 | Shelby | B003 | Stationary internal combustion engine, large bore No. 2 fuel oil-fired electric generator (General Motors Model MP45B); 30 MMBtu/h maximum heat input | 2016-06-16 | catalytic converter | Mostardi/Platt | 2.5 MW | 70 % DRE | 2.5 MW | 89.2 % DRE | 10 | CO - Carbon Monoxide | PP | Y | NA |  | Yes
2006 | 410 | 0302020143 | Ford Motor Co.-Lima | 1155 Bible Road | Lima | 45801 |  | Allen | P051 | 4 Cell Engine Testing Dynamometer - East | 2006-05-04 | afterburner | KBD Technic, Inc. | 80 gal/hr | 21.1 lbs/hr; 95% DRE | 45.2 gal/hr | 0.06 lbs/hr; 99.97% DRE | 10 | CO - Carbon Monoxide | PASS | NA | Y
2006 | 417 | 0302020143 | Ford Motor Co.-Lima | 1155 Bible Road | Lima | 45801 |  | Allen | P050 | 4 Cell Engine Testing Dynamometer - West Block | 2006-05-05 | afterburner | KBD Technic, Inc. | 80 gal/hr | 21.1 lbs/hr; 95% DRE | 33.9 gal/hr | 0.14 lbs/hr; 99.85% DRE | 10 | CO - Carbon Monoxide | PASS | NA | Y
2006 | 1218 | 1318120179 | Ford Motor Company, Cleveland Engine Plants | 17601 Brookpark Rd | Brook Park | 44142 | 1518 | Cuyahoga | P245 | This PTI application is for the modification of emissions unit P245 to allow the capacity of testing larger (3.5 liter) engines and to provide a larger thermal (recuperative) oxidizer to control the resulting engine exhaust emissions. | 2006-12-08 | Thermal Oxidizer | Conestoga-Rovers & Associates | Three 3.5L D35 Engines | 8.1 lbs/hr & 95% Destruction Effcy. | Three 3.5L D35 Engines | 0.6 lbs/hr & >99.6% Destruction Effcy. | 10 | CO - Carbon Monoxide | PASS | NA | Y
2005 | 1142 | 1409090081 | Miami University | Cole Service Building | Oxford | 45056 |  | Butler | P002 | 5732 KW Lean Burn Natural Gas Fired 4-stroke Reciprocating Engine | 2005-08-17 | CO CATALYST | ENVIRONMENTAL QUALITY MANAGEMENT | 5.7 MW | 3.3 LB/HR; 93% CONTROL | 5.7 MW | 0.2 LB/HR; 99.6% CONTROL | 10 | CO - Carbon Monoxide | PASS | NA | Y | THE TEMPERATURE OF THE GAS AT THE CATALYST INLET WAS 667 DEGREES F AND THE PRESSURE DROP WAS 8.0". | Yes
2005 | 1145 | 1409090081 | Miami University | Cole Service Building | Oxford | 45056 |  | Butler | P001 | 5732 KW Lean Burn Natural Gas Fired 4-stroke Reciprocating Engine | 2005-08-18 | CO CATALYST | ENVIRONMENTAL QUALITY MANAGEMENT | 5.7 MW | 3.3 LB/HR; 93% CONTROL | 5.7 MW | 0.1 LB/HR; 99.6% CONTROL | 10 | CO - Carbon Monoxide | PASS | NA | Y | THE TEMPERATURE OF THE GAS AT THE CATALYST INLET WAS 669 DEGREES F AND THE PRESSURE DROP WAS 8.0". | Yes
2006 | 1336 | 1409090081 | Miami University | Cole Service Building | Oxford | 45056 |  | Butler | P001 | 5732 KW Lean Burn Natural Gas Fired 4-stroke Reciprocating Engine | 2006-05-04 | CO CATALYST | ENVIRONMENTAL QUALITY MANAGEMENT | 5.7 MW | 3.3 LB/HR; 93% CONTROL | 5.6 MW | 0.06 LB/HR; 99.6% CONTROL | 10 | CO - Carbon Monoxide | PASS | NA | Y | THE TEMPERATURE OF THE GAS AT THE CATALYST INLET WAS 680 DEGREES F AND THE PRESSURE DROP WAS 7.5". | Yes
2006 | 1337 | 1409090081 | Miami University | Cole Service Building | Oxford | 45056 |  | Butler | P002 | 5732 KW Lean Burn Natural Gas Fired 4-stroke Reciprocating Engine | 2006-05-05 | CO CATALYST | ENVIRONMENTAL QUALITY MANAGEMENT | 5.7 MW | 3.3 LB/HR; 93% CONTROL | 5.6 MW | 0.08 LB/HR; 99.6% CONTROL | 10 | CO - Carbon Monoxide | PASS | NA | Y | THE TEMPERATURE OF THE GAS AT THE CATALYST INLET WAS 682 DEGREES F AND THE PRESSURE DROP WAS 7.5". | Yes
2006 | 1338 | 1409090081 | Miami University | Cole Service Building | Oxford | 45056 |  | Butler | P001 | 5732 KW Lean Burn Natural Gas Fired 4-stroke Reciprocating Engine | 2006-10-31 | CO CATALYST | ENVIRONMENTAL QUALITY MANAGEMENT | 5.7 MW | 3.3 LB/HR; 93% CONTROL | 5.6 MW | 0.13 LB/HR; 99.6% CONTROL | 10 | CO - Carbon Monoxide | PASS | NA | Y | THE TEMPERATURE OF THE GAS AT THE CATALYST INLET WAS 677 DEGREES F AND THE PRESSURE DROP WAS 7.6". | Yes
2006 | 1339 | 1409090081 | Miami University | Cole Service Building | Oxford | 45056 |  | Butler | P002 | 5732 KW Lean Burn Natural Gas Fired 4-stroke Reciprocating Engine | 2006-10-31 | CO CATALYST | ENVIRONMENTAL QUALITY MANAGEMENT | 5.7 MW | 3.3 LB/HR; 93% CONTROL | 5.6 MW | 0.18 LB/HR; 99.5% CONTROL | 10 | CO - Carbon Monoxide | PASS | NA | Y | THE TEMPERATURE OF THE GAS AT THE CATALYST INLET WAS 656 DEGREES F AND THE PRESSURE DROP WAS 7.5". | Yes
2007 | 1547 | 1409090081 | Miami University | Cole Service Building | Oxford | 45056 |  | Butler | P001 | 5732 KW Lean Burn Natural Gas Fired 4-stroke Reciprocating Engine | 2007-10-30 | CO CATALYST | ENVIRONMENTAL QUALITY MANAGEMENT | 5.7 MW | 3.3 LB/HR; 93% CONTROL | 5.6 MW | 0.10 LB/HR; 99.6% CONTROL | 10 | CO - Carbon Monoxide | PASS | NA | Y | THE TEMPERATURE OF THE GAS AT THE CATALYST INLET WAS 675 DEGREES F AND THE PRESSURE DROP WAS 7.5". | Yes
2007 | 1548 | 1409090081 | Miami University | Cole Service Building | Oxford | 45056 |  | Butler | P002 | 5732 KW Lean Burn Natural Gas Fired 4-stroke Reciprocating Engine | 2007-10-30 | CO CATALYST | ENVIRONMENTAL QUALITY MANAGEMENT | 5.7 MW | 3.3 LB/HR; 93% CONTROL | 5.6 MW | 0.11 LB/HR; 99.6% CONTROL | 10 | CO - Carbon Monoxide | PASS | NA | Y | THE TEMPERATURE OF THE GAS AT THE CATALYST INLET WAS 678 DEGREES F AND THE PRESSURE DROP WAS 7.4". | Yes
2008 | 1720 | 1409090081 | Miami University | Cole Service Building | Oxford | 45056 |  | Butler | P001 | 5732 KW Lean Burn Natural Gas Fired 4-stroke Reciprocating Engine | 2008-09-09 | CO CATALYST | ENVIRONMENTAL QUALITY MANAGEMENT | 5700 kW | 3.3 LB/HR; 93% CONTROL | 5485 kW | 0.10 LB/HR; 99.6% CONTROL | 10 | CO - Carbon Monoxide | PASS | NA | Y | THE TEMPERATURE OF THE GAS AT THE CATALYST INLET WAS 693 DEGREES F AND THE PRESSURE DROP WAS 7.13". | Yes
2008 | 1721 | 1409090081 | Miami University | Cole Service Building | Oxford | 45056 |  | Butler | P002 | 5732 KW Lean Burn Natural Gas Fired 4-stroke Reciprocating Engine | 2008-09-09 | CO CATALYST | ENVIRONMENTAL QUALITY MANAGEMENT | 5700 kW | 3.3 LB/HR; 93% CONTROL | 5498 kW | 0.12 LB/HR; 99.6% CONTROL | 10 | CO - Carbon Monoxide | PASS | NA | Y | THE TEMPERATURE OF THE GAS AT THE CATALYST INLET WAS 700 DEGREES F AND THE PRESSURE DROP WAS 7.45". | Yes
2011 | 1059 | 1409090081 | Miami University | Cole Service Building | Oxford | 45056 |  | Butler | P001 | 5732 KW Lean Burn Natural Gas Fired 4-stroke Reciprocating Engine | 2011-09-07 | CATALYTIC OXIDIZER | ENVIRONMENTAL QUALITY MANAGEMENT | 5732 kW | 3.3 LB/HR; 93% CONTROL | 5387.7 kW | 0.09 LB/HR; 99.5% CONTROL | 10 | CO - Carbon Monoxide | PASS | NA | Y | Average Catalytic Oxidizer during testing was 909 degrees F Average Pressure across the Catalytic Oxidizer was 6.9 inches of water column | Yes
2011 | 1060 | 1409090081 | Miami University | Cole Service Building | Oxford | 45056 |  | Butler | P002 | 5732 KW Lean Burn Natural Gas Fired 4-stroke Reciprocating Engine | 2011-09-07 | CATALYTIC OXIDIZER | ENVIRONMENTAL QUALITY MANAGEMENT | 5732 kW | 3.3 LB/HR; 93% DE | 5393.6 kW | 0.13 LB/HR; 99.4% DE | 10 | CO - Carbon Monoxide | PASS | NA | Y | Catalytic Oxidizer Temperatures averaged 909 degrees F during the test The Pressure Drop across the Catalytic Oxidizer averaged 6.9 inches of water column during the test | Yes
2012 | 1286 | 1409090081 | Miami University | Cole Service Building | Oxford | 45056 |  | Butler | P001 | 5732 KW Lean Burn Natural Gas Fired 4-stroke Reciprocating Engine | 2012-09-05 | CATALYTIC OXIDIZER | ENVIRONMENTAL QUALITY MANAGEMENT | 5732 kW | 3.3 LB/HR; 93% CONTROL | 5400.0 kW | 0.17 LB/HR; 99.0% CONTROL | 10 | CO - Carbon Monoxide | PASS | NA | Y | Average Catalytic Oxidizer during testing was 942 degrees F Average Pressure across the Catalytic Oxidizer was 7.0 inches of water column | Yes
2012 | 1287 | 1409090081 | Miami University | Cole Service Building | Oxford | 45056 |  | Butler | P002 | 5732 KW Lean Burn Natural Gas Fired 4-stroke Reciprocating Engine | 2012-09-05 | CATALYTIC OXIDIZER | ENVIRONMENTAL QUALITY MANAGEMENT | 5732 kW | 3.3 LB/HR; 93% DE | 5650.0 kW | 0.09 LB/HR; 99.4% DE | 10 | CO - Carbon Monoxide | PASS | NA | Y | Catalytic Oxidizer Temperatures averaged 905 degrees F during the test The Pressure Drop across the Catalytic Oxidizer averaged 7.1 inches of water column during the test | Yes
2013 | 1525 | 1409090081 | Miami University | Cole Service Building | Oxford | 45056 |  | Butler | P001 | 5732 KW Lean Burn Natural Gas Fired 4-stroke Reciprocating Engine | 2013-09-04 | CATALYTIC OXIDIZER | ENVIRONMENTAL QUALITY MANAGEMENT | 5732 kW | 3.3 LB/HR; 93% CONTROL | 5405.0 kW | 0.17 LB/HR; 99.2% CONTROL | 10 | CO - Carbon Monoxide | PASS | NA | Y | Average Catalytic Oxidizer during testing was 915.8 degrees F Average Pressure across the Catalytic Oxidizer was 6.8 inches of water column | Yes
2013 | 1526 | 1409090081 | Miami University | Cole Service Building | Oxford | 45056 |  | Butler | P002 | 5732 KW Lean Burn Natural Gas Fired 4-stroke Reciprocating Engine | 2013-09-04 | CATALYTIC OXIDIZER | ENVIRONMENTAL QUALITY MANAGEMENT | 5732 kW | 3.3 LB/HR; 93% DE | 5408.0 kW | 0.06 LB/HR; 99.6% DE | 10 | CO - Carbon Monoxide | PASS | NA | Y | Catalytic Oxidizer Temperatures averaged 933.8 degrees F during the test The Pressure Drop across the Catalytic Oxidizer averaged 7.0 inches of water column during the test | Yes
2014 | 545 | 1409090081 | Miami University | Cole Service Building | Oxford | 45056 |  | Butler | P002 | 5732 KW Lean Burn Natural Gas Fired 4-stroke Reciprocating Engine | 2014-11-26 | CATALYTIC OXIDIZER | ENVIRONMENTAL QUALITY MANAGEMENT | 5732 kW | 3.3 LB/HR; 93% DE | 5545 kW | 0.15 LB/HR; 99.2% DE | 10 | CO - Carbon Monoxide | PASS | NA | Y | Report ID: 90701 ITT ID: 88725 Catalytic Oxidizer Temperatures averaged 799 degrees F during the test The Pressure Drop across the Catalytic Oxidizer averaged 7.2 inches of water column during the test | Yes
2014 | 555 | 1409090081 | Miami University | Cole Service Building | Oxford | 45056 |  | Butler | P001 | 5732 KW Lean Burn Natural Gas Fired 4-stroke Reciprocating Engine | 2014-11-25 | CATALYTIC OXIDIZER | ENVIRONMENTAL QUALITY MANAGEMENT | 5732 kW | 3.3 LB/HR; 93% CONTROL | 5512 kW | 0.16 LB/HR; 99.1% CONTROL | 10 | CO - Carbon Monoxide | PASS | NA | Y | Report ID: 90701 ITT ID: 88725 Average Catalytic Oxidizer during testing was 780 degrees F Average Pressure across the Catalytic Oxidizer was 7.1 inches of water column | Yes
2007 | 1019 | 0575000174 | Honda of America Mfg., Inc. Anna Engine Plant | 12500 Meranda Road | Anna | 45302 | 9699 | Shelby | P006 | PED Engine Testing dynamometers with nine (9) test stands and two thermal oxidizers | 2007-01-03 | RTO | KBD Technic | 120 liters/hr | 7.05 lb/hr | 120 liters/hr | 0.45 lb.hr | 10 | CO - Carbon Monoxide | PASS | NA | Y
2016 | 1281 | 0575000174 | Honda of America Mfg., Inc. Anna Engine Plant | 12500 Meranda Road | Anna | 45302 | 9699 | Shelby | P006 | PED Engine Testing dynamometers with nine (9) test stands and two thermal oxidizers | 2016-07-13 | RTO | KBD Technic | 120 liters/hr | 7.05 lb/hr | 120 liters/hr | 0.13 lb/hr | 10 | CO - Carbon Monoxide | PP | Y | NA
2004 | 136 | 0180000156 | Honda R & D North America Inc. | 21001 St. Rt. 739 | Raymond | 43067 |  | Union | B027 | Engine testing dynamometer, Bldg 5 Room 100B | 2004-05-11 | thermal incinerator | ALMEGA ENVIRONMENTAL, INC. | 22 gallons | 96% reduction (capture x dre) | 21+ gallons | 99.3% reduction (capture x dre) | 10 | CO - Carbon Monoxide | PASS | NA | Y
2012 | 191 | 0180000156 | Honda R & D North America Inc. | 21001 St. Rt. 739 | Raymond | 43067 |  | Union | B014 | Performance Dynamometer, engine testing w/ incinerator control, Bldg. 13 Room 120 | 2012-11-06 | thermal incinerator | KBD Technic | 60 gallons/hr (but the current unit can only achieve about 25 gal/hr) | 98% DE | 19.5 gallons/hr | 99.9% DE | 10 | CO - Carbon Monoxide | PASS | NA | Y | RTOB temp = 1400F
2015 | 917 | 0180000156 | Honda R & D North America Inc. | 21001 St. Rt. 739 | Raymond | 43067 |  | Union | B014 | Performance Dynamometer, engine testing w/ incinerator control, Bldg. 13 Room 120 | 2015-01-14 | thermal incinerator | KBD Technic | 4 dynos per thermal incinerator; 60 gal/hr | 98% DE | 5 dynos per thermal incinerator; 22.1 gal/hr | 99.3% DE | 10 | CO - Carbon Monoxide | PP | NA | Y | thermal incincerator temp = 1380F (Side B only) These dynos are permitted to operate at a maximum 60 gallons per hour, but the current engines are not capable of running that high. The tested operating rate (gal/hr) reported above was the average in Bldg 13 during the test. This test was conducted to demonstrate that Side B can meet the 98% CO DE when controlling 5 dynos. A compliance demonstration is still needed for Side A. Side B will remain in operation until B054 is ready for compliance testing at which time Honda R&D will complete compliance testing on Side A and "check" Side B (10% of Side A results) at that time.
2015 | 921 | 0180000156 | Honda R & D North America Inc. | 21001 St. Rt. 739 | Raymond | 43067 |  | Union | B014 | Performance Dynamometer, engine testing w/ incinerator control, Bldg. 13 Room 120 | 2015-05-27 | Bldg 13 RTO(Thermal Incinerator): Control effieciency by design | KBD Technic | 5 dynos per thermal incinerator; 60 gal/hr | 98% DE | 6 dynos per thermal incinerator; 21.2 gal/hr | 99.3% DE | 10 | CO - Carbon Monoxide | PP | NA | Y | thermal incincerator temp = 1400°F (Side B only) These dynos are permitted to operate at a maximum 60 gallons per hour, but the current engines are not capable of running that high. The tested operating rate (gal/hr) reported above was the average in Bldg 13 during the test. This test was conducted to demonstrate that Side B can meet the 98% CO DE when controlling 6 dynos. A compliance demonstration is still needed for Side A.
2015 | 922 | 0180000156 | Honda R & D North America Inc. | 21001 St. Rt. 739 | Raymond | 43067 |  | Union | B013 | Performance Dynamometer, engine testing w/ incinerator control, Bldg. 5 Room 101 | 2015-01-13 | thermal incinerator | KBD Technic | 7 dynos to both thermal incinerators; 60 gal/hr | 98% DE | 5-6 dynos operating at all times; 15.5 gal/hr | 99.7% DE | 10 | CO - Carbon Monoxide | PP | NA | Y | thermal incincerator temp = 1375F (both sides) 1 of the 7 dynos permitted to vent to the thermal incinerators has not yet been installed (B057). These dynos are permitted to operate at a maximum 60 gallons per hour, but the current engines are not capable of running that high. The tested operating rate (gal/hr) reported above was the average in Bldg 5 during the test.
2015 | 927 | 0180000156 | Honda R & D North America Inc. | 21001 St. Rt. 739 | Raymond | 43067 |  | Union | B015 | Durability Dynamometer, engine testing w/ incinerator control, Bldg. 5 Room 105 | 2015-01-13 | thermal incinerator | KBD Technic | 7 dynos to both thermal incinerators; 60 gal/hr | 98% DE | 5-6 dynos operating at all times; 15.5 gal/hr | 99.7%DE | 10 | CO - Carbon Monoxide | PP | NA | Y | thermal incincerator temp = 1375F (both sides) 1 of the 7 dynos permitted to vent to the thermal incinerators has not yet been installed (B057). These dynos are permitted to operate at a maximum 60 gallons per hour, but the current engines are not capable of running that high. The tested operating rate (gal/hr) reported above was the average in Bldg 5 during the test.
2015 | 928 | 0180000156 | Honda R & D North America Inc. | 21001 St. Rt. 739 | Raymond | 43067 |  | Union | B027 | Engine testing dynamometer, Bldg 5 Room 100B | 2015-01-13 | thermal incinerator | KBD Technic | 7 dynos to both thermal incinerators; 60 gal/hr | 98% DE | 5-6 dynos operating at all times; 15.5 gal/hr | 99.7%DE | 10 | CO - Carbon Monoxide | PP | NA | Y | thermal incincerator temp = 1375F (both sides) 1 of the 7 dynos permitted to vent to the thermal incinerators has not yet been installed (B057). These dynos are permitted to operate at a maximum 60 gallons per hour, but the current engines are not capable of running that high. The tested operating rate (gal/hr) reported above was the average in Bldg 5 during the test.
2016 | 2246 | 0180000156 | Honda R & D North America Inc. | 21001 St. Rt. 739 | Raymond | 43067 |  | Union | B015 | Durability Dynamometer, engine testing w/ incinerator control, Bldg. 5 Room 105 | 2016-02-11 | B015 CAT(Catalytic Incinerator): B015 Catalyst System | KBD Technic | N/A | 98% CO DRE | N/A | 99.8% CO DRE | 10 | CO - Carbon Monoxide | PP | Y | NA | Incinerator 3-hour avg = 700°F
2016 | 2420 | 0180000156 | Honda R & D North America Inc. | 21001 St. Rt. 739 | Raymond | 43067 |  | Union | B014 | Performance Dynamometer, engine testing w/ incinerator control, Bldg. 13 Room 120 | 2016-02-11 | Bldg 13 RTO(Thermal Incinerator): Control effieciency by design | KBD Technic | N/A | 98% CO DRE | N/A | 99.9% CO DRE | 10 | CO - Carbon Monoxide | PP | Y | NA | TO 3-hour avg = 1380°F
2014 | 1833 | 0370010058 | Jay Plastics, Inc. | 150 East Longview Avenue | Mansfield | 44903 | 4206 | Richland | P004 | Generator #1 - 10.98 MMBtu/hr (1391 HP), natural gas-fired, 4SRB, spark-ignited RICE for use as a generated power supply (peak shaving). | 2014-02-26 | Nonselective Catalytic Reduction | Air Compliance Testing, Inc. | 1038 kW | 75% reduction efficiency | 768.8 kW | 82.5% reduction efficiency | 10 | CO - Carbon Monoxide | PASS | NA | Y | Low process weight rate determination made by Chad Winebrenner. | Yes
2014 | 875 | 0370010128 | Jay Plastics-Broscho Fab. Prod. Div. | 1595 W. LONGVIEW AVENUE | Mansfield | 44906 |  | Richland | P006 | 9.361 mmBtu/hr (1531 HP) NG, 4-stroke, LB, SI ICE - Generator #4 | 2014-02-26 | GEN1 cat(Catalytic Converter): 3-way catalytic converter for Generator #1 | Air Compliance Testing, Inc. | 1142 kW | 4.0 g/bhp-hr | 1089.05 kW | 1.1 g/bhp-hr | 10 | CO - Carbon Monoxide | PASS | NA | Y |  | Yes
2014 | 887 | 0370010128 | Jay Plastics-Broscho Fab. Prod. Div. | 1595 W. LONGVIEW AVENUE | Mansfield | 44906 |  | Richland | P002 | 11.581 mmBtu/hour (1475 HP), Natural Gas-Fired, 4-Stroke, Rich-Burn, Spark Ignition, Reciprocating Internal Combustion Engine, w/NSCR | 2014-02-28 | GEN1 cat(Catalytic Converter): 3-way catalytic converter for Generator #1 | Air Compliance Testing, Inc. | 1368 kW | 1.80 g/bhp-hr, 75% reduction efficiency | 1042.5 kW | 1.41 g/bhp-hr, 87.1% reduction efficiency | 10 | CO - Carbon Monoxide | PASS | NA | Y | Low process weight rate determination made by Chad Winebrenner. | Yes
2014 | 1838 | 0370010128 | Jay Plastics-Broscho Fab. Prod. Div. | 1595 W. LONGVIEW AVENUE | Mansfield | 44906 |  | Richland | P003 | 11.581 mmBtu/hour (1475 HP), Natural Gas-Fired, 4-Stroke,Rich-Burn, Spark Ignition, Reciprocating Internal Combustion Engine, w/NSCR. | 2014-03-01 | GEN1 cat(Catalytic Converter): 3-way catalytic converter for Generator #1 | Air Compliance Testing, Inc. | 1368 kW | 75% reduction efficiency | 1020.95 kW | 84.8% reduction efficiency | 10 | CO - Carbon Monoxide | PASS | NA | Y | Low process weight rate determination made by Chad Winebrenner. | Yes
2014 | 1846 | 0370010128 | Jay Plastics-Broscho Fab. Prod. Div. | 1595 W. LONGVIEW AVENUE | Mansfield | 44906 |  | Richland | P004 | 11.581 mmBtu/hour (1475 HP), Natural Gas-Fired, 4-Stroke, Rich-Burn, Spark Ignition, Reciprocating Internal Combustion Engine, w/NSCR. | 2014-03-01 | GEN1 cat(Catalytic Converter): 3-way catalytic converter for Generator #1 | Air Compliance Testing, Inc. | 1368 kW | 75% reduction efficiency | 1000 kW | 87.3% reduction efficiency | 10 | CO - Carbon Monoxide | PASS | NA | Y | Low process weight rate determination made by Chad Winebrenner. | Yes
2016 | 1304 | 0210002039 | Kilgore Compressor Station-Utica Gas Services, LLC | Pontiff Rd | Kilgore | 43988 |  | Carroll | P013 | 605 hp NG-fired generator equipped w/3-way catalyst Baldor IGLC420-2N: engine reconstructed and given new manufacture date 2016-02-23 (see compliance reports) | 2016-04-18 | CC013(Catalytic Converter): Generator #3 - Three-way Catalyst | Alliance Source Testing, Inc. | 605 Hp | 4.0g/hp-hr & 86 ppm @ 15%O2 | 555 | 0.154 g/hp-hr & 18.2 ppm @ 15%O2 | 10 | CO - Carbon Monoxide | PP | Y | NA
2012 | 373 | 0285000421 | PIONEER EQUIPMENT, INC. | 16875 JERICHO RD. | DALTON | 44618 |  | Wayne | P004 | Stationary natural gas, spark ignition (SI) internal combustion engine (ICE); 440 horsepower (hp), used as primary power source | 2012-10-05 | None | Custom Stack Analysis | 440 Hp | 540 ppm @15%O2 or 4.0 g/hp-hr | 340 HP | 284.11 and 1.1 | 10 | CO - Carbon Monoxide | PASS | NA | Y | The Tested average emission rate comes from only runs two and three. Run one was omittted from the average because of an adjustment made after the test run was completed.

## Engine VOC
REPORTING YEAR | RECORD_NUMBER | FACILITY ID | FACILITY NAME | ADDRESS | CITY | ZIP5 | ZIP4 | COUNTY | EUID | EUID DESCRIPTION | EVALUATION DATE | CONTROL EQUPMENT | COMPANY PERFORMING TEST | MAX RATE | ALLOWABLE RATE | TESTED OPERATING RATE | TESTED EMISSION RATE | METHOD NUMBER | POLLUTANTS | RESULTS | CONFORM | AUDIT | NOTES | COULD_BE_GENERATOR
2008 | 398 | 0125102034 | Dominion - Groveport Compressor Station | 5509 Berger Road | Groveport | 43125 |  | Franklin | B002 | 4200 HP Engine-spark ignition, 2-stroke, lean burn | 2008-11-05 | none | DOMINION TRANSMISSION | 4200 hp | 8.33 lbs/hr | 4066 hp | 0.92 lbs/hr | 25A | Total Hydrocarbons | PASS | NA | Y
2008 | 400 | 0125102034 | Dominion - Groveport Compressor Station | 5509 Berger Road | Groveport | 43125 |  | Franklin | B001 | 4200 HP Engine-spark ignition, 2-stroke, lean burn | 2008-11-06 | none | DOMINION TRANSMISSION | 4200 hp | 18.52 lbs/hr | 4072.9 | 4.80 lbs/hr | 25A | Total Hydrocarbons | PASS | NA | Y
2008 | 405 | 0125102034 | Dominion - Groveport Compressor Station | 5509 Berger Road | Groveport | 43125 |  | Franklin | B003 | 3200 HP Engine-spark ignition, 2-stroke, lean burn | 2008-11-06 | none | DOMINION TRANSMISSION | 3200 hp | 5.64 lbs/hr | 3149.6 hp | 0.61lbs/hr | 25A | Total Hydrocarbons | PASS | NA | Y
2011 | 323 | 0250000911 | East Ohio Gas Company - Austintown | 9686 NEW ROAD | Austintown Twp. | 44451 | 9708 | Mahoning | B003 | Natural gas-fired, 4-stroke, lean burn, reciprocating internal combustion engine (Caterpillar G3516TALE) rated at 1,340 HP, 11.9 mmBtu/hr equipped with a selective catalytic reduction system to control carbon monoxide (CO), volatile organic compounds (VOC) and formaldehyde. | 2011-04-28 | Selective catalytic reduction | Environmental Quality Management, Inc. | 1340 HP | 86 ppmvd @ 15% O2, 1.0 g/HP-hr | 1270 HP | 58.9 ppmvd @ 15% O2, 0.29 g/HPhr | 25A | Total Hydrocarbons | FAIL | NA | Y
2011 | 362 | 0285000366 | East Ohio Gas - Chippewa Station | 17045 Galehouse Road | Doylestown | 44230 |  | Wayne | B010 | 2,370 hp 4SLB SI ICE; CAT G3608 | 2011-06-28 | oxidation catalyst | Environmental Quality Management, Inc. | 100% ¿10% load | .95 lb/hr | 100% +/- 10% of load rating | 0.10 lb/hr | 25A | Total Hydrocarbons | PASS | NA | Y
2011 | 768 | 0661005002 | Summerfield Compressor Station | between CR-45 and HWY 233 | Caldwell | 43724 |  | Noble | P001 | Natural Gas Engine(1) 1,380 hp engine | 2011-03-29 | Catalytic Silencer | BCMJ Controls | 1,380 Hp | 0.7 g/Hp-hr, 60 -15% O2 ppmvd | 1,104 Hp | 0.13 g/Hp-hr, 7.5 - 15% O2 ppmvd | 25A | Total Hydrocarbons | PASS | NA | Y
2011 | 772 | 0661005002 | Summerfield Compressor Station | between CR-45 and HWY 233 | Caldwell | 43724 |  | Noble | P002 | Natural Gas Engine (2) 1,380 hp | 2011-03-29 | Catalytic Silencer | BCMJ Controls | 1,380 Hp | 0.7 g/Hp-hr, 60 -15% O2 ppmvd | 1,104 Hp | 0.10 g/Hp-hr, 5.7 - 15% O2 ppmvd | 25A | Total Hydrocarbons | PASS | NA | Y
2011 | 964 | 0857103154 | PINNACLE GAS PRODUCERS LLC | 4220 PINNACLE RD | MORAINE | 45439 |  | Montgomery | B001 | 12 MMBtu/hour (1,626 bhp) pipeline quality gas/natural gas-fired compressor engine | 2011-03-10 | N/A | DTE ENERGY | 1200 RPM | 5.38 LB/HR NMOC | 1017 RPM | NON-DETECT NMOC | 25A | Total Hydrocarbons | PASS | NA | Y | NON-DETECT NMOC RESULTS AFTER USE OF BOTH METHOD 18 AND ALT-078 DATA INDICATED THAT THE DATA DETERMINED FROM M25A WAS COMPRISED PRIMARILY OF METHANE. THE NOVEMBER DEMONSTRATION FROM THIS SITE MAY HAVE BEEN INACCURATELY SAMPLED AS THE METHANE SAMPLE WAS TAKEN AFTER CONDENSATE REMOVAL LEADING TO QUESTIONABLE RESUTS.
2012 | 275 | 0210012015 | Chesapeake Exploration LLC - Snoddy 11-13-5 Pad | Sorrel Road (TWP HWY 620) | Carrollton | 44615 |  | Carroll | P002 | Flash gas compressor with catalyst, 211 hp SI ICE | 2012-10-03 | Catalyst | Alliance Source Testing. | 211 hp | 86 ppmvd@15%O2 | 116 hp | 3.1 ppmvd @15%O2 | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y
2012 | 320 | 0250000911 | East Ohio Gas Company - Austintown | 9686 NEW ROAD | Austintown Twp. | 44451 | 9708 | Mahoning | B003 | Natural gas-fired, 4-stroke, lean burn, reciprocating internal combustion engine (Caterpillar G3516TALE) rated at 1,340 HP, 11.9 mmBtu/hr equipped with a selective catalytic reduction system to control carbon monoxide (CO), volatile organic compounds (VOC) and formaldehyde. | 2012-03-19 | Selective catalytic reduction | Environmental Quality Management, Inc. | 1340 HP | 86 ppmvd @ 15% O2, 1.0 g/HP-hr | 1264 HP | 21.9 ppmvd @ 15% O2, 0.11 g/HPhr | 25A | Total Hydrocarbons | PASS | NA | Y
2012 | 335 | 0250092002 | City of Struthers WWTP | 530 Lowellville Road | Struthers | 44471 |  | Mahoning | P001 | Stationary internal combustion engine | 2012-01-27 | None | Custom Stack Analysis, LLC | 585 HP | 1.0 g/HP-hr, 80 ppmvd at 15% O2 | 247 HP | 0.19 g/HP-hr, 10.54 ppm at 15% O2 | 25A | Total Hydrocarbons | PASS | NA | Y
2012 | 339 | 0250092002 | City of Struthers WWTP | 530 Lowellville Road | Struthers | 44471 |  | Mahoning | P002 | Waukesha H24GLD Engine | 2012-01-30 | None | Custom Stack Analysis, LLC | 585 HP | 1.0 g/HP-hr, 80 ppmvd at 15% O2 | 247 HP | 0.13 g/HP-hr, 7.53 ppm at 15% O2 | 25A | Total Hydrocarbons | PASS | NA | Y
2012 | 364 | 0285000366 | East Ohio Gas - Chippewa Station | 17045 Galehouse Road | Doylestown | 44230 |  | Wayne | B010 | 2,370 hp 4SLB SI ICE; CAT G3608 | 2012-06-12 | oxidation catalyst | Environmental Quality Management, Inc. | 100% ¿10% load | 1.0 grams/hp-hr | 100% +/- 10% load rating | .006 grams hp/hr | 24A | VOC - Volatile Organic Compounds | PASS | NA | Y
2012 | 369 | 0285000388 | East Ohio Gas Company - Paint | STATE RTE 250 | Wooster | 44624 |  | Wayne | B002 | Natural gas fired Internal Combustion Engine with max input capacity of 11.9 MMBtu/hr - Caterpillar G3516TALE with 1340 HP, 4-stroke, selective catalytic reduction (SCR) | 2012-08-29 | Three way Catalyst | Environmental Quality Management | 1340 HP | 86 ppm @ 15% O2 and 1.0 g/hp-hr | 1233 HP-hr | 17.7 ppm @ 15% O2 and 0.08 g/hp-hr | 25A | Total Hydrocarbons | PASS | NA | Y
2012 | 729 | 0661005002 | Summerfield Compressor Station | between CR-45 and HWY 233 | Caldwell | 43724 |  | Noble | P001 | Natural Gas Engine(1) 1,380 hp engine | 2012-03-12 | Catalytic Silencer | BCMJ Controls | 1,380 Hp | 0.7 g/Hp-hr, 60 -15% O2 ppmvd | 1,104 Hp | 0.05g/Hp-hr, 3.0 - 15% O2 ppmvd | 25A | Total Hydrocarbons | PASS | NA | Y
2012 | 735 | 0661005002 | Summerfield Compressor Station | between CR-45 and HWY 233 | Caldwell | 43724 |  | Noble | P002 | Natural Gas Engine (2) 1,380 hp | 2012-03-12 | Catalytic Silencer | BCMJ Controls | 1,380 Hp | 0.7 g/Hp-hr, 60 -15% O2 ppmvd | 1,104 Hp | 0.05g/Hp-hr, 2.7 - 15% O2 ppmvd | 25A | Total Hydrocarbons | PASS | NA | Y
2013 | 147 | 0210012004 | Augusta Compressor Facility- Utica Gas Services, L.L.C. | 8034 Bane Rd NE | East Twp. | 44427 |  | Carroll | P012 | 1,775-hp Caterpillar G3606 Compressor Engine w/ Oxidation Catalyst | 2013-10-08 | Oxid. Cat. 3(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 4(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 5(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 6(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 7(Catalytic Converter): | Alliance Source Testing | 1775 Hp | 0.54 lbs/hr, 0.7 g/hp/hr, 60ppmvd@15%O2 | 1703 Hp or 96% of Max | 0.17 lbs/hr, 0.05 g/hp/hr, 4.2ppmvd@15%O2 | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y
2013 | 152 | 0210012004 | Augusta Compressor Facility- Utica Gas Services, L.L.C. | 8034 Bane Rd NE | East Twp. | 44427 |  | Carroll | P013 | 1,775-hp Caterpillar G3606 Compressor Engine w/ Oxidation Catalyst | 2013-10-08 | Oxid. Cat. 3(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 4(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 5(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 6(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 7(Catalytic Converter): | Alliance Source Testing | 1775 Hp | 0.54 lbs/hr, 0.7 g/hp/hr, 60ppmvd@15%O2 | 1680 Hp or 95% of Max | 0.13 lbs/hr, 0.04 g/hp/hr, 3.2ppmvd@15%O2 | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y
2013 | 160 | 0210012004 | Augusta Compressor Facility- Utica Gas Services, L.L.C. | 8034 Bane Rd NE | East Twp. | 44427 |  | Carroll | P006 | 1,775-hp Caterpillar G3606 Compressor Engine w/ Oxidation Catalyst | 2013-10-09 | Oxid. Cat. 3(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 4(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 5(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 6(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 7(Catalytic Converter): | Alliance Source Testing | 1775 Hp | 0.54 lbs/hr, 0.7 g/hp/hr, 60ppmvd@15%O2 | 1651 Hp or 93% of Max | 0.16 lbs/hr, 0.05 g/hp/hr, 4.1ppmvd@15%O2 | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y
2013 | 162 | 0210012004 | Augusta Compressor Facility- Utica Gas Services, L.L.C. | 8034 Bane Rd NE | East Twp. | 44427 |  | Carroll | P007 | 1,775-hp Caterpillar G3606 Compressor Engine w/ Oxidation Catalyst | 2013-10-09 | Oxid. Cat. 3(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 4(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 5(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 6(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 7(Catalytic Converter): | Alliance Source Testing | 1775 Hp | 0.54 lbs/hr, 0.7 g/hp/hr, 60ppmvd@15%O2 | 1624 Hp or 91% of Max | 0.23 lbs/hr, 0.06 g/hp/hr, 5.7ppmvd@15%O2 | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y
2013 | 166 | 0210012004 | Augusta Compressor Facility- Utica Gas Services, L.L.C. | 8034 Bane Rd NE | East Twp. | 44427 |  | Carroll | P008 | 1,775-hp Caterpillar G3606 Compressor Engine w/ Oxidation Catalyst | 2013-10-09 | Oxid. Cat. 3(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 4(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 5(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 6(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 7(Catalytic Converter): | Alliance Source Testing | 1775 Hp | 0.54 lbs/hr, 0.7 g/hp/hr, 60ppmvd@15%O2 | 1610 Hp or 91% of Max | 0.21 lbs/hr, 0.1 g/hp/hr, 5.3ppmvd@15%O2 | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y
2013 | 186 | 0210002013 | Chesapeake Exploration LLC - Slates 16-12-5 | County Highway 59 | Kilgore | 43903 |  | Carroll | P002 | 211 hp CAT G3306TA Flash Gas Compressor equipped with catalyst. For this EU, GP12.1 covers one or multiple stationary natural gas-fired spark ignition (SI) internal combustion engines (ICE) with a combined total horsepower (HP) of no more than 1,800 HP for the site. Includes 2007 and later model year engines manufactured after the applicable effective date identified in 40 CFR 60.4230(a)(3) and engines manufactured before the effective date of the NSPS, where compliance with the Part 60 Subpart JJJJ emissions standards for the same size engine can be met by retrofitting the engine with a control device and demonstrated through stack testing. | 2013-08-08 | N/A | Alliance Source Testing, Inc. | 211 bhp | 60 ppmvd@15%O2 | 96% or 202 bhp | 6.0 ppmvd@15%O2 | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y | Caterpillar 215 bhp Natural Gas Engine G6X08478
2013 | 189 | 0210002014 | Chesapeake Exploration LLC - Scott 24-12-5 Pad | Ponder Rd | Kilgore | 44615 |  | Carroll | P002 | 211 hp CAT G3306TA flash gas compressor equipped with catalyst. For this EU, GP12.1 covers one or multiple stationary natural gas-fired spark ignition (SI) internal combustion engines (ICE) with a combined total horsepower (HP) of no more than 1,800 HP for the site. Includes 2007 and later model year engines manufactured after the applicable effective date identified in 40 CFR 60.4230(a)(3) and engines manufactured before the effective date of the NSPS, where compliance with the Part 60 Subpart JJJJ emissions standards for the same size engine can be met by retrofitting the engine with a control device and demonstrated through stack testing. | 2013-05-22 | Catalyst | Alliance Source Testing, Inc. | 215 hp | 2.9 lb/hr or 1.0 g/hp-hr | 176 = 75% | 0.06 lb/hr or 0.2 g/Hp-hr | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y | Testing was accepted a the rate of 75% of max given that the facility is aware if they increase above this rate by more than 10% of the tested rate they will have to test again.
2013 | 193 | 0210012002 | Utica Gas Services, LLC-Carrollton Compressor Facility | 2098 Panda Road SE | Carrollton | 44615 |  | Carroll | P009 | 1,775 HP natural gas-fired Caterpillar G3606 engine #6 equipped with an oxidation catalyst | 2013-03-06 | Oxid. Cat.(Catalytic Converter): Oxidative Catalyst | Air Hygiene Inc. | 1775 Hp | VOC< 60 ppmvd @ 15% O2 and 0.7 g/ hp-hr. | 1652 Hp | 3.9 ppmvd@ 15% O2 and 0.04 g/hp-hr | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y | Method 320 utilized to provide the NMHC numbers in place of 25A. 320 pollutant designation is not applicable to this test event. Using the 25A tab for VOC reporting purposes.
2013 | 195 | 0210012002 | Utica Gas Services, LLC-Carrollton Compressor Facility | 2098 Panda Road SE | Carrollton | 44615 |  | Carroll | P010 | 1,775 HP natural gas-fired Caterpillar G3606 engine #7 equipped with an oxidation catalyst | 2013-03-06 | Oxid. Cat.(Catalytic Converter): Oxidative Catalyst | Air Hygiene, Inc. | 1775 Hp | VOC< 60 ppmvd @ 15% O2 and 0.7 g/ hp-hr. | 1608 Hp | 4.49 ppmvd@ 15% O2 and 0.05 g/hp-hr | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y | Method 320 utilized to provide the NMHC numbers in place of 25A. 320 pollutant designation is not applicable to this test event. Using the 25A tab for VOC reporting purposes.
2013 | 199 | 0210012002 | Utica Gas Services, LLC-Carrollton Compressor Facility | 2098 Panda Road SE | Carrollton | 44615 |  | Carroll | P006 | 1,775 HP natural gas-fired Caterpillar G3606 engine #3 equipped with an oxidation catalyst | 2013-03-07 | Oxid. Cat.(Catalytic Converter): Oxidative Catalyst | Alliance Source Testing | 1775 HP | VOC< 60 ppmvd @ 15% O2 and 0.7 g/ hp-hr. | 1666 Hp | 6.4 ppmvd@ 15% O2 and 0.05 g/hp-hr | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y
2013 | 203 | 0210012002 | Utica Gas Services, LLC-Carrollton Compressor Facility | 2098 Panda Road SE | Carrollton | 44615 |  | Carroll | P007 | 1,775 HP natural gas-fired Caterpillar G3606 engine #4 equipped with an oxidation catalyst | 2013-03-07 | Oxid. Cat.(Catalytic Converter): Oxidative Catalyst | Alliance Source Testing | 1775 Hp | VOC< 60 ppmvd @ 15% O2 and 0.7 g/ hp-hr. | 1690 Hp | 5.9 ppmvd@ 15% O2 and 0.1 g/hp-hr | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y
2013 | 206 | 0210012002 | Utica Gas Services, LLC-Carrollton Compressor Facility | 2098 Panda Road SE | Carrollton | 44615 |  | Carroll | P008 | 1,775 HP natural gas-fired Caterpillar G3606 engine #5 equipped with an oxidation catalyst | 2013-03-07 | Oxid. Cat.(Catalytic Converter): Oxidative Catalyst | Air Hygiene Inc. | 1775 Hp | VOC< 60 ppmvd @ 15% O2 and 0.7 g/ hp-hr. | 1657 Hp | 5.5 ppmvd@ 15% O2 and 0.05 g/hp-hr | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y | Method 320 utilized to provide the NMHC numbers in place of 25A. 320 pollutant designation is not applicable to this test event. Using the 25A tab for VOC reporting purposes.
2013 | 208 | 0210012002 | Utica Gas Services, LLC-Carrollton Compressor Facility | 2098 Panda Road SE | Carrollton | 44615 |  | Carroll | P011 | 1,775 HP natural gas-fired Caterpillar G3606 engine #8 equipped with an oxidation catalyst | 2013-03-07 | Oxid. Cat.(Catalytic Converter): Oxidative Catalyst | Air Hygiene, Inc. | 1775 Hp | VOC< 60 ppmvd @ 15% O2 and 0.7 g/ hp-hr. | 1654 Hp | 2.52 ppmvd@ 15% O2 and 0.02 g/hp-hr | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y | Method 320 utilized to provide the NMHC numbers in place of 25A. 320 pollutant designation is not applicable to this test event. Using the 25A tab for VOC reporting purposes.
2013 | 210 | 0210012002 | Utica Gas Services, LLC-Carrollton Compressor Facility | 2098 Panda Road SE | Carrollton | 44615 |  | Carroll | P012 | 1,775 HP natural gas-fired Caterpillar G3606 engine #9 equipped with an oxidation catalyst | 2013-03-08 | Oxid. Cat.(Catalytic Converter): Oxidative Catalyst | Air Hygiene, Inc | 1775 hp | VOC< 60 ppmvd @ 15% O2 and 0.7 g/ hp-hr. | 1661 Hp | 3.31 ppmvd@ 15% O2 and 0.03 g/hp-hr | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y | Method 320 utilized to provide the NMHC numbers in place of 25A. 320 pollutant designation is not applicable to this test event. Using the 25A tab for VOC reporting purposes.
2013 | 214 | 0210012002 | Utica Gas Services, LLC-Carrollton Compressor Facility | 2098 Panda Road SE | Carrollton | 44615 |  | Carroll | P004 | 1,775 HP natural gas-fired Caterpillar G3606 engine #1 equipped with an oxidation catalyst. | 2013-05-01 | Oxid. Cat.(Catalytic Converter): Oxidative Catalyst | Air Hygiene Inc. | 1775 Hp | 86 ppmvd @ 15% O2 and 1.0g/hp-hr | 1678 Hp | 4.5 ppmvd @ 15% O2 and .04 g/hp-hr | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y
2013 | 218 | 0210012002 | Utica Gas Services, LLC-Carrollton Compressor Facility | 2098 Panda Road SE | Carrollton | 44615 |  | Carroll | P005 | 1,775 HP natural gas-fired Caterpillar G3606 engine #2 equipped with an oxidation catalyst | 2013-05-01 | Oxid. Cat.(Catalytic Converter): Oxidative Catalyst | Air Hygiene Inc. | 1775 Hp | 86 ppmvd @ 15% O2 and 1.0g/hp-hr | 1625 Hp | 4.96 ppmvd @ 15% O2 and 0 g/hp-hr | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y
2013 | 219 | 0210012002 | Utica Gas Services, LLC-Carrollton Compressor Facility | 2098 Panda Road SE | Carrollton | 44615 |  | Carroll | P013 | 1,775 HP natural gas-fired Caterpillar G3606 engine #10equipped with an oxidation catalyst | 2013-05-01 | Oxid. Cat.(Catalytic Converter): Oxidative Catalyst | Air Hygiene Inc. | 1775 Hp | 86 ppmvd @ 15% O2 and 1.0g/hp-hr | 1620Hp | 4.21 ppmvd @ 15% O2 and 0 g/hp-hr | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y
2013 | 225 | 0210012004 | Augusta Compressor Facility- Utica Gas Services, L.L.C. | 8034 Bane Rd NE | East Twp. | 44427 |  | Carroll | P006 | 1,775-hp Caterpillar G3606 Compressor Engine w/ Oxidation Catalyst | 2013-10-08 | Oxid. Cat. 3(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 4(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 5(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 6(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 7(Catalytic Converter): | Alliance Source Testing | 1775 Hp | 0.54 lbs/hr, 0.7 g/hp/hr, 60ppmvd@15%O2 | 1651 Hp or 93% of Max | 0.16 lbs/hr, 0.05 g/hp/hr, 4.1ppmvd@15%O2 | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y
2013 | 230 | 0210012004 | Augusta Compressor Facility- Utica Gas Services, L.L.C. | 8034 Bane Rd NE | East Twp. | 44427 |  | Carroll | P007 | 1,775-hp Caterpillar G3606 Compressor Engine w/ Oxidation Catalyst | 2013-10-08 | Oxid. Cat. 3(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 4(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 5(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 6(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 7(Catalytic Converter): | Alliance Source Testing | 1775 Hp | 0.54 lbs/hr, 0.7 g/hp/hr, 60ppmvd@15%O2 | 1624 Hp or 91% of Max | 0.23 lbs/hr, 0.06 g/hp/hr, 5.7ppmvd@15%O2 | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y
2013 | 233 | 0210012004 | Augusta Compressor Facility- Utica Gas Services, L.L.C. | 8034 Bane Rd NE | East Twp. | 44427 |  | Carroll | P008 | 1,775-hp Caterpillar G3606 Compressor Engine w/ Oxidation Catalyst | 2013-10-08 | Oxid. Cat. 3(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 4(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 5(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 6(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 7(Catalytic Converter): | Alliance Source Testing | 1775 Hp | 0.54 lbs/hr, 0.7 g/hp/hr, 60ppmvd@15%O2 | 1610 Hp or 91% of Max | 0.21 lbs/hr, 0.1 g/hp/hr, 5.3ppmvd@15%O2 | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y
2013 | 235 | 0210012004 | Augusta Compressor Facility- Utica Gas Services, L.L.C. | 8034 Bane Rd NE | East Twp. | 44427 |  | Carroll | P009 | 1,775-hp Caterpillar G3606 Compressor Engine w/ Oxidation Catalyst | 2013-10-08 | Oxid. Cat. 3(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 4(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 5(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 6(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 7(Catalytic Converter): | Alliance Source Testing | 1775 Hp | 0.54 lbs/hr, 0.7 g/hp/hr, 60ppmvd@15%O2 | 1724 Hp or 97% of Max | 0.24 lbs/hr, 0.1 g/hp/hr, 5.9ppmvd@15%O2 | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y
2013 | 238 | 0210012004 | Augusta Compressor Facility- Utica Gas Services, L.L.C. | 8034 Bane Rd NE | East Twp. | 44427 |  | Carroll | P010 | 1,775-hp Caterpillar G3606 Compressor Engine w/ Oxidation Catalyst | 2013-10-08 | Oxid. Cat. 3(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 4(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 5(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 6(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 7(Catalytic Converter): | Alliance Source Testing | 1775 Hp | 0.54 lbs/hr, 0.7 g/hp/hr, 60ppmvd@15%O2 | 1621 Hp or 91% of Max | 0.24 lbs/hr, 0.1 g/hp/hr, 6.2ppmvd@15%O2 | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y
2013 | 240 | 0210012004 | Augusta Compressor Facility- Utica Gas Services, L.L.C. | 8034 Bane Rd NE | East Twp. | 44427 |  | Carroll | P011 | 1,775-hp Caterpillar G3606 Compressor Engine w/ Oxidation Catalyst | 2013-10-08 | Oxid. Cat. 3(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 4(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 5(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 6(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 7(Catalytic Converter): | Alliance Source Testing | 1775 Hp | 0.54 lbs/hr, 0.7 g/hp/hr, 60ppmvd@15%O2 | 1632 Hp or 92% of Max | 0.14 lbs/hr, 0.04 g/hp/hr, 3.5ppmvd@15%O2 | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y
2013 | 243 | 0210012004 | Augusta Compressor Facility- Utica Gas Services, L.L.C. | 8034 Bane Rd NE | East Twp. | 44427 |  | Carroll | P009 | 1,775-hp Caterpillar G3606 Compressor Engine w/ Oxidation Catalyst | 2013-10-09 | Oxid. Cat. 3(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 4(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 5(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 6(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 7(Catalytic Converter): | Alliance Source Testing | 1775 Hp | 0.54 lbs/hr, 0.7 g/hp/hr, 60ppmvd@15%O2 | 1724 Hp or 97% of Max | 0.24 lbs/hr, 0.1 g/hp/hr, 5.9ppmvd@15%O2 | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y
2013 | 277 | 0210012004 | Augusta Compressor Facility- Utica Gas Services, L.L.C. | 8034 Bane Rd NE | East Twp. | 44427 |  | Carroll | P010 | 1,775-hp Caterpillar G3606 Compressor Engine w/ Oxidation Catalyst | 2013-10-09 | Oxid. Cat. 3(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 4(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 5(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 6(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 7(Catalytic Converter): | Alliance Source Testing | 1775 Hp | 0.54 lbs/hr, 0.7 g/hp/hr, 60ppmvd@15%O2 | 1621 Hp or 91% of Max | 0.24 lbs/hr, 0.1 g/hp/hr, 6.2ppmvd@15%O2 | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y
2013 | 280 | 0210012004 | Augusta Compressor Facility- Utica Gas Services, L.L.C. | 8034 Bane Rd NE | East Twp. | 44427 |  | Carroll | P011 | 1,775-hp Caterpillar G3606 Compressor Engine w/ Oxidation Catalyst | 2013-10-09 | Oxid. Cat. 3(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 4(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 5(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 6(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 7(Catalytic Converter): | Alliance Source Testing | 1775 Hp | 0.54 lbs/hr, 0.7 g/hp/hr, 60ppmvd@15%O2 | 1632 Hp or 92% of Max | 0.14 lbs/hr, 0.04 g/hp/hr, 3.5ppmvd@15%O2 | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y
2013 | 285 | 0210012004 | Augusta Compressor Facility- Utica Gas Services, L.L.C. | 8034 Bane Rd NE | East Twp. | 44427 |  | Carroll | P012 | 1,775-hp Caterpillar G3606 Compressor Engine w/ Oxidation Catalyst | 2013-10-09 | Oxid. Cat. 3(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 4(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 5(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 6(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 7(Catalytic Converter): | Alliance Source Testing | 1775 Hp | 0.54 lbs/hr, 0.7 g/hp/hr, 60ppmvd@15%O2 | 1703 Hp or 96% of Max | 0.17 lbs/hr, 0.05 g/hp/hr, 4.2ppmvd@15%O2 | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y
2013 | 287 | 0210012004 | Augusta Compressor Facility- Utica Gas Services, L.L.C. | 8034 Bane Rd NE | East Twp. | 44427 |  | Carroll | P013 | 1,775-hp Caterpillar G3606 Compressor Engine w/ Oxidation Catalyst | 2013-10-09 | Oxid. Cat. 3(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 4(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 5(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 6(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 7(Catalytic Converter): | Alliance Source Testing | 1775 Hp | 0.54 lbs/hr, 0.7 g/hp/hr, 60ppmvd@15%O2 | 1680 Hp or 95% of Max | 0.13 lbs/hr, 0.04 g/hp/hr, 3.2ppmvd@15%O2 | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y
2013 | 295 | 0210012004 | Augusta Compressor Facility- Utica Gas Services, L.L.C. | 8034 Bane Rd NE | East Twp. | 44427 |  | Carroll | P006 | 1,775-hp Caterpillar G3606 Compressor Engine w/ Oxidation Catalyst | 2013-10-10 | Oxid. Cat. 3(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 4(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 5(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 6(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 7(Catalytic Converter): | Alliance Source Testing | 1775 Hp | 0.54 lbs/hr, 0.7 g/hp/hr, 60ppmvd@15%O2 | 1651 Hp or 93% of Max | 0.16 lbs/hr, 0.05 g/hp/hr, 4.1ppmvd@15%O2 | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y
2013 | 299 | 0210012004 | Augusta Compressor Facility- Utica Gas Services, L.L.C. | 8034 Bane Rd NE | East Twp. | 44427 |  | Carroll | P007 | 1,775-hp Caterpillar G3606 Compressor Engine w/ Oxidation Catalyst | 2013-10-10 | Oxid. Cat. 3(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 4(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 5(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 6(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 7(Catalytic Converter): | Alliance Source Testing | 1775 Hp | 0.54 lbs/hr, 0.7 g/hp/hr, 60ppmvd@15%O2 | 1624 Hp or 91% of Max | 0.23 lbs/hr, 0.06 g/hp/hr, 5.7ppmvd@15%O2 | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y
2013 | 303 | 0210012004 | Augusta Compressor Facility- Utica Gas Services, L.L.C. | 8034 Bane Rd NE | East Twp. | 44427 |  | Carroll | P008 | 1,775-hp Caterpillar G3606 Compressor Engine w/ Oxidation Catalyst | 2013-10-10 | Oxid. Cat. 3(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 4(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 5(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 6(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 7(Catalytic Converter): | Alliance Source Testing | 1775 Hp | 0.54 lbs/hr, 0.7 g/hp/hr, 60ppmvd@15%O2 | 1610 Hp or 91% of Max | 0.21 lbs/hr, 0.1 g/hp/hr, 5.3ppmvd@15%O2 | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y
2013 | 306 | 0210012004 | Augusta Compressor Facility- Utica Gas Services, L.L.C. | 8034 Bane Rd NE | East Twp. | 44427 |  | Carroll | P009 | 1,775-hp Caterpillar G3606 Compressor Engine w/ Oxidation Catalyst | 2013-10-10 | Oxid. Cat. 3(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 4(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 5(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 6(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 7(Catalytic Converter): | Alliance Source Testing | 1775 Hp | 0.54 lbs/hr, 0.7 g/hp/hr, 60ppmvd@15%O2 | 1724 Hp or 97% of Max | 0.24 lbs/hr, 0.1 g/hp/hr, 5.9ppmvd@15%O2 | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y
2013 | 308 | 0210012004 | Augusta Compressor Facility- Utica Gas Services, L.L.C. | 8034 Bane Rd NE | East Twp. | 44427 |  | Carroll | P010 | 1,775-hp Caterpillar G3606 Compressor Engine w/ Oxidation Catalyst | 2013-10-10 | Oxid. Cat. 3(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 4(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 5(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 6(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 7(Catalytic Converter): | Alliance Source Testing | 1775 Hp | 0.54 lbs/hr, 0.7 g/hp/hr, 60ppmvd@15%O2 | 1621 Hp or 91% of Max | 0.24 lbs/hr, 0.1 g/hp/hr, 6.2ppmvd@15%O2 | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y
2013 | 311 | 0210012004 | Augusta Compressor Facility- Utica Gas Services, L.L.C. | 8034 Bane Rd NE | East Twp. | 44427 |  | Carroll | P011 | 1,775-hp Caterpillar G3606 Compressor Engine w/ Oxidation Catalyst | 2013-10-10 | Oxid. Cat. 3(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 4(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 5(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 6(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 7(Catalytic Converter): | Alliance Source Testing | 1775 Hp | 0.54 lbs/hr, 0.7 g/hp/hr, 60ppmvd@15%O2 | 1632 Hp or 92% of Max | 0.14 lbs/hr, 0.04 g/hp/hr, 3.5ppmvd@15%O2 | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y
2013 | 314 | 0210012004 | Augusta Compressor Facility- Utica Gas Services, L.L.C. | 8034 Bane Rd NE | East Twp. | 44427 |  | Carroll | P012 | 1,775-hp Caterpillar G3606 Compressor Engine w/ Oxidation Catalyst | 2013-10-10 | Oxid. Cat. 3(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 4(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 5(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 6(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 7(Catalytic Converter): | Alliance Source Testing | 1775 Hp | 0.54 lbs/hr, 0.7 g/hp/hr, 60ppmvd@15%O2 | 1703 Hp or 96% of Max | 0.17 lbs/hr, 0.05 g/hp/hr, 4.2ppmvd@15%O2 | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y
2013 | 318 | 0210012004 | Augusta Compressor Facility- Utica Gas Services, L.L.C. | 8034 Bane Rd NE | East Twp. | 44427 |  | Carroll | P013 | 1,775-hp Caterpillar G3606 Compressor Engine w/ Oxidation Catalyst | 2013-10-10 | Oxid. Cat. 3(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 4(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 5(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 6(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 7(Catalytic Converter): | Alliance Source Testing | 1775 Hp | 0.54 lbs/hr, 0.7 g/hp/hr, 60ppmvd@15%O2 | 1680 Hp or 95% of Max | 0.13 lbs/hr, 0.04 g/hp/hr, 3.2ppmvd@15%O2 | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y
2013 | 330 | 0210012008 | Chesapeake Exploration LLC - Mangun 22-15-5 Pad | Lustre Rd NE | Carrollton | 44607 |  | Carroll | P002 | 145 hp Spark Ignition Internal Combustion Engine | 2013-03-06 | Catalyst | Alliance Source Testing | 145 HP | 60 ppmvd @ 15% O2 | 130 HP | 2.9 ppmvd @ 15% O2 | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y
2013 | 338 | 0210012020 | Chesapeake Exploration LLC - Rutledge 10-14-6 Pad | Canyon Rd SW | Carrollton | 44615 |  | Carroll | P002 | Natural Gas Engines | 2013-05-22 | Catalyst | Alliance Source Testing, Inc. | 215 hp | 2.9 lb/hr and 1.0 g-hp/hr | 194 =90% | 0.1 lb/hr and 0.1 g-hp/hr | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y
2013 | 345 | 0210012024 | Chesapeake Exploration LLC - Brunk 32-13-5 Pad | Pinto Rd SE | Carrollton | 44615 |  | Carroll | P002 | Natural Gas Engines | 2013-08-09 | N/A | Alliance Source Testing | 215 bhp | 60 ppmvd@15%O2 | 91% or 196 bhp | 16.8 ppmvd@15%O2 | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y | Caterpillar 215 hp Natural Gas engine serial# 4FD04197
2013 | 346 | 0210012025 | Chesapeake Exploration LLC - Davis Farms 2-14-6 Pad | Pillar Rd SW | Carrollton | 44615 |  | Carroll | P002 | Natural Gas Engines | 2013-08-08 | N/A | Alliance Source Testing, Inc. | 215 bhp | 60 ppmvd@15%O2 | 91% or 197 bhp | 8.6 ppmvd@15%O2 | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y | Caterpillar 215 hp Natural Gas Engine serial# 4FD04263
2013 | 670 | 0285000366 | East Ohio Gas - Chippewa Station | 17045 Galehouse Road | Doylestown | 44230 |  | Wayne | B010 | 2,370 hp 4SLB SI ICE; CAT G3608 | 2013-06-11 | Engine 5 Converter(Catalytic Converter): Engine #5; Cat B010(Catalytic Converter): Catalytic Converter for B010, engine #6 | Environmental Quality Management, Inc. | 2370 Hp | 86 ppmvd@15%O2 or 1.0 g/hp-hr | 98% of max | 23.0 ppmvd@15%O2 and 0.122 gram/hp-hr | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y
2013 | 683 | 0285012009 | Aspire Energy of Ohio LLC - AEO-C06 | County Rd 40 | Penn Twp. | 43758 |  | Morgan | P001 | Portable 276 bhp (@1,800 RPM), 2.05 MMBtu/hr Caterpillar Model G3406 TA, 4-stroke rich burn (4SRB), spark ignition (SI), natural gas-fired internal combustion engine, driving a pump or compressor, manufactured April 2012 and installed in October 2012. | 2013-10-10 | Converter(Catalytic Converter): Catalytic Converter | Custom Stack Analysis, LLC. | 276 hp | 0.7 g/hp-hr 60 ppm @ 15% O2 | 179 hp | 0.144 g/hp-hr 10.25 ppm @ 15% O2 | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y | Averages: 37.491 ppm 0.4005 lbs/hr carbon 10.25 ppm @ 15% O2 0.144 g/hp-hr
2013 | 1050 | 0607015001 | Tri-County Compressor Station (MarkWest / Ohio Oil Gath | North of intersection of Hwy 379 and Town | Barnesville | 43713 |  | Belmont | P004 | Compressor Engine #4 - 1980 HP (15.43 MMBtu/hr) Waukesha P9390 - natural gas-fired four-stroke rich burn internal combustion engine equipped with a three-way oxidation catalyst controlling CH2O, CO, NOx, & VOCs by 80, 97, 98.5 & 66 percent respectively | 2013-11-15 | CC002(Catalytic Converter): Compressor Engine #2 - 3-way Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - 3-way Catalyst; CC004(Catalytic Converter): Compressor Engine #4 - 3-way Catalyst; CC005(Catalytic Converter): Compressor Engine #5 - 3-w | Air Hygiene International | 1980 Hp | 60 ppm | 1881 Hp | 0.73 ppm | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y | testing November 15th and 16th, 2013
2013 | 1051 | 0607015001 | Tri-County Compressor Station (MarkWest / Ohio Oil Gath | North of intersection of Hwy 379 and Town | Barnesville | 43713 |  | Belmont | P005 | Compressor Engine #5 - 1980 HP (15.43 MMBtu/hr) Waukesha P9390 - natural gas-fired four-stroke rich burn internal combustion engine equipped with a three-way oxidation catalyst controlling CH2O, CO, NOx, & VOCs by 80, 97, 98.5 & 66 percent respectively | 2013-11-15 | CC002(Catalytic Converter): Compressor Engine #2 - 3-way Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - 3-way Catalyst; CC004(Catalytic Converter): Compressor Engine #4 - 3-way Catalyst; CC005(Catalytic Converter): Compressor Engine #5 - 3-w | Air Hygiene International | 1980 Hp | 60 ppm | 1881 Hp | 1.24 ppm | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y | testing November 15th and 16th, 2013
2013 | 1075 | 0679000330 | East Ohio Gas Jefferson Compressor Sta. | 4378 Williams Lake Rd SW | New Philadelphia | 44663 |  | Tuscarawas | P001 | 1340 HP 4 stroke lean burn natural gas fired reciprocating engine with catalytic oxidation | 2013-09-25 | S001(Catalytic Converter): Catalytic Converter for P001 | Environmental Quality Management, Inc. | 1340 | 1.0 g/HP-hr; 86 ppmvd @ 15% O2 | 1134 | 0.012 g/HP-hr; 6.5 ppmvd @ 15% O2 | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y | PTIO P0110413 and NSPS JJJJ testing requirements.
2013 | 1152 | 0607015001 | Tri-County Compressor Station (MarkWest / Ohio Oil Gath | North of intersection of Hwy 379 and Town | Barnesville | 43713 |  | Belmont | P003 | Compressor Engine #3 - 1980 HP (15.43 MMBtu/hr) Waukesha P9390 - natural gas-fired four-stroke rich burn internal combustion engine equipped with a three-way oxidation catalyst controlling CH2O, CO, NOx, & VOCs by 80, 97, 98.5 & 66 percent respectively | 2013-11-15 | CC002(Catalytic Converter): Compressor Engine #2 - 3-way Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - 3-way Catalyst; CC004(Catalytic Converter): Compressor Engine #4 - 3-way Catalyst; CC005(Catalytic Converter): Compressor Engine #5 - 3-w | Air Hygiene International | 1980 Hp | 60 ppm | 1861 Hp | 1.0 ppm | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y | testing November 15th and 16th, 2013
2013 | 1155 | 0607015001 | Tri-County Compressor Station (MarkWest / Ohio Oil Gath | North of intersection of Hwy 379 and Town | Barnesville | 43713 |  | Belmont | P006 | Compressor Engine #6 - 1980 HP (15.43 MMBtu/hr) Waukesha P9390 - natural gas-fired four-stroke rich burn internal combustion engine equipped with a three-way oxidation catalyst controlling CH2O, CO, NOx, & VOCs by 80, 97, 98.5 & 66 percent respectively | 2013-11-15 | CC002(Catalytic Converter): Compressor Engine #2 - 3-way Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - 3-way Catalyst; CC004(Catalytic Converter): Compressor Engine #4 - 3-way Catalyst; CC005(Catalytic Converter): Compressor Engine #5 - 3-w | Air Hygiene International | 1980 Hp | 60 ppm | 1881 Hp | 1.0 ppm | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y | testing November 15th and 16th, 2013
2013 | 1176 | 0634005029 | Cadiz Gas Plant | 43071 Industrial Park Rd | Cadiz | 43907 |  | Harrison | P007 | Compressor Engine #7 - 4735 HP Caterpillar G3616 engine (CM-1206-7) - natural gas-fired four-stroke lean burn internal combustion engine equipped with an oxidation catalyst controlling CO, VOC and formaldehyde 95, 75, and 90 percent respectively. | 2013-11-14 | CC007(Catalytic Converter): oxidation catalyst | Air Hygiene International | 4,735 | 60.0 ppm | 4,715 hp | 2.8 ppm | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y
2013 | 1180 | 0634005029 | Cadiz Gas Plant | 43071 Industrial Park Rd | Cadiz | 43907 |  | Harrison | P008 | Compressor Engine #8 - 4735 HP Caterpillar G3616 engine (CM-1206-8) - natural gas-fired four-stroke lean burn internal combustion engine equipped with an oxidation catalyst controlling CO, VOC and formaldehyde 95, 75, and 90 percent respectively. | 2013-11-14 | CC008(Catalytic Converter): oxidation catalyst | Air Hygiene International | 4,735 hp | 60.0 ppm | 4,725 hp | 3.5 ppm | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y
2013 | 1182 | 0634005035 | Chesapeake Exploration LLC- Henderson South 10-12-6 Pad | Township Highway 225 | Scio | 43988 |  | Harrison | P002 | Flash Gas Compressor equipped with catalyst, 145 hp, Cat G3306 NA (Spark Ignition Internal Combustion Engine, P002) Flash Gas Compressor equipped with catalyst, 211 hp, CAT G3306 TA (Spark Ignition Internal Combustion Engine, P002) | 2013-08-23 | none | Alliance Source Testing | 211 Hp | 60 ppm | 185 Hp | 4.4 ppm | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y
2013 | 1190 | 0634005040 | Archer Compressor Facility | County Highway 45 | Cadiz | 43907 |  | Harrison | P002 | Compressor Engine #2 - 1775 HP Caterpillar G3606 (4S-LB) - natural gas-fired four-cycle lean burn internal combustion engine rated equipped with an oxidation catalyst controlling CO and VOC emissions. | 2013-12-12 | OxidCat-102(Catalytic Converter): Oxidative Catalyst; OxidCat-102(Catalytic Converter): Oxidative Catalyst | Alliance Source Testing, LLC | 1775 HP | 0.88 lb/hr | 1621 | 0.47 lb/hr | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y | PTIO P0113393 and NSPS JJJJ testing requirements.
2013 | 1195 | 0634005040 | Archer Compressor Facility | County Highway 45 | Cadiz | 43907 |  | Harrison | P003 | Compressor Engine #3 - 1775 HP Caterpillar G3606 (4S-LB) - natural gas-fired four-cycle lean burn internal combustion engine rated equipped with an oxidation catalyst controlling CO and VOC emissions. | 2013-12-12 | OxidCat-102(Catalytic Converter): Oxidative Catalyst; OxidCat-102(Catalytic Converter): Oxidative Catalyst | Alliance Source Testing, LLC | 1775 HP | 0.88 lb/hr | 1598 | 0.32 lb/hr | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y | PTIO P0113393 and NSPS JJJJ testing requirements.
2013 | 1198 | 0634005040 | Archer Compressor Facility | County Highway 45 | Cadiz | 43907 |  | Harrison | P004 | Compressor Engine #4 - 1775 HP Caterpillar G3606 (4S-LB) - natural gas-fired four-cycle lean burn internal combustion engine rated equipped with an oxidation catalyst controlling CO and VOC emissions. | 2013-12-12 | OxidCat-102(Catalytic Converter): Oxidative Catalyst; OxidCat-102(Catalytic Converter): Oxidative Catalyst | Alliance Source Testing, LLC | 1775 HP | 0.88 lb/hr | 1609 | 0.40 lb/hr | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y | PTIO P0113393 and NSPS JJJJ testing requirements.
2013 | 1201 | 0634005040 | Archer Compressor Facility | County Highway 45 | Cadiz | 43907 |  | Harrison | P005 | Compressor Engine #5 - 1775 HP Caterpillar G3606 (4S-LB) - natural gas-fired four-cycle lean burn internal combustion engine rated equipped with an oxidation catalyst controlling CO and VOC emissions. | 2013-12-12 | OxidCat-102(Catalytic Converter): Oxidative Catalyst; OxidCat-102(Catalytic Converter): Oxidative Catalyst | Alliance Source Testing, LLC | 1775 HP | 0.88 lb/hr | 1615 | 0.35 lb/hr | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y | PTIO P0113393 and NSPS JJJJ testing requirements.
2013 | 1202 | 0634005040 | Archer Compressor Facility | County Highway 45 | Cadiz | 43907 |  | Harrison | P001 | Compressor Engine #1 - 1775 HP Caterpillar G3606 (4S-LB) - natural gas-fired four-cycle lean burn internal combustion engine rated equipped with an oxidation catalyst controlling CO and VOC emissions. | 2013-12-13 | OxidCat-101(Catalytic Converter): Oxidative Catalyst | Alliance Source Testing, LLC | 1775 HP | 0.88 lb/hr | 1632 HP | 0.47 lb/hr | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y | PTIO P0113393 and NSPS JJJJ testing requirements.
2013 | 1240 | 0656035002 | Statoil - Eisenbarth Pad | 42240 Long Ridge Road | Clarington | 43931 |  | Monroe | P002 | (1) - 860 Hp, 6.5 mmBTU/hr, 4 stroke, lean burn, catalytic oxidation, Caterpillar G 3512 LE natural gas-fired internal combustion engine. | 2013-04-11 | Oxidative catalyst | Air Hygiene international, Inc. | 860 | 1.0 g/hp-hr 86 ppmvd @ 15% O2 | 860 | 0.06 g/hp-hr 5.52 ppmvd @ 15% O2 | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y
2013 | 1249 | 0661005002 | Summerfield Compressor Station | between CR-45 and HWY 233 | Caldwell | 43724 |  | Noble | P001 | Natural Gas Engine(1) 1,380 hp engine | 2013-03-12 | Catalyst 1(Catalytic Converter): Oxidation Catalyst 1 | BCMJ Controls | 1380 Hp | 0.7 g/Hp-hr | 1178 Hp | 0.07 g/Hp-hr | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y
2013 | 1252 | 0661005002 | Summerfield Compressor Station | between CR-45 and HWY 233 | Caldwell | 43724 |  | Noble | P002 | Natural Gas Engine (2) 1,380 hp | 2013-03-12 | Catalyst 1(Catalytic Converter): Oxidation Catalyst 1 | BCMJ Controls | 1380 Hp | 0.7 g/Hp-hr | 1178 Hp | 0.13 g/Hp-hr | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y
2013 | 1371 | 0857751312 | Clean Water Ltd. | 300 Cherokee Drive | Dayton | 45417 |  | Montgomery | P042 | Centrifuge 2 with fixed roof vented through closed-vent system to a demister followed by a RTO control device equipped with a VOC entrapment chamber at the outlet of the RTO. | 2013-11-25 | RTO(Thermal Incinerator): Regenerative Thermal Oxidizer | Industrial Air Science | see memo | 95%DE | see memo | 96%DE | 25A | Total Hydrocarbons | PASS | NA | Y | This test was designed to determine the destruction efficiency of the common control (regenerative thermal oxidizer) tied to the closed vent system for overall control. A new closed vent system pressure drop was established at -0.70" during this compliance test. In addition, a new RTO operating temperature of 1555 degrees Fahrenheit was established. All major aspects of the facility appeared to be operating at representative conditions. Specifically, the G-cones were holding or receiving waste water throughout the test. The VDR was fed in the first run while the blower operated throughout runs 2 and 3. The SBR blowers operated throughout the test. Three centrifuges operated in the first test run. The DAF processed waste water during 2 test runs. Dryer fuel was loaded during 2 test runs and the decanter operated in the initial run. Drums were not bulked during the compliance test as that was accomplished the week before the test. Samples were collected and analyzed for methane with the intent of subtraction from the total hydrocarbons. The result of the methane analysis indicated methane as a minor contributor to the exhaust VOC loading during this compliance test. Additionally, a test was run on 11/21/2014 but not used for compliance. That data is available in an additional test detail file.
2013 | 1372 | 0857751312 | Clean Water Ltd. | 300 Cherokee Drive | Dayton | 45417 |  | Montgomery | P043 | Centrifuge 3 with fixed roof vented through closed-vent system to a demister followed by a RTO control device equipped with a VOC entrapment chamber at the outlet of the RTO. | 2013-11-25 | RTO(Thermal Incinerator): Regenerative Thermal Oxidizer | Industrial Air Science | see memo | 95%DE | see memo | 96%DE | 25A | Total Hydrocarbons | PASS | NA | Y | This test was designed to determine the destruction efficiency of the common control (regenerative thermal oxidizer) tied to the closed vent system for overall control. A new closed vent system pressure drop was established at -0.70" during this compliance test. In addition, a new RTO operating temperature of 1555 degrees Fahrenheit was established. All major aspects of the facility appeared to be operating at representative conditions. Specifically, the G-cones were holding or receiving waste water throughout the test. The VDR was fed in the first run while the blower operated throughout runs 2 and 3. The SBR blowers operated throughout the test. Three centrifuges operated in the first test run. The DAF processed waste water during 2 test runs. Dryer fuel was loaded during 2 test runs and the decanter operated in the initial run. Drums were not bulked during the compliance test as that was accomplished the week before the test. Samples were collected and analyzed for methane with the intent of subtraction from the total hydrocarbons. The result of the methane analysis indicated methane as a minor contributor to the exhaust VOC loading during this compliance test. Additionally, a test was run on 11/21/2014 but not used for compliance. That data is available in an additional test detail file.
2013 | 1373 | 0857751312 | Clean Water Ltd. | 300 Cherokee Drive | Dayton | 45417 |  | Montgomery | P045 | Decanter Centrifuge vented through closed-vent system to a demister followed by a RTO control device equipped with a VOC entrapment chamber at the outlet of the RTO | 2013-11-25 | RTO(Thermal Incinerator): Regenerative Thermal Oxidizer | Industrial Air Science | see memo | 95%DE | see memo | 96%DE | 25A | Total Hydrocarbons | PASS | NA | Y | This test was designed to determine the destruction efficiency of the common control (regenerative thermal oxidizer) tied to the closed vent system for overall control. A new closed vent system pressure drop was established at -0.70" during this compliance test. In addition, a new RTO operating temperature of 1555 degrees Fahrenheit was established. All major aspects of the facility appeared to be operating at representative conditions. Specifically, the G-cones were holding or receiving waste water throughout the test. The VDR was fed in the first run while the blower operated throughout runs 2 and 3. The SBR blowers operated throughout the test. Three centrifuges operated in the first test run. The DAF processed waste water during 2 test runs. Dryer fuel was loaded during 2 test runs and the decanter operated in the initial run. Drums were not bulked during the compliance test as that was accomplished the week before the test. Samples were collected and analyzed for methane with the intent of subtraction from the total hydrocarbons. The result of the methane analysis indicated methane as a minor contributor to the exhaust VOC loading during this compliance test. Additionally, a test was run on 11/21/2014 but not used for compliance. That data is available in an additional test detail file.
2014 | 182 | 0210002039 | Kilgore Compressor Station-Utica Gas Services, LLC | Pontiff Rd | Kilgore | 43988 |  | Carroll | P009 | 1,775 hp NG-fired 4SLB Stationary ICE equipped w/catalyst Caterpillar G3606: Serial Number: 4ZS01776 | 2014-01-14 | CC001(Catalytic Converter): Compressor Engine #1 - Oxidation Catalyst; CC002(Catalytic Converter): Compressor Engine #2 - Oxidation Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - Oxidation Catalyst; CC004(Catalytic Converter): Compressor Eng | Alliance Source Testing, Inc. | 1775 | NSPS 0.7g/Hp-hr & 60ppm @ 15% O2, TV .71lb/hr | 1722 | NSPS 0.1g/Hp-hr & 12.3ppm @ 15% O2, TV .53lb/hr | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y | The report was accepted as verification of compliance by the OEPA. However a few instances onsite were witnessed and variances were allowed to the testers for only accepting two runs as verification of compliance for P005 (NOx) and P009 (CO). Many issues could be attributed to the cold weather, however are preventable, and all efforts to prevent these issues from happening in the future will, and have been, taken into account for future test acceptance.
2014 | 186 | 0210002039 | Kilgore Compressor Station-Utica Gas Services, LLC | Pontiff Rd | Kilgore | 43988 |  | Carroll | P010 | 1,775 hp NG-fired 4SLB Stationary ICE equipped w/catalyst Caterpillar G3606: Serial Number: 4ZS01814 | 2014-01-14 | CC001(Catalytic Converter): Compressor Engine #1 - Oxidation Catalyst; CC002(Catalytic Converter): Compressor Engine #2 - Oxidation Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - Oxidation Catalyst; CC004(Catalytic Converter): Compressor Eng | Alliance Source Testing, Inc. | 1775 | NSPS 0.7g/Hp-hr & 60ppm @ 15% O2, TV .71lb/hr | 1663 | NSPS 0.2g/Hp-hr & 15.6ppm @ 15% O2, TV ..66lb/hr | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y | The report was accepted as verification of compliance by the OEPA. However a few instances onsite were witnessed and variances were allowed to the testers for only accepting two runs as verification of compliance for P005 (NOx) and P009 (CO). Many issues could be attributed to the cold weather, however are preventable, and all efforts to prevent these issues from happening in the future will, and have been, taken into account for future test acceptance.
2014 | 188 | 0210012004 | Augusta Compressor Facility- Utica Gas Services, L.L.C. | 8034 Bane Rd NE | East Twp. | 44427 |  | Carroll | P013 | 1,775-hp Caterpillar G3606 Compressor Engine w/ Oxidation Catalyst | 2014-09-17 | Oxid. Cat. 3(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 4(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 5(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 6(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 7(Catalytic Converter): | Great Plains Analytical Services | 1775 Hp | 0.54 lbs/hr, 0.7 g/hp/hr, 60ppmvd@15%O2 | 1780 | 0.47 lbs/hr, 0.12g/hp/hr, 11.59ppmvd@15%O2 | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y
2014 | 193 | 0210012004 | Augusta Compressor Facility- Utica Gas Services, L.L.C. | 8034 Bane Rd NE | East Twp. | 44427 |  | Carroll | P006 | 1,775-hp Caterpillar G3606 Compressor Engine w/ Oxidation Catalyst | 2014-09-18 | Oxid. Cat. 3(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 4(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 5(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 6(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 7(Catalytic Converter): | Great Plains Analytical Services | 1775 Hp | 0.54 lbs/hr, 0.7 g/hp/hr, 60ppmvd@15%O2 | 1831 | 0.36 lbs/hr, 0.09 g/hp/hr, 8.91 ppmvd@15%O2 | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y
2014 | 195 | 0210012004 | Augusta Compressor Facility- Utica Gas Services, L.L.C. | 8034 Bane Rd NE | East Twp. | 44427 |  | Carroll | P007 | 1,775-hp Caterpillar G3606 Compressor Engine w/ Oxidation Catalyst | 2014-09-18 | Oxid. Cat. 3(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 4(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 5(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 6(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 7(Catalytic Converter): | Great Plains Analytical Services | 1775 Hp | 0.54 lbs/hr, 0.7 g/hp/hr, 60ppmvd@15%O2 | 1839 | 0.34 lbs/hr, 0.08 g/hp/hr, 8.16 ppmvd@15%O2 | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y
2014 | 197 | 0210012004 | Augusta Compressor Facility- Utica Gas Services, L.L.C. | 8034 Bane Rd NE | East Twp. | 44427 |  | Carroll | P008 | 1,775-hp Caterpillar G3606 Compressor Engine w/ Oxidation Catalyst | 2014-09-18 | Oxid. Cat. 3(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 4(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 5(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 6(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 7(Catalytic Converter): | Great Plains Analytical Services | 1775 Hp | 0.54 lbs/hr, 0.7 g/hp/hr, 60ppmvd@15%O2 | 1809 | 0.27 lbs/hr, 0.06 g/hp/hr, 6.8 ppmvd@15%O2 | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y
2014 | 225 | 0210002026 | Chesapeake Exploration LLC - Gartrell 23-13-6 Pad | Ohio 164 | Orange Twp. | 44695 |  | Carroll | P002 | 215 hp CAT G3406NA natural gas engine flash gas compressor equipped with catalyst. | 2014-04-08 | Catalyst | Alliance Source Testing | 211 HP | 60ppmvd@15%O2 | 175 HP or 83% of Max | 2.7 ppmvd@15%O2 | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y | If engine exceeds 10% of the tested rate the engine will require a retest.
2014 | 226 | 0210002029 | Chesapeake Exploration LLC - Colescott 11-12-5 Pad | Branch Rd | Kilgore | 44615 |  | Carroll | P002 | 215 hp CAT G3406NA flash gas compressor using natural gas engines and equipped with a catalyst. | 2014-04-08 | Catalyst | Alliance Source Testing | 211 Hp | 60 ppmvd@15% O2 | 165 HP or 78% of Max | 0.30 ppmvd @15% O2 | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y | Engine will have to retest if the engine exceed 10% operation of the tested rate.
2014 | 235 | 0210002039 | Kilgore Compressor Station-Utica Gas Services, LLC | Pontiff Rd | Kilgore | 43988 |  | Carroll | P001 | 1,775 hp NG-fired 4SLB Stationary ICE equipped w/catalyst Caterpillar G3606 Serial Number: 4ZS01713 | 2014-01-14 | CC001(Catalytic Converter): Compressor Engine #1 - Oxidation Catalyst; CC002(Catalytic Converter): Compressor Engine #2 - Oxidation Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - Oxidation Catalyst; CC004(Catalytic Converter): Compressor Eng | Alliance Source Testing, Inc. | 1775 | NSPS 0.7g/Hp-hr & 60ppm @ 15% O2, TV .71lb/hr | 1722 | NSPS 0.2g/Hp-hr & 13.3ppm @ 15% O2, TV .58lb/hr | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y | The report was accepted as verification of compliance by the OEPA. However a few instances onsite were witnessed and variances were allowed to the testers for only accepting two runs as verification of compliance for P005 (NOx) and P009 (CO). Many issues could be attributed to the cold weather, however are preventable, and all efforts to prevent these issues from happening in the future will, and have been, taken into account for future test acceptance.
2014 | 240 | 0210002039 | Kilgore Compressor Station-Utica Gas Services, LLC | Pontiff Rd | Kilgore | 43988 |  | Carroll | P002 | 1,775 hp NG-fired 4SLB Stationary ICE equipped w/catalyst Caterpillar G3606: Serial Number: 4ZS01796 | 2014-01-14 | CC001(Catalytic Converter): Compressor Engine #1 - Oxidation Catalyst; CC002(Catalytic Converter): Compressor Engine #2 - Oxidation Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - Oxidation Catalyst; CC004(Catalytic Converter): Compressor Eng | Alliance Source Testing, Inc. | 1775 | NSPS 0.7g/Hp-hr & 60ppm @ 15% O2, TV .71lb/hr | 1698 | NSPS 0.1g/Hp-hr & 12.4ppm @ 15% O2, TV .53lb/hr | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y | The report was accepted as verification of compliance by the OEPA. However a few instances onsite were witnessed and variances were allowed to the testers for only accepting two runs as verification of compliance for P005 (NOx) and P009 (CO). Many issues could be attributed to the cold weather, however are preventable, and all efforts to prevent these issues from happening in the future will, and have been, taken into account for future test acceptance.
2014 | 242 | 0210002039 | Kilgore Compressor Station-Utica Gas Services, LLC | Pontiff Rd | Kilgore | 43988 |  | Carroll | P003 | 1,775 hp NG-fired 4SLB Stationary ICE equipped w/catalyst Caterpillar G3606: Serial Number: 4ZS01797 | 2014-01-14 | CC001(Catalytic Converter): Compressor Engine #1 - Oxidation Catalyst; CC002(Catalytic Converter): Compressor Engine #2 - Oxidation Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - Oxidation Catalyst; CC004(Catalytic Converter): Compressor Eng | Alliance Source Testing, Inc. | 1775 | NSPS 0.7g/Hp-hr & 60ppm @ 15% O2, TV .71lb/hr | 1669 | NSPS 0.1g/Hp-hr & 11.6ppm @ 15% O2, TV .49lb/hr | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y | The report was accepted as verification of compliance by the OEPA. However a few instances onsite were witnessed and variances were allowed to the testers for only accepting two runs as verification of compliance for P005 (NOx) and P009 (CO). Many issues could be attributed to the cold weather, however are preventable, and all efforts to prevent these issues from happening in the future will, and have been, taken into account for future test acceptance.
2014 | 244 | 0210002039 | Kilgore Compressor Station-Utica Gas Services, LLC | Pontiff Rd | Kilgore | 43988 |  | Carroll | P004 | 1,775 hp NG-fired 4SLB Stationary ICE equipped w/catalyst Caterpillar G3606: Serial Number: 4ZS01800 | 2014-01-14 | CC001(Catalytic Converter): Compressor Engine #1 - Oxidation Catalyst; CC002(Catalytic Converter): Compressor Engine #2 - Oxidation Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - Oxidation Catalyst; CC004(Catalytic Converter): Compressor Eng | Alliance Source Testing, Inc. | 1775 | NSPS 0.7g/Hp-hr & 60ppm @ 15% O2, TV .71lb/hr | 1698 | NSPS 0.2g/Hp-hr & 12.8ppm @ 15% O2, TV .56lb/hr | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y | The report was accepted as verification of compliance by the OEPA. However a few instances onsite were witnessed and variances were allowed to the testers for only accepting two runs as verification of compliance for P005 (NOx) and P009 (CO). Many issues could be attributed to the cold weather, however are preventable, and all efforts to prevent these issues from happening in the future will, and have been, taken into account for future test acceptance.
2014 | 247 | 0210002039 | Kilgore Compressor Station-Utica Gas Services, LLC | Pontiff Rd | Kilgore | 43988 |  | Carroll | P005 | 1,775 hp NG-fired 4SLB Stationary ICE equipped w/catalyst Caterpillar G3606: Serial Number: 4ZS01804 | 2014-01-14 | CC001(Catalytic Converter): Compressor Engine #1 - Oxidation Catalyst; CC002(Catalytic Converter): Compressor Engine #2 - Oxidation Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - Oxidation Catalyst; CC004(Catalytic Converter): Compressor Eng | Alliance Source Testing, Inc. | 1775 | NSPS 0.7g/Hp-hr & 60ppm @ 15% O2, TV .71lb/hr | 1698 | NSPS 0.2g/Hp-hr & 13.3ppm @ 15% O2, TV .56lb/hr | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y | The report was accepted as verification of compliance by the OEPA. However a few instances onsite were witnessed and variances were allowed to the testers for only accepting two runs as verification of compliance for P005 (NOx) and P009 (CO). Many issues could be attributed to the cold weather, however are preventable, and all efforts to prevent these issues from happening in the future will, and have been, taken into account for future test acceptance.
2014 | 252 | 0210002039 | Kilgore Compressor Station-Utica Gas Services, LLC | Pontiff Rd | Kilgore | 43988 |  | Carroll | P006 | 1,775 hp NG-fired 4SLB Stationary ICE equipped w/catalyst Caterpillar G3606: Serial Number: 4ZS01805 | 2014-01-14 | CC001(Catalytic Converter): Compressor Engine #1 - Oxidation Catalyst; CC002(Catalytic Converter): Compressor Engine #2 - Oxidation Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - Oxidation Catalyst; CC004(Catalytic Converter): Compressor Eng | Alliance Source Testing, Inc. | 1775 | NSPS 0.7g/Hp-hr & 60ppm @ 15% O2, TV .71lb/hr | 1698 | NSPS 0.1g/Hp-hr & 12ppm @ 15% O2, TV .52lb/hr | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y | The report was accepted as verification of compliance by the OEPA. However a few instances onsite were witnessed and variances were allowed to the testers for only accepting two runs as verification of compliance for P005 (NOx) and P009 (CO). Many issues could be attributed to the cold weather, however are preventable, and all efforts to prevent these issues from happening in the future will, and have been, taken into account for future test acceptance.
2014 | 253 | 0210002039 | Kilgore Compressor Station-Utica Gas Services, LLC | Pontiff Rd | Kilgore | 43988 |  | Carroll | P007 | 1,775 hp NG-fired 4SLB Stationary ICE equipped w/catalyst Caterpillar G3606: Serial Number: 4ZS01807 | 2014-01-14 | CC001(Catalytic Converter): Compressor Engine #1 - Oxidation Catalyst; CC002(Catalytic Converter): Compressor Engine #2 - Oxidation Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - Oxidation Catalyst; CC004(Catalytic Converter): Compressor Eng | Alliance Source Testing, Inc. | 1775 | NSPS 0.7g/Hp-hr & 60ppm @ 15% O2, TV .71lb/hr | 1716 | NSPS 0.1g/Hp-hr &11.0ppm @ 15% O2, TV .48lb/hr | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y | The report was accepted as verification of compliance by the OEPA. However a few instances onsite were witnessed and variances were allowed to the testers for only accepting two runs as verification of compliance for P005 (NOx) and P009 (CO). Many issues could be attributed to the cold weather, however are preventable, and all efforts to prevent these issues from happening in the future will, and have been, taken into account for future test acceptance.
2014 | 258 | 0210002039 | Kilgore Compressor Station-Utica Gas Services, LLC | Pontiff Rd | Kilgore | 43988 |  | Carroll | P008 | 1,775 hp NG-fired 4SLB Stationary ICE equipped w/catalyst Caterpillar G3606: Serial Number: 4ZS01808 | 2014-01-14 | CC001(Catalytic Converter): Compressor Engine #1 - Oxidation Catalyst; CC002(Catalytic Converter): Compressor Engine #2 - Oxidation Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - Oxidation Catalyst; CC004(Catalytic Converter): Compressor Eng | Alliance Source Testing, Inc. | 1775 | NSPS 0.7g/Hp-hr & 60ppm @ 15% O2, TV .71lb/hr | 1769 | NSPS 0.2g/Hp-hr & 13.9ppm @ 15% O2, TV .6lb/hr | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y | The report was accepted as verification of compliance by the OEPA. However a few instances onsite were witnessed and variances were allowed to the testers for only accepting two runs as verification of compliance for P005 (NOx) and P009 (CO). Many issues could be attributed to the cold weather, however are preventable, and all efforts to prevent these issues from happening in the future will, and have been, taken into account for future test acceptance.
2014 | 270 | 0210002039 | Kilgore Compressor Station-Utica Gas Services, LLC | Pontiff Rd | Kilgore | 43988 |  | Carroll | P001 | 1,775 hp NG-fired 4SLB Stationary ICE equipped w/catalyst Caterpillar G3606 Serial Number: 4ZS01713 | 2014-01-15 | CC001(Catalytic Converter): Compressor Engine #1 - Oxidation Catalyst; CC002(Catalytic Converter): Compressor Engine #2 - Oxidation Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - Oxidation Catalyst; CC004(Catalytic Converter): Compressor Eng | Alliance Source Testing, Inc. | 1775 | NSPS 0.7g/Hp-hr & 60ppm @ 15% O2, TV .71lb/hr | 1722 | NSPS 0.2g/Hp-hr & 13.3ppm @ 15% O2, TV .58lb/hr | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y | The report was accepted as verification of compliance by the OEPA. However a few instances onsite were witnessed and variances were allowed to the testers for only accepting two runs as verification of compliance for P005 (NOx) and P009 (CO). Many issues could be attributed to the cold weather, however are preventable, and all efforts to prevent these issues from happening in the future will, and have been, taken into account for future test acceptance.
2014 | 272 | 0210002039 | Kilgore Compressor Station-Utica Gas Services, LLC | Pontiff Rd | Kilgore | 43988 |  | Carroll | P002 | 1,775 hp NG-fired 4SLB Stationary ICE equipped w/catalyst Caterpillar G3606: Serial Number: 4ZS01796 | 2014-01-15 | CC001(Catalytic Converter): Compressor Engine #1 - Oxidation Catalyst; CC002(Catalytic Converter): Compressor Engine #2 - Oxidation Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - Oxidation Catalyst; CC004(Catalytic Converter): Compressor Eng | Alliance Source Testing, Inc. | 1775 | NSPS 0.7g/Hp-hr & 60ppm @ 15% O2, TV .71lb/hr | 1698 | NSPS 0.1g/Hp-hr & 12.4ppm @ 15% O2, TV .53lb/hr | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y | The report was accepted as verification of compliance by the OEPA. However a few instances onsite were witnessed and variances were allowed to the testers for only accepting two runs as verification of compliance for P005 (NOx) and P009 (CO). Many issues could be attributed to the cold weather, however are preventable, and all efforts to prevent these issues from happening in the future will, and have been, taken into account for future test acceptance.
2014 | 274 | 0210002039 | Kilgore Compressor Station-Utica Gas Services, LLC | Pontiff Rd | Kilgore | 43988 |  | Carroll | P003 | 1,775 hp NG-fired 4SLB Stationary ICE equipped w/catalyst Caterpillar G3606: Serial Number: 4ZS01797 | 2014-01-15 | CC001(Catalytic Converter): Compressor Engine #1 - Oxidation Catalyst; CC002(Catalytic Converter): Compressor Engine #2 - Oxidation Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - Oxidation Catalyst; CC004(Catalytic Converter): Compressor Eng | Alliance Source Testing, Inc. | 1775 | NSPS 0.7g/Hp-hr & 60ppm @ 15% O2, TV .71lb/hr | 1669 | NSPS 0.1g/Hp-hr & 11.6ppm @ 15% O2, TV .49lb/hr | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y | The report was accepted as verification of compliance by the OEPA. However a few instances onsite were witnessed and variances were allowed to the testers for only accepting two runs as verification of compliance for P005 (NOx) and P009 (CO). Many issues could be attributed to the cold weather, however are preventable, and all efforts to prevent these issues from happening in the future will, and have been, taken into account for future test acceptance.
2014 | 277 | 0210002039 | Kilgore Compressor Station-Utica Gas Services, LLC | Pontiff Rd | Kilgore | 43988 |  | Carroll | P004 | 1,775 hp NG-fired 4SLB Stationary ICE equipped w/catalyst Caterpillar G3606: Serial Number: 4ZS01800 | 2014-01-15 | CC001(Catalytic Converter): Compressor Engine #1 - Oxidation Catalyst; CC002(Catalytic Converter): Compressor Engine #2 - Oxidation Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - Oxidation Catalyst; CC004(Catalytic Converter): Compressor Eng | Alliance Source Testing, Inc. | 1775 | NSPS 0.7g/Hp-hr & 60ppm @ 15% O2, TV .71lb/hr | 1698 | NSPS 0.2g/Hp-hr & 12.8ppm @ 15% O2, TV .56lb/hr | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y | The report was accepted as verification of compliance by the OEPA. However a few instances onsite were witnessed and variances were allowed to the testers for only accepting two runs as verification of compliance for P005 (NOx) and P009 (CO). Many issues could be attributed to the cold weather, however are preventable, and all efforts to prevent these issues from happening in the future will, and have been, taken into account for future test acceptance.
2014 | 281 | 0210002039 | Kilgore Compressor Station-Utica Gas Services, LLC | Pontiff Rd | Kilgore | 43988 |  | Carroll | P005 | 1,775 hp NG-fired 4SLB Stationary ICE equipped w/catalyst Caterpillar G3606: Serial Number: 4ZS01804 | 2014-01-15 | CC001(Catalytic Converter): Compressor Engine #1 - Oxidation Catalyst; CC002(Catalytic Converter): Compressor Engine #2 - Oxidation Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - Oxidation Catalyst; CC004(Catalytic Converter): Compressor Eng | Alliance Source Testing, Inc. | 1775 | NSPS 0.7g/Hp-hr & 60ppm @ 15% O2, TV .71lb/hr | 1698 | NSPS 0.2g/Hp-hr & 13.3ppm @ 15% O2, TV .56lb/hr | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y | The report was accepted as verification of compliance by the OEPA. However a few instances onsite were witnessed and variances were allowed to the testers for only accepting two runs as verification of compliance for P005 (NOx) and P009 (CO). Many issues could be attributed to the cold weather, however are preventable, and all efforts to prevent these issues from happening in the future will, and have been, taken into account for future test acceptance.
2014 | 283 | 0210002039 | Kilgore Compressor Station-Utica Gas Services, LLC | Pontiff Rd | Kilgore | 43988 |  | Carroll | P006 | 1,775 hp NG-fired 4SLB Stationary ICE equipped w/catalyst Caterpillar G3606: Serial Number: 4ZS01805 | 2014-01-15 | CC001(Catalytic Converter): Compressor Engine #1 - Oxidation Catalyst; CC002(Catalytic Converter): Compressor Engine #2 - Oxidation Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - Oxidation Catalyst; CC004(Catalytic Converter): Compressor Eng | Alliance Source Testing, Inc. | 1775 | NSPS 0.7g/Hp-hr & 60ppm @ 15% O2, TV .71lb/hr | 1698 | NSPS 0.1g/Hp-hr & 12ppm @ 15% O2, TV .52lb/hr | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y | The report was accepted as verification of compliance by the OEPA. However a few instances onsite were witnessed and variances were allowed to the testers for only accepting two runs as verification of compliance for P005 (NOx) and P009 (CO). Many issues could be attributed to the cold weather, however are preventable, and all efforts to prevent these issues from happening in the future will, and have been, taken into account for future test acceptance.
2014 | 286 | 0210002039 | Kilgore Compressor Station-Utica Gas Services, LLC | Pontiff Rd | Kilgore | 43988 |  | Carroll | P007 | 1,775 hp NG-fired 4SLB Stationary ICE equipped w/catalyst Caterpillar G3606: Serial Number: 4ZS01807 | 2014-01-15 | CC001(Catalytic Converter): Compressor Engine #1 - Oxidation Catalyst; CC002(Catalytic Converter): Compressor Engine #2 - Oxidation Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - Oxidation Catalyst; CC004(Catalytic Converter): Compressor Eng | Alliance Source Testing, Inc. | 1775 | NSPS 0.7g/Hp-hr & 60ppm @ 15% O2, TV .71lb/hr | 1716 | NSPS 0.1g/Hp-hr &11.0ppm @ 15% O2, TV .48lb/hr | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y | The report was accepted as verification of compliance by the OEPA. However a few instances onsite were witnessed and variances were allowed to the testers for only accepting two runs as verification of compliance for P005 (NOx) and P009 (CO). Many issues could be attributed to the cold weather, however are preventable, and all efforts to prevent these issues from happening in the future will, and have been, taken into account for future test acceptance.
2014 | 289 | 0210002039 | Kilgore Compressor Station-Utica Gas Services, LLC | Pontiff Rd | Kilgore | 43988 |  | Carroll | P008 | 1,775 hp NG-fired 4SLB Stationary ICE equipped w/catalyst Caterpillar G3606: Serial Number: 4ZS01808 | 2014-01-15 | CC001(Catalytic Converter): Compressor Engine #1 - Oxidation Catalyst; CC002(Catalytic Converter): Compressor Engine #2 - Oxidation Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - Oxidation Catalyst; CC004(Catalytic Converter): Compressor Eng | Alliance Source Testing, Inc. | 1775 | NSPS 0.7g/Hp-hr & 60ppm @ 15% O2, TV .71lb/hr | 1769 | NSPS 0.2g/Hp-hr & 13.9ppm @ 15% O2, TV .6lb/hr | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y | The report was accepted as verification of compliance by the OEPA. However a few instances onsite were witnessed and variances were allowed to the testers for only accepting two runs as verification of compliance for P005 (NOx) and P009 (CO). Many issues could be attributed to the cold weather, however are preventable, and all efforts to prevent these issues from happening in the future will, and have been, taken into account for future test acceptance.
2014 | 293 | 0210002039 | Kilgore Compressor Station-Utica Gas Services, LLC | Pontiff Rd | Kilgore | 43988 |  | Carroll | P009 | 1,775 hp NG-fired 4SLB Stationary ICE equipped w/catalyst Caterpillar G3606: Serial Number: 4ZS01776 | 2014-01-15 | CC001(Catalytic Converter): Compressor Engine #1 - Oxidation Catalyst; CC002(Catalytic Converter): Compressor Engine #2 - Oxidation Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - Oxidation Catalyst; CC004(Catalytic Converter): Compressor Eng | Alliance Source Testing, Inc. | 1775 | NSPS 0.7g/Hp-hr & 60ppm @ 15% O2, TV .71lb/hr | 1722 | NSPS 0.1g/Hp-hr & 12.3ppm @ 15% O2, TV .53lb/hr | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y | The report was accepted as verification of compliance by the OEPA. However a few instances onsite were witnessed and variances were allowed to the testers for only accepting two runs as verification of compliance for P005 (NOx) and P009 (CO). Many issues could be attributed to the cold weather, however are preventable, and all efforts to prevent these issues from happening in the future will, and have been, taken into account for future test acceptance.
2014 | 295 | 0210002039 | Kilgore Compressor Station-Utica Gas Services, LLC | Pontiff Rd | Kilgore | 43988 |  | Carroll | P010 | 1,775 hp NG-fired 4SLB Stationary ICE equipped w/catalyst Caterpillar G3606: Serial Number: 4ZS01814 | 2014-01-15 | CC001(Catalytic Converter): Compressor Engine #1 - Oxidation Catalyst; CC002(Catalytic Converter): Compressor Engine #2 - Oxidation Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - Oxidation Catalyst; CC004(Catalytic Converter): Compressor Eng | Alliance Source Testing, Inc. | 1775 | NSPS 0.7g/Hp-hr & 60ppm @ 15% O2, TV .71lb/hr | 1663 | NSPS 0.2g/Hp-hr & 15.6ppm @ 15% O2, TV ..66lb/hr | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y | The report was accepted as verification of compliance by the OEPA. However a few instances onsite were witnessed and variances were allowed to the testers for only accepting two runs as verification of compliance for P005 (NOx) and P009 (CO). Many issues could be attributed to the cold weather, however are preventable, and all efforts to prevent these issues from happening in the future will, and have been, taken into account for future test acceptance.
2014 | 307 | 0210002039 | Kilgore Compressor Station-Utica Gas Services, LLC | Pontiff Rd | Kilgore | 43988 |  | Carroll | P001 | 1,775 hp NG-fired 4SLB Stationary ICE equipped w/catalyst Caterpillar G3606 Serial Number: 4ZS01713 | 2014-01-16 | CC001(Catalytic Converter): Compressor Engine #1 - Oxidation Catalyst; CC002(Catalytic Converter): Compressor Engine #2 - Oxidation Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - Oxidation Catalyst; CC004(Catalytic Converter): Compressor Eng | Alliance Source Testing, Inc. | 1775 | NSPS 0.7g/Hp-hr & 60ppm @ 15% O2, TV .71lb/hr | 1722 | NSPS 0.2g/Hp-hr & 13.3ppm @ 15% O2, TV .58lb/hr | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y | The report was accepted as verification of compliance by the OEPA. However a few instances onsite were witnessed and variances were allowed to the testers for only accepting two runs as verification of compliance for P005 (NOx) and P009 (CO). Many issues could be attributed to the cold weather, however are preventable, and all efforts to prevent these issues from happening in the future will, and have been, taken into account for future test acceptance.
2014 | 310 | 0210002039 | Kilgore Compressor Station-Utica Gas Services, LLC | Pontiff Rd | Kilgore | 43988 |  | Carroll | P002 | 1,775 hp NG-fired 4SLB Stationary ICE equipped w/catalyst Caterpillar G3606: Serial Number: 4ZS01796 | 2014-01-16 | CC001(Catalytic Converter): Compressor Engine #1 - Oxidation Catalyst; CC002(Catalytic Converter): Compressor Engine #2 - Oxidation Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - Oxidation Catalyst; CC004(Catalytic Converter): Compressor Eng | Alliance Source Testing, Inc. | 1775 | NSPS 0.7g/Hp-hr & 60ppm @ 15% O2, TV .71lb/hr | 1698 | NSPS 0.1g/Hp-hr & 12.4ppm @ 15% O2, TV .53lb/hr | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y | The report was accepted as verification of compliance by the OEPA. However a few instances onsite were witnessed and variances were allowed to the testers for only accepting two runs as verification of compliance for P005 (NOx) and P009 (CO). Many issues could be attributed to the cold weather, however are preventable, and all efforts to prevent these issues from happening in the future will, and have been, taken into account for future test acceptance.
2014 | 315 | 0210002039 | Kilgore Compressor Station-Utica Gas Services, LLC | Pontiff Rd | Kilgore | 43988 |  | Carroll | P003 | 1,775 hp NG-fired 4SLB Stationary ICE equipped w/catalyst Caterpillar G3606: Serial Number: 4ZS01797 | 2014-01-16 | CC001(Catalytic Converter): Compressor Engine #1 - Oxidation Catalyst; CC002(Catalytic Converter): Compressor Engine #2 - Oxidation Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - Oxidation Catalyst; CC004(Catalytic Converter): Compressor Eng | Alliance Source Testing, Inc. | 1775 | NSPS 0.7g/Hp-hr & 60ppm @ 15% O2, TV .71lb/hr | 1669 | NSPS 0.1g/Hp-hr & 11.6ppm @ 15% O2, TV .49lb/hr | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y | The report was accepted as verification of compliance by the OEPA. However a few instances onsite were witnessed and variances were allowed to the testers for only accepting two runs as verification of compliance for P005 (NOx) and P009 (CO). Many issues could be attributed to the cold weather, however are preventable, and all efforts to prevent these issues from happening in the future will, and have been, taken into account for future test acceptance.
2014 | 318 | 0210002039 | Kilgore Compressor Station-Utica Gas Services, LLC | Pontiff Rd | Kilgore | 43988 |  | Carroll | P004 | 1,775 hp NG-fired 4SLB Stationary ICE equipped w/catalyst Caterpillar G3606: Serial Number: 4ZS01800 | 2014-01-16 | CC001(Catalytic Converter): Compressor Engine #1 - Oxidation Catalyst; CC002(Catalytic Converter): Compressor Engine #2 - Oxidation Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - Oxidation Catalyst; CC004(Catalytic Converter): Compressor Eng | Alliance Source Testing, Inc. | 1775 | NSPS 0.7g/Hp-hr & 60ppm @ 15% O2, TV .71lb/hr | 1698 | NSPS 0.2g/Hp-hr & 12.8ppm @ 15% O2, TV .56lb/hr | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y | The report was accepted as verification of compliance by the OEPA. However a few instances onsite were witnessed and variances were allowed to the testers for only accepting two runs as verification of compliance for P005 (NOx) and P009 (CO). Many issues could be attributed to the cold weather, however are preventable, and all efforts to prevent these issues from happening in the future will, and have been, taken into account for future test acceptance.
2014 | 319 | 0210002039 | Kilgore Compressor Station-Utica Gas Services, LLC | Pontiff Rd | Kilgore | 43988 |  | Carroll | P005 | 1,775 hp NG-fired 4SLB Stationary ICE equipped w/catalyst Caterpillar G3606: Serial Number: 4ZS01804 | 2014-01-16 | CC001(Catalytic Converter): Compressor Engine #1 - Oxidation Catalyst; CC002(Catalytic Converter): Compressor Engine #2 - Oxidation Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - Oxidation Catalyst; CC004(Catalytic Converter): Compressor Eng | Alliance Source Testing, Inc. | 1775 | NSPS 0.7g/Hp-hr & 60ppm @ 15% O2, TV .71lb/hr | 1698 | NSPS 0.2g/Hp-hr & 13.3ppm @ 15% O2, TV .56lb/hr | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y | The report was accepted as verification of compliance by the OEPA. However a few instances onsite were witnessed and variances were allowed to the testers for only accepting two runs as verification of compliance for P005 (NOx) and P009 (CO). Many issues could be attributed to the cold weather, however are preventable, and all efforts to prevent these issues from happening in the future will, and have been, taken into account for future test acceptance.
2014 | 322 | 0210002039 | Kilgore Compressor Station-Utica Gas Services, LLC | Pontiff Rd | Kilgore | 43988 |  | Carroll | P006 | 1,775 hp NG-fired 4SLB Stationary ICE equipped w/catalyst Caterpillar G3606: Serial Number: 4ZS01805 | 2014-01-16 | CC001(Catalytic Converter): Compressor Engine #1 - Oxidation Catalyst; CC002(Catalytic Converter): Compressor Engine #2 - Oxidation Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - Oxidation Catalyst; CC004(Catalytic Converter): Compressor Eng | Alliance Source Testing, Inc. | 1775 | NSPS 0.7g/Hp-hr & 60ppm @ 15% O2, TV .71lb/hr | 1698 | NSPS 0.1g/Hp-hr & 12ppm @ 15% O2, TV .52lb/hr | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y | The report was accepted as verification of compliance by the OEPA. However a few instances onsite were witnessed and variances were allowed to the testers for only accepting two runs as verification of compliance for P005 (NOx) and P009 (CO). Many issues could be attributed to the cold weather, however are preventable, and all efforts to prevent these issues from happening in the future will, and have been, taken into account for future test acceptance.
2014 | 326 | 0210002039 | Kilgore Compressor Station-Utica Gas Services, LLC | Pontiff Rd | Kilgore | 43988 |  | Carroll | P007 | 1,775 hp NG-fired 4SLB Stationary ICE equipped w/catalyst Caterpillar G3606: Serial Number: 4ZS01807 | 2014-01-16 | CC001(Catalytic Converter): Compressor Engine #1 - Oxidation Catalyst; CC002(Catalytic Converter): Compressor Engine #2 - Oxidation Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - Oxidation Catalyst; CC004(Catalytic Converter): Compressor Eng | Alliance Source Testing, Inc. | 1775 | NSPS 0.7g/Hp-hr & 60ppm @ 15% O2, TV .71lb/hr | 1716 | NSPS 0.1g/Hp-hr &11.0ppm @ 15% O2, TV .48lb/hr | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y | The report was accepted as verification of compliance by the OEPA. However a few instances onsite were witnessed and variances were allowed to the testers for only accepting two runs as verification of compliance for P005 (NOx) and P009 (CO). Many issues could be attributed to the cold weather, however are preventable, and all efforts to prevent these issues from happening in the future will, and have been, taken into account for future test acceptance.
2014 | 330 | 0210002039 | Kilgore Compressor Station-Utica Gas Services, LLC | Pontiff Rd | Kilgore | 43988 |  | Carroll | P008 | 1,775 hp NG-fired 4SLB Stationary ICE equipped w/catalyst Caterpillar G3606: Serial Number: 4ZS01808 | 2014-01-16 | CC001(Catalytic Converter): Compressor Engine #1 - Oxidation Catalyst; CC002(Catalytic Converter): Compressor Engine #2 - Oxidation Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - Oxidation Catalyst; CC004(Catalytic Converter): Compressor Eng | Alliance Source Testing, Inc. | 1775 | NSPS 0.7g/Hp-hr & 60ppm @ 15% O2, TV .71lb/hr | 1769 | NSPS 0.2g/Hp-hr & 13.9ppm @ 15% O2, TV .6lb/hr | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y | The report was accepted as verification of compliance by the OEPA. However a few instances onsite were witnessed and variances were allowed to the testers for only accepting two runs as verification of compliance for P005 (NOx) and P009 (CO). Many issues could be attributed to the cold weather, however are preventable, and all efforts to prevent these issues from happening in the future will, and have been, taken into account for future test acceptance.
2014 | 331 | 0210002039 | Kilgore Compressor Station-Utica Gas Services, LLC | Pontiff Rd | Kilgore | 43988 |  | Carroll | P009 | 1,775 hp NG-fired 4SLB Stationary ICE equipped w/catalyst Caterpillar G3606: Serial Number: 4ZS01776 | 2014-01-16 | CC001(Catalytic Converter): Compressor Engine #1 - Oxidation Catalyst; CC002(Catalytic Converter): Compressor Engine #2 - Oxidation Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - Oxidation Catalyst; CC004(Catalytic Converter): Compressor Eng | Alliance Source Testing, Inc. | 1775 | NSPS 0.7g/Hp-hr & 60ppm @ 15% O2, TV .71lb/hr | 1722 | NSPS 0.1g/Hp-hr & 12.3ppm @ 15% O2, TV .53lb/hr | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y | The report was accepted as verification of compliance by the OEPA. However a few instances onsite were witnessed and variances were allowed to the testers for only accepting two runs as verification of compliance for P005 (NOx) and P009 (CO). Many issues could be attributed to the cold weather, however are preventable, and all efforts to prevent these issues from happening in the future will, and have been, taken into account for future test acceptance.
2014 | 334 | 0210002039 | Kilgore Compressor Station-Utica Gas Services, LLC | Pontiff Rd | Kilgore | 43988 |  | Carroll | P010 | 1,775 hp NG-fired 4SLB Stationary ICE equipped w/catalyst Caterpillar G3606: Serial Number: 4ZS01814 | 2014-01-16 | CC001(Catalytic Converter): Compressor Engine #1 - Oxidation Catalyst; CC002(Catalytic Converter): Compressor Engine #2 - Oxidation Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - Oxidation Catalyst; CC004(Catalytic Converter): Compressor Eng | Alliance Source Testing, Inc. | 1775 | NSPS 0.7g/Hp-hr & 60ppm @ 15% O2, TV .71lb/hr | 1663 | NSPS 0.2g/Hp-hr & 15.6ppm @ 15% O2, TV ..66lb/hr | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y | The report was accepted as verification of compliance by the OEPA. However a few instances onsite were witnessed and variances were allowed to the testers for only accepting two runs as verification of compliance for P005 (NOx) and P009 (CO). Many issues could be attributed to the cold weather, however are preventable, and all efforts to prevent these issues from happening in the future will, and have been, taken into account for future test acceptance.
2014 | 346 | 0210002039 | Kilgore Compressor Station-Utica Gas Services, LLC | Pontiff Rd | Kilgore | 43988 |  | Carroll | P001 | 1,775 hp NG-fired 4SLB Stationary ICE equipped w/catalyst Caterpillar G3606 Serial Number: 4ZS01713 | 2014-01-17 | CC001(Catalytic Converter): Compressor Engine #1 - Oxidation Catalyst; CC002(Catalytic Converter): Compressor Engine #2 - Oxidation Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - Oxidation Catalyst; CC004(Catalytic Converter): Compressor Eng | Alliance Source Testing, Inc. | 1775 | NSPS 0.7g/Hp-hr & 60ppm @ 15% O2, TV .71lb/hr | 1722 | NSPS 0.2g/Hp-hr & 13.3ppm @ 15% O2, TV .58lb/hr | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y | The report was accepted as verification of compliance by the OEPA. However a few instances onsite were witnessed and variances were allowed to the testers for only accepting two runs as verification of compliance for P005 (NOx) and P009 (CO). Many issues could be attributed to the cold weather, however are preventable, and all efforts to prevent these issues from happening in the future will, and have been, taken into account for future test acceptance.
2014 | 351 | 0210002039 | Kilgore Compressor Station-Utica Gas Services, LLC | Pontiff Rd | Kilgore | 43988 |  | Carroll | P002 | 1,775 hp NG-fired 4SLB Stationary ICE equipped w/catalyst Caterpillar G3606: Serial Number: 4ZS01796 | 2014-01-17 | CC001(Catalytic Converter): Compressor Engine #1 - Oxidation Catalyst; CC002(Catalytic Converter): Compressor Engine #2 - Oxidation Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - Oxidation Catalyst; CC004(Catalytic Converter): Compressor Eng | Alliance Source Testing, Inc. | 1775 | NSPS 0.7g/Hp-hr & 60ppm @ 15% O2, TV .71lb/hr | 1698 | NSPS 0.1g/Hp-hr & 12.4ppm @ 15% O2, TV .53lb/hr | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y | The report was accepted as verification of compliance by the OEPA. However a few instances onsite were witnessed and variances were allowed to the testers for only accepting two runs as verification of compliance for P005 (NOx) and P009 (CO). Many issues could be attributed to the cold weather, however are preventable, and all efforts to prevent these issues from happening in the future will, and have been, taken into account for future test acceptance.
2014 | 354 | 0210002039 | Kilgore Compressor Station-Utica Gas Services, LLC | Pontiff Rd | Kilgore | 43988 |  | Carroll | P003 | 1,775 hp NG-fired 4SLB Stationary ICE equipped w/catalyst Caterpillar G3606: Serial Number: 4ZS01797 | 2014-01-17 | CC001(Catalytic Converter): Compressor Engine #1 - Oxidation Catalyst; CC002(Catalytic Converter): Compressor Engine #2 - Oxidation Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - Oxidation Catalyst; CC004(Catalytic Converter): Compressor Eng | Alliance Source Testing, Inc. | 1775 | NSPS 0.7g/Hp-hr & 60ppm @ 15% O2, TV .71lb/hr | 1669 | NSPS 0.1g/Hp-hr & 11.6ppm @ 15% O2, TV .49lb/hr | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y | The report was accepted as verification of compliance by the OEPA. However a few instances onsite were witnessed and variances were allowed to the testers for only accepting two runs as verification of compliance for P005 (NOx) and P009 (CO). Many issues could be attributed to the cold weather, however are preventable, and all efforts to prevent these issues from happening in the future will, and have been, taken into account for future test acceptance.
2014 | 357 | 0210002039 | Kilgore Compressor Station-Utica Gas Services, LLC | Pontiff Rd | Kilgore | 43988 |  | Carroll | P004 | 1,775 hp NG-fired 4SLB Stationary ICE equipped w/catalyst Caterpillar G3606: Serial Number: 4ZS01800 | 2014-01-17 | CC001(Catalytic Converter): Compressor Engine #1 - Oxidation Catalyst; CC002(Catalytic Converter): Compressor Engine #2 - Oxidation Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - Oxidation Catalyst; CC004(Catalytic Converter): Compressor Eng | Alliance Source Testing, Inc. | 1775 | NSPS 0.7g/Hp-hr & 60ppm @ 15% O2, TV .71lb/hr | 1698 | NSPS 0.2g/Hp-hr & 12.8ppm @ 15% O2, TV .56lb/hr | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y | The report was accepted as verification of compliance by the OEPA. However a few instances onsite were witnessed and variances were allowed to the testers for only accepting two runs as verification of compliance for P005 (NOx) and P009 (CO). Many issues could be attributed to the cold weather, however are preventable, and all efforts to prevent these issues from happening in the future will, and have been, taken into account for future test acceptance.
2014 | 358 | 0210002039 | Kilgore Compressor Station-Utica Gas Services, LLC | Pontiff Rd | Kilgore | 43988 |  | Carroll | P005 | 1,775 hp NG-fired 4SLB Stationary ICE equipped w/catalyst Caterpillar G3606: Serial Number: 4ZS01804 | 2014-01-17 | CC001(Catalytic Converter): Compressor Engine #1 - Oxidation Catalyst; CC002(Catalytic Converter): Compressor Engine #2 - Oxidation Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - Oxidation Catalyst; CC004(Catalytic Converter): Compressor Eng | Alliance Source Testing, Inc. | 1775 | NSPS 0.7g/Hp-hr & 60ppm @ 15% O2, TV .71lb/hr | 1698 | NSPS 0.2g/Hp-hr & 13.3ppm @ 15% O2, TV .56lb/hr | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y | The report was accepted as verification of compliance by the OEPA. However a few instances onsite were witnessed and variances were allowed to the testers for only accepting two runs as verification of compliance for P005 (NOx) and P009 (CO). Many issues could be attributed to the cold weather, however are preventable, and all efforts to prevent these issues from happening in the future will, and have been, taken into account for future test acceptance.
2014 | 362 | 0210002039 | Kilgore Compressor Station-Utica Gas Services, LLC | Pontiff Rd | Kilgore | 43988 |  | Carroll | P006 | 1,775 hp NG-fired 4SLB Stationary ICE equipped w/catalyst Caterpillar G3606: Serial Number: 4ZS01805 | 2014-01-17 | CC001(Catalytic Converter): Compressor Engine #1 - Oxidation Catalyst; CC002(Catalytic Converter): Compressor Engine #2 - Oxidation Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - Oxidation Catalyst; CC004(Catalytic Converter): Compressor Eng | Alliance Source Testing, Inc. | 1775 | NSPS 0.7g/Hp-hr & 60ppm @ 15% O2, TV .71lb/hr | 1698 | NSPS 0.1g/Hp-hr & 12ppm @ 15% O2, TV .52lb/hr | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y | The report was accepted as verification of compliance by the OEPA. However a few instances onsite were witnessed and variances were allowed to the testers for only accepting two runs as verification of compliance for P005 (NOx) and P009 (CO). Many issues could be attributed to the cold weather, however are preventable, and all efforts to prevent these issues from happening in the future will, and have been, taken into account for future test acceptance.
2014 | 365 | 0210002039 | Kilgore Compressor Station-Utica Gas Services, LLC | Pontiff Rd | Kilgore | 43988 |  | Carroll | P007 | 1,775 hp NG-fired 4SLB Stationary ICE equipped w/catalyst Caterpillar G3606: Serial Number: 4ZS01807 | 2014-01-17 | CC001(Catalytic Converter): Compressor Engine #1 - Oxidation Catalyst; CC002(Catalytic Converter): Compressor Engine #2 - Oxidation Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - Oxidation Catalyst; CC004(Catalytic Converter): Compressor Eng | Alliance Source Testing, Inc. | 1775 | NSPS 0.7g/Hp-hr & 60ppm @ 15% O2, TV .71lb/hr | 1716 | NSPS 0.1g/Hp-hr &11.0ppm @ 15% O2, TV .48lb/hr | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y | The report was accepted as verification of compliance by the OEPA. However a few instances onsite were witnessed and variances were allowed to the testers for only accepting two runs as verification of compliance for P005 (NOx) and P009 (CO). Many issues could be attributed to the cold weather, however are preventable, and all efforts to prevent these issues from happening in the future will, and have been, taken into account for future test acceptance.
2014 | 369 | 0210002039 | Kilgore Compressor Station-Utica Gas Services, LLC | Pontiff Rd | Kilgore | 43988 |  | Carroll | P008 | 1,775 hp NG-fired 4SLB Stationary ICE equipped w/catalyst Caterpillar G3606: Serial Number: 4ZS01808 | 2014-01-17 | CC001(Catalytic Converter): Compressor Engine #1 - Oxidation Catalyst; CC002(Catalytic Converter): Compressor Engine #2 - Oxidation Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - Oxidation Catalyst; CC004(Catalytic Converter): Compressor Eng | Alliance Source Testing, Inc. | 1775 | NSPS 0.7g/Hp-hr & 60ppm @ 15% O2, TV .71lb/hr | 1769 | NSPS 0.2g/Hp-hr & 13.9ppm @ 15% O2, TV .6lb/hr | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y | The report was accepted as verification of compliance by the OEPA. However a few instances onsite were witnessed and variances were allowed to the testers for only accepting two runs as verification of compliance for P005 (NOx) and P009 (CO). Many issues could be attributed to the cold weather, however are preventable, and all efforts to prevent these issues from happening in the future will, and have been, taken into account for future test acceptance.
2014 | 370 | 0210002039 | Kilgore Compressor Station-Utica Gas Services, LLC | Pontiff Rd | Kilgore | 43988 |  | Carroll | P009 | 1,775 hp NG-fired 4SLB Stationary ICE equipped w/catalyst Caterpillar G3606: Serial Number: 4ZS01776 | 2014-01-17 | CC001(Catalytic Converter): Compressor Engine #1 - Oxidation Catalyst; CC002(Catalytic Converter): Compressor Engine #2 - Oxidation Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - Oxidation Catalyst; CC004(Catalytic Converter): Compressor Eng | Alliance Source Testing, Inc. | 1775 | NSPS 0.7g/Hp-hr & 60ppm @ 15% O2, TV .71lb/hr | 1722 | NSPS 0.1g/Hp-hr & 12.3ppm @ 15% O2, TV .53lb/hr | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y | The report was accepted as verification of compliance by the OEPA. However a few instances onsite were witnessed and variances were allowed to the testers for only accepting two runs as verification of compliance for P005 (NOx) and P009 (CO). Many issues could be attributed to the cold weather, however are preventable, and all efforts to prevent these issues from happening in the future will, and have been, taken into account for future test acceptance.
2014 | 373 | 0210002039 | Kilgore Compressor Station-Utica Gas Services, LLC | Pontiff Rd | Kilgore | 43988 |  | Carroll | P010 | 1,775 hp NG-fired 4SLB Stationary ICE equipped w/catalyst Caterpillar G3606: Serial Number: 4ZS01814 | 2014-01-17 | CC001(Catalytic Converter): Compressor Engine #1 - Oxidation Catalyst; CC002(Catalytic Converter): Compressor Engine #2 - Oxidation Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - Oxidation Catalyst; CC004(Catalytic Converter): Compressor Eng | Alliance Source Testing, Inc. | 1775 | NSPS 0.7g/Hp-hr & 60ppm @ 15% O2, TV .71lb/hr | 1663 | NSPS 0.2g/Hp-hr & 15.6ppm @ 15% O2, TV ..66lb/hr | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y | The report was accepted as verification of compliance by the OEPA. However a few instances onsite were witnessed and variances were allowed to the testers for only accepting two runs as verification of compliance for P005 (NOx) and P009 (CO). Many issues could be attributed to the cold weather, however are preventable, and all efforts to prevent these issues from happening in the future will, and have been, taken into account for future test acceptance.
2014 | 387 | 0210002039 | Kilgore Compressor Station-Utica Gas Services, LLC | Pontiff Rd | Kilgore | 43988 |  | Carroll | P001 | 1,775 hp NG-fired 4SLB Stationary ICE equipped w/catalyst Caterpillar G3606 Serial Number: 4ZS01713 | 2014-01-18 | CC001(Catalytic Converter): Compressor Engine #1 - Oxidation Catalyst; CC002(Catalytic Converter): Compressor Engine #2 - Oxidation Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - Oxidation Catalyst; CC004(Catalytic Converter): Compressor Eng | Alliance Source Testing, Inc. | 1775 | NSPS 0.7g/Hp-hr & 60ppm @ 15% O2, TV .71lb/hr | 1722 | NSPS 0.2g/Hp-hr & 13.3ppm @ 15% O2, TV .58lb/hr | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y | The report was accepted as verification of compliance by the OEPA. However a few instances onsite were witnessed and variances were allowed to the testers for only accepting two runs as verification of compliance for P005 (NOx) and P009 (CO). Many issues could be attributed to the cold weather, however are preventable, and all efforts to prevent these issues from happening in the future will, and have been, taken into account for future test acceptance.
2014 | 390 | 0210002039 | Kilgore Compressor Station-Utica Gas Services, LLC | Pontiff Rd | Kilgore | 43988 |  | Carroll | P002 | 1,775 hp NG-fired 4SLB Stationary ICE equipped w/catalyst Caterpillar G3606: Serial Number: 4ZS01796 | 2014-01-18 | CC001(Catalytic Converter): Compressor Engine #1 - Oxidation Catalyst; CC002(Catalytic Converter): Compressor Engine #2 - Oxidation Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - Oxidation Catalyst; CC004(Catalytic Converter): Compressor Eng | Alliance Source Testing, Inc. | 1775 | NSPS 0.7g/Hp-hr & 60ppm @ 15% O2, TV .71lb/hr | 1698 | NSPS 0.1g/Hp-hr & 12.4ppm @ 15% O2, TV .53lb/hr | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y | The report was accepted as verification of compliance by the OEPA. However a few instances onsite were witnessed and variances were allowed to the testers for only accepting two runs as verification of compliance for P005 (NOx) and P009 (CO). Many issues could be attributed to the cold weather, however are preventable, and all efforts to prevent these issues from happening in the future will, and have been, taken into account for future test acceptance.
2014 | 392 | 0210002039 | Kilgore Compressor Station-Utica Gas Services, LLC | Pontiff Rd | Kilgore | 43988 |  | Carroll | P003 | 1,775 hp NG-fired 4SLB Stationary ICE equipped w/catalyst Caterpillar G3606: Serial Number: 4ZS01797 | 2014-01-18 | CC001(Catalytic Converter): Compressor Engine #1 - Oxidation Catalyst; CC002(Catalytic Converter): Compressor Engine #2 - Oxidation Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - Oxidation Catalyst; CC004(Catalytic Converter): Compressor Eng | Alliance Source Testing, Inc. | 1775 | NSPS 0.7g/Hp-hr & 60ppm @ 15% O2, TV .71lb/hr | 1669 | NSPS 0.1g/Hp-hr & 11.6ppm @ 15% O2, TV .49lb/hr | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y | The report was accepted as verification of compliance by the OEPA. However a few instances onsite were witnessed and variances were allowed to the testers for only accepting two runs as verification of compliance for P005 (NOx) and P009 (CO). Many issues could be attributed to the cold weather, however are preventable, and all efforts to prevent these issues from happening in the future will, and have been, taken into account for future test acceptance.
2014 | 394 | 0210002039 | Kilgore Compressor Station-Utica Gas Services, LLC | Pontiff Rd | Kilgore | 43988 |  | Carroll | P004 | 1,775 hp NG-fired 4SLB Stationary ICE equipped w/catalyst Caterpillar G3606: Serial Number: 4ZS01800 | 2014-01-18 | CC001(Catalytic Converter): Compressor Engine #1 - Oxidation Catalyst; CC002(Catalytic Converter): Compressor Engine #2 - Oxidation Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - Oxidation Catalyst; CC004(Catalytic Converter): Compressor Eng | Alliance Source Testing, Inc. | 1775 | NSPS 0.7g/Hp-hr & 60ppm @ 15% O2, TV .71lb/hr | 1698 | NSPS 0.2g/Hp-hr & 12.8ppm @ 15% O2, TV .56lb/hr | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y | The report was accepted as verification of compliance by the OEPA. However a few instances onsite were witnessed and variances were allowed to the testers for only accepting two runs as verification of compliance for P005 (NOx) and P009 (CO). Many issues could be attributed to the cold weather, however are preventable, and all efforts to prevent these issues from happening in the future will, and have been, taken into account for future test acceptance.
2014 | 399 | 0210002039 | Kilgore Compressor Station-Utica Gas Services, LLC | Pontiff Rd | Kilgore | 43988 |  | Carroll | P005 | 1,775 hp NG-fired 4SLB Stationary ICE equipped w/catalyst Caterpillar G3606: Serial Number: 4ZS01804 | 2014-01-18 | CC001(Catalytic Converter): Compressor Engine #1 - Oxidation Catalyst; CC002(Catalytic Converter): Compressor Engine #2 - Oxidation Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - Oxidation Catalyst; CC004(Catalytic Converter): Compressor Eng | Alliance Source Testing, Inc. | 1775 | NSPS 0.7g/Hp-hr & 60ppm @ 15% O2, TV .71lb/hr | 1698 | NSPS 0.2g/Hp-hr & 13.3ppm @ 15% O2, TV .56lb/hr | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y | The report was accepted as verification of compliance by the OEPA. However a few instances onsite were witnessed and variances were allowed to the testers for only accepting two runs as verification of compliance for P005 (NOx) and P009 (CO). Many issues could be attributed to the cold weather, however are preventable, and all efforts to prevent these issues from happening in the future will, and have been, taken into account for future test acceptance.
2014 | 400 | 0210002039 | Kilgore Compressor Station-Utica Gas Services, LLC | Pontiff Rd | Kilgore | 43988 |  | Carroll | P006 | 1,775 hp NG-fired 4SLB Stationary ICE equipped w/catalyst Caterpillar G3606: Serial Number: 4ZS01805 | 2014-01-18 | CC001(Catalytic Converter): Compressor Engine #1 - Oxidation Catalyst; CC002(Catalytic Converter): Compressor Engine #2 - Oxidation Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - Oxidation Catalyst; CC004(Catalytic Converter): Compressor Eng | Alliance Source Testing, Inc. | 1775 | NSPS 0.7g/Hp-hr & 60ppm @ 15% O2, TV .71lb/hr | 1698 | NSPS 0.1g/Hp-hr & 12ppm @ 15% O2, TV .52lb/hr | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y | The report was accepted as verification of compliance by the OEPA. However a few instances onsite were witnessed and variances were allowed to the testers for only accepting two runs as verification of compliance for P005 (NOx) and P009 (CO). Many issues could be attributed to the cold weather, however are preventable, and all efforts to prevent these issues from happening in the future will, and have been, taken into account for future test acceptance.
2014 | 404 | 0210002039 | Kilgore Compressor Station-Utica Gas Services, LLC | Pontiff Rd | Kilgore | 43988 |  | Carroll | P007 | 1,775 hp NG-fired 4SLB Stationary ICE equipped w/catalyst Caterpillar G3606: Serial Number: 4ZS01807 | 2014-01-18 | CC001(Catalytic Converter): Compressor Engine #1 - Oxidation Catalyst; CC002(Catalytic Converter): Compressor Engine #2 - Oxidation Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - Oxidation Catalyst; CC004(Catalytic Converter): Compressor Eng | Alliance Source Testing, Inc. | 1775 | NSPS 0.7g/Hp-hr & 60ppm @ 15% O2, TV .71lb/hr | 1716 | NSPS 0.1g/Hp-hr &11.0ppm @ 15% O2, TV .48lb/hr | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y | The report was accepted as verification of compliance by the OEPA. However a few instances onsite were witnessed and variances were allowed to the testers for only accepting two runs as verification of compliance for P005 (NOx) and P009 (CO). Many issues could be attributed to the cold weather, however are preventable, and all efforts to prevent these issues from happening in the future will, and have been, taken into account for future test acceptance.
2014 | 407 | 0210002039 | Kilgore Compressor Station-Utica Gas Services, LLC | Pontiff Rd | Kilgore | 43988 |  | Carroll | P008 | 1,775 hp NG-fired 4SLB Stationary ICE equipped w/catalyst Caterpillar G3606: Serial Number: 4ZS01808 | 2014-01-18 | CC001(Catalytic Converter): Compressor Engine #1 - Oxidation Catalyst; CC002(Catalytic Converter): Compressor Engine #2 - Oxidation Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - Oxidation Catalyst; CC004(Catalytic Converter): Compressor Eng | Alliance Source Testing, Inc. | 1775 | NSPS 0.7g/Hp-hr & 60ppm @ 15% O2, TV .71lb/hr | 1769 | NSPS 0.2g/Hp-hr & 13.9ppm @ 15% O2, TV .6lb/hr | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y | The report was accepted as verification of compliance by the OEPA. However a few instances onsite were witnessed and variances were allowed to the testers for only accepting two runs as verification of compliance for P005 (NOx) and P009 (CO). Many issues could be attributed to the cold weather, however are preventable, and all efforts to prevent these issues from happening in the future will, and have been, taken into account for future test acceptance.
2014 | 409 | 0210002039 | Kilgore Compressor Station-Utica Gas Services, LLC | Pontiff Rd | Kilgore | 43988 |  | Carroll | P009 | 1,775 hp NG-fired 4SLB Stationary ICE equipped w/catalyst Caterpillar G3606: Serial Number: 4ZS01776 | 2014-01-18 | CC001(Catalytic Converter): Compressor Engine #1 - Oxidation Catalyst; CC002(Catalytic Converter): Compressor Engine #2 - Oxidation Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - Oxidation Catalyst; CC004(Catalytic Converter): Compressor Eng | Alliance Source Testing, Inc. | 1775 | NSPS 0.7g/Hp-hr & 60ppm @ 15% O2, TV .71lb/hr | 1722 | NSPS 0.1g/Hp-hr & 12.3ppm @ 15% O2, TV .53lb/hr | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y | The report was accepted as verification of compliance by the OEPA. However a few instances onsite were witnessed and variances were allowed to the testers for only accepting two runs as verification of compliance for P005 (NOx) and P009 (CO). Many issues could be attributed to the cold weather, however are preventable, and all efforts to prevent these issues from happening in the future will, and have been, taken into account for future test acceptance.
2014 | 412 | 0210002039 | Kilgore Compressor Station-Utica Gas Services, LLC | Pontiff Rd | Kilgore | 43988 |  | Carroll | P010 | 1,775 hp NG-fired 4SLB Stationary ICE equipped w/catalyst Caterpillar G3606: Serial Number: 4ZS01814 | 2014-01-18 | CC001(Catalytic Converter): Compressor Engine #1 - Oxidation Catalyst; CC002(Catalytic Converter): Compressor Engine #2 - Oxidation Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - Oxidation Catalyst; CC004(Catalytic Converter): Compressor Eng | Alliance Source Testing, Inc. | 1775 | NSPS 0.7g/Hp-hr & 60ppm @ 15% O2, TV .71lb/hr | 1663 | NSPS 0.2g/Hp-hr & 15.6ppm @ 15% O2, TV ..66lb/hr | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y | The report was accepted as verification of compliance by the OEPA. However a few instances onsite were witnessed and variances were allowed to the testers for only accepting two runs as verification of compliance for P005 (NOx) and P009 (CO). Many issues could be attributed to the cold weather, however are preventable, and all efforts to prevent these issues from happening in the future will, and have been, taken into account for future test acceptance.
2014 | 425 | 0210002039 | Kilgore Compressor Station-Utica Gas Services, LLC | Pontiff Rd | Kilgore | 43988 |  | Carroll | P001 | 1,775 hp NG-fired 4SLB Stationary ICE equipped w/catalyst Caterpillar G3606 Serial Number: 4ZS01713 | 2014-12-15 | CC001(Catalytic Converter): Compressor Engine #1 - Oxidation Catalyst; CC002(Catalytic Converter): Compressor Engine #2 - Oxidation Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - Oxidation Catalyst; CC004(Catalytic Converter): Compressor Eng | Alliance Source Testing, Inc. | 1775 | 0.7g/Hp-hr & .71lb/hr | 1651 | 0.04g/Hp-hr & 0.13lb/hr | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y
2014 | 428 | 0210002039 | Kilgore Compressor Station-Utica Gas Services, LLC | Pontiff Rd | Kilgore | 43988 |  | Carroll | P002 | 1,775 hp NG-fired 4SLB Stationary ICE equipped w/catalyst Caterpillar G3606: Serial Number: 4ZS01796 | 2014-12-15 | CC001(Catalytic Converter): Compressor Engine #1 - Oxidation Catalyst; CC002(Catalytic Converter): Compressor Engine #2 - Oxidation Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - Oxidation Catalyst; CC004(Catalytic Converter): Compressor Eng | Alliance Source Testing, Inc. | 1775 | 0.7g/Hp-hr & .71lb/hr | 1633 | 0.04g/Hp-hr & 0.16lb/hr | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y
2014 | 431 | 0210002039 | Kilgore Compressor Station-Utica Gas Services, LLC | Pontiff Rd | Kilgore | 43988 |  | Carroll | P003 | 1,775 hp NG-fired 4SLB Stationary ICE equipped w/catalyst Caterpillar G3606: Serial Number: 4ZS01797 | 2014-12-15 | CC001(Catalytic Converter): Compressor Engine #1 - Oxidation Catalyst; CC002(Catalytic Converter): Compressor Engine #2 - Oxidation Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - Oxidation Catalyst; CC004(Catalytic Converter): Compressor Eng | Alliance Source Testing, Inc. | 1775 | 0.7g/Hp-hr & .71lb/hr | 1598 | 0.03g/Hp-hr & 0.13lb/hr | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y
2014 | 435 | 0210002039 | Kilgore Compressor Station-Utica Gas Services, LLC | Pontiff Rd | Kilgore | 43988 |  | Carroll | P004 | 1,775 hp NG-fired 4SLB Stationary ICE equipped w/catalyst Caterpillar G3606: Serial Number: 4ZS01800 | 2014-12-15 | CC001(Catalytic Converter): Compressor Engine #1 - Oxidation Catalyst; CC002(Catalytic Converter): Compressor Engine #2 - Oxidation Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - Oxidation Catalyst; CC004(Catalytic Converter): Compressor Eng | Alliance Source Testing, Inc. | 1775 | 0.7g/Hp-hr & .71lb/hr | 1651 | 0.03g/Hp-hr & 0.12lb/hr | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y
2014 | 436 | 0210002039 | Kilgore Compressor Station-Utica Gas Services, LLC | Pontiff Rd | Kilgore | 43988 |  | Carroll | P005 | 1,775 hp NG-fired 4SLB Stationary ICE equipped w/catalyst Caterpillar G3606: Serial Number: 4ZS01804 | 2014-12-15 | CC001(Catalytic Converter): Compressor Engine #1 - Oxidation Catalyst; CC002(Catalytic Converter): Compressor Engine #2 - Oxidation Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - Oxidation Catalyst; CC004(Catalytic Converter): Compressor Eng | Alliance Source Testing, Inc. | 1775 | 0.7g/Hp-hr & .71lb/hr | 1604 | 0.03g/Hp-hr & 0.11lb/hr | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y
2014 | 441 | 0210002039 | Kilgore Compressor Station-Utica Gas Services, LLC | Pontiff Rd | Kilgore | 43988 |  | Carroll | P006 | 1,775 hp NG-fired 4SLB Stationary ICE equipped w/catalyst Caterpillar G3606: Serial Number: 4ZS01805 | 2014-12-15 | CC001(Catalytic Converter): Compressor Engine #1 - Oxidation Catalyst; CC002(Catalytic Converter): Compressor Engine #2 - Oxidation Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - Oxidation Catalyst; CC004(Catalytic Converter): Compressor Eng | Alliance Source Testing, Inc. | 1775 | 0.7g/Hp-hr & .71lb/hr | 1604 | 0.03g/Hp-hr & 0.10lb/hr | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y
2014 | 442 | 0210002039 | Kilgore Compressor Station-Utica Gas Services, LLC | Pontiff Rd | Kilgore | 43988 |  | Carroll | P007 | 1,775 hp NG-fired 4SLB Stationary ICE equipped w/catalyst Caterpillar G3606: Serial Number: 4ZS01807 | 2014-12-15 | CC001(Catalytic Converter): Compressor Engine #1 - Oxidation Catalyst; CC002(Catalytic Converter): Compressor Engine #2 - Oxidation Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - Oxidation Catalyst; CC004(Catalytic Converter): Compressor Eng | Alliance Source Testing, Inc. | 1775 | 0.7g/Hp-hr & .71lb/hr | 1610 | 0.03g/Hp-hr & 0.09lb/hr | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y
2014 | 445 | 0210002039 | Kilgore Compressor Station-Utica Gas Services, LLC | Pontiff Rd | Kilgore | 43988 |  | Carroll | P008 | 1,775 hp NG-fired 4SLB Stationary ICE equipped w/catalyst Caterpillar G3606: Serial Number: 4ZS01808 | 2014-12-15 | CC001(Catalytic Converter): Compressor Engine #1 - Oxidation Catalyst; CC002(Catalytic Converter): Compressor Engine #2 - Oxidation Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - Oxidation Catalyst; CC004(Catalytic Converter): Compressor Eng | Alliance Source Testing, Inc. | 1775 | 0.7g/Hp-hr & .71lb/hr | 1687 | 0.03g/Hp-hr & 0.12lb/hr | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y
2014 | 450 | 0210002039 | Kilgore Compressor Station-Utica Gas Services, LLC | Pontiff Rd | Kilgore | 43988 |  | Carroll | P009 | 1,775 hp NG-fired 4SLB Stationary ICE equipped w/catalyst Caterpillar G3606: Serial Number: 4ZS01776 | 2014-12-15 | CC001(Catalytic Converter): Compressor Engine #1 - Oxidation Catalyst; CC002(Catalytic Converter): Compressor Engine #2 - Oxidation Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - Oxidation Catalyst; CC004(Catalytic Converter): Compressor Eng | Alliance Source Testing, Inc. | 1775 | 0.7g/Hp-hr & .71lb/hr | 1616 | 0.03g/Hp-hr & 0.11lb/hr | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y
2014 | 452 | 0210002039 | Kilgore Compressor Station-Utica Gas Services, LLC | Pontiff Rd | Kilgore | 43988 |  | Carroll | P010 | 1,775 hp NG-fired 4SLB Stationary ICE equipped w/catalyst Caterpillar G3606: Serial Number: 4ZS01814 | 2014-12-15 | CC001(Catalytic Converter): Compressor Engine #1 - Oxidation Catalyst; CC002(Catalytic Converter): Compressor Engine #2 - Oxidation Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - Oxidation Catalyst; CC004(Catalytic Converter): Compressor Eng | Alliance Source Testing, Inc. | 1775 | 0.7g/Hp-hr & .71lb/hr | 1616 | 0.03g/Hp-hr & 0.09lb/hr | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y
2014 | 455 | 0210002039 | Kilgore Compressor Station-Utica Gas Services, LLC | Pontiff Rd | Kilgore | 43988 |  | Carroll | P001 | 1,775 hp NG-fired 4SLB Stationary ICE equipped w/catalyst Caterpillar G3606 Serial Number: 4ZS01713 | 2014-12-16 | CC001(Catalytic Converter): Compressor Engine #1 - Oxidation Catalyst; CC002(Catalytic Converter): Compressor Engine #2 - Oxidation Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - Oxidation Catalyst; CC004(Catalytic Converter): Compressor Eng | Alliance Source Testing, Inc. | 1775 | 0.7g/Hp-hr & .71lb/hr | 1651 | 0.04g/Hp-hr & 0.13lb/hr | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y
2014 | 457 | 0210002039 | Kilgore Compressor Station-Utica Gas Services, LLC | Pontiff Rd | Kilgore | 43988 |  | Carroll | P002 | 1,775 hp NG-fired 4SLB Stationary ICE equipped w/catalyst Caterpillar G3606: Serial Number: 4ZS01796 | 2014-12-16 | CC001(Catalytic Converter): Compressor Engine #1 - Oxidation Catalyst; CC002(Catalytic Converter): Compressor Engine #2 - Oxidation Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - Oxidation Catalyst; CC004(Catalytic Converter): Compressor Eng | Alliance Source Testing, Inc. | 1775 | 0.7g/Hp-hr & .71lb/hr | 1633 | 0.04g/Hp-hr & 0.16lb/hr | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y
2014 | 460 | 0210002039 | Kilgore Compressor Station-Utica Gas Services, LLC | Pontiff Rd | Kilgore | 43988 |  | Carroll | P003 | 1,775 hp NG-fired 4SLB Stationary ICE equipped w/catalyst Caterpillar G3606: Serial Number: 4ZS01797 | 2014-12-16 | CC001(Catalytic Converter): Compressor Engine #1 - Oxidation Catalyst; CC002(Catalytic Converter): Compressor Engine #2 - Oxidation Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - Oxidation Catalyst; CC004(Catalytic Converter): Compressor Eng | Alliance Source Testing, Inc. | 1775 | 0.7g/Hp-hr & .71lb/hr | 1598 | 0.03g/Hp-hr & 0.13lb/hr | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y
2014 | 463 | 0210002039 | Kilgore Compressor Station-Utica Gas Services, LLC | Pontiff Rd | Kilgore | 43988 |  | Carroll | P004 | 1,775 hp NG-fired 4SLB Stationary ICE equipped w/catalyst Caterpillar G3606: Serial Number: 4ZS01800 | 2014-12-16 | CC001(Catalytic Converter): Compressor Engine #1 - Oxidation Catalyst; CC002(Catalytic Converter): Compressor Engine #2 - Oxidation Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - Oxidation Catalyst; CC004(Catalytic Converter): Compressor Eng | Alliance Source Testing, Inc. | 1775 | 0.7g/Hp-hr & .71lb/hr | 1651 | 0.03g/Hp-hr & 0.12lb/hr | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y
2014 | 468 | 0210002039 | Kilgore Compressor Station-Utica Gas Services, LLC | Pontiff Rd | Kilgore | 43988 |  | Carroll | P005 | 1,775 hp NG-fired 4SLB Stationary ICE equipped w/catalyst Caterpillar G3606: Serial Number: 4ZS01804 | 2014-12-16 | CC001(Catalytic Converter): Compressor Engine #1 - Oxidation Catalyst; CC002(Catalytic Converter): Compressor Engine #2 - Oxidation Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - Oxidation Catalyst; CC004(Catalytic Converter): Compressor Eng | Alliance Source Testing, Inc. | 1775 | 0.7g/Hp-hr & .71lb/hr | 1604 | 0.03g/Hp-hr & 0.11lb/hr | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y
2014 | 470 | 0210002039 | Kilgore Compressor Station-Utica Gas Services, LLC | Pontiff Rd | Kilgore | 43988 |  | Carroll | P006 | 1,775 hp NG-fired 4SLB Stationary ICE equipped w/catalyst Caterpillar G3606: Serial Number: 4ZS01805 | 2014-12-16 | CC001(Catalytic Converter): Compressor Engine #1 - Oxidation Catalyst; CC002(Catalytic Converter): Compressor Engine #2 - Oxidation Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - Oxidation Catalyst; CC004(Catalytic Converter): Compressor Eng | Alliance Source Testing, Inc. | 1775 | 0.7g/Hp-hr & .71lb/hr | 1604 | 0.03g/Hp-hr & 0.10lb/hr | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y
2014 | 474 | 0210002039 | Kilgore Compressor Station-Utica Gas Services, LLC | Pontiff Rd | Kilgore | 43988 |  | Carroll | P007 | 1,775 hp NG-fired 4SLB Stationary ICE equipped w/catalyst Caterpillar G3606: Serial Number: 4ZS01807 | 2014-12-16 | CC001(Catalytic Converter): Compressor Engine #1 - Oxidation Catalyst; CC002(Catalytic Converter): Compressor Engine #2 - Oxidation Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - Oxidation Catalyst; CC004(Catalytic Converter): Compressor Eng | Alliance Source Testing, Inc. | 1775 | 0.7g/Hp-hr & .71lb/hr | 1610 | 0.03g/Hp-hr & 0.09lb/hr | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y
2014 | 476 | 0210002039 | Kilgore Compressor Station-Utica Gas Services, LLC | Pontiff Rd | Kilgore | 43988 |  | Carroll | P008 | 1,775 hp NG-fired 4SLB Stationary ICE equipped w/catalyst Caterpillar G3606: Serial Number: 4ZS01808 | 2014-12-16 | CC001(Catalytic Converter): Compressor Engine #1 - Oxidation Catalyst; CC002(Catalytic Converter): Compressor Engine #2 - Oxidation Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - Oxidation Catalyst; CC004(Catalytic Converter): Compressor Eng | Alliance Source Testing, Inc. | 1775 | 0.7g/Hp-hr & .71lb/hr | 1687 | 0.03g/Hp-hr & 0.12lb/hr | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y
2014 | 479 | 0210002039 | Kilgore Compressor Station-Utica Gas Services, LLC | Pontiff Rd | Kilgore | 43988 |  | Carroll | P009 | 1,775 hp NG-fired 4SLB Stationary ICE equipped w/catalyst Caterpillar G3606: Serial Number: 4ZS01776 | 2014-12-16 | CC001(Catalytic Converter): Compressor Engine #1 - Oxidation Catalyst; CC002(Catalytic Converter): Compressor Engine #2 - Oxidation Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - Oxidation Catalyst; CC004(Catalytic Converter): Compressor Eng | Alliance Source Testing, Inc. | 1775 | 0.7g/Hp-hr & .71lb/hr | 1616 | 0.03g/Hp-hr & 0.11lb/hr | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y
2014 | 482 | 0210002039 | Kilgore Compressor Station-Utica Gas Services, LLC | Pontiff Rd | Kilgore | 43988 |  | Carroll | P010 | 1,775 hp NG-fired 4SLB Stationary ICE equipped w/catalyst Caterpillar G3606: Serial Number: 4ZS01814 | 2014-12-16 | CC001(Catalytic Converter): Compressor Engine #1 - Oxidation Catalyst; CC002(Catalytic Converter): Compressor Engine #2 - Oxidation Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - Oxidation Catalyst; CC004(Catalytic Converter): Compressor Eng | Alliance Source Testing, Inc. | 1775 | 0.7g/Hp-hr & .71lb/hr | 1616 | 0.03g/Hp-hr & 0.09lb/hr | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y
2014 | 485 | 0210002039 | Kilgore Compressor Station-Utica Gas Services, LLC | Pontiff Rd | Kilgore | 43988 |  | Carroll | P001 | 1,775 hp NG-fired 4SLB Stationary ICE equipped w/catalyst Caterpillar G3606 Serial Number: 4ZS01713 | 2014-12-17 | CC001(Catalytic Converter): Compressor Engine #1 - Oxidation Catalyst; CC002(Catalytic Converter): Compressor Engine #2 - Oxidation Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - Oxidation Catalyst; CC004(Catalytic Converter): Compressor Eng | Alliance Source Testing, Inc. | 1775 | 0.7g/Hp-hr & .71lb/hr | 1651 | 0.04g/Hp-hr & 0.13lb/hr | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y
2014 | 487 | 0210002039 | Kilgore Compressor Station-Utica Gas Services, LLC | Pontiff Rd | Kilgore | 43988 |  | Carroll | P002 | 1,775 hp NG-fired 4SLB Stationary ICE equipped w/catalyst Caterpillar G3606: Serial Number: 4ZS01796 | 2014-12-17 | CC001(Catalytic Converter): Compressor Engine #1 - Oxidation Catalyst; CC002(Catalytic Converter): Compressor Engine #2 - Oxidation Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - Oxidation Catalyst; CC004(Catalytic Converter): Compressor Eng | Alliance Source Testing, Inc. | 1775 | 0.7g/Hp-hr & .71lb/hr | 1633 | 0.04g/Hp-hr & 0.16lb/hr | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y
2014 | 490 | 0210002039 | Kilgore Compressor Station-Utica Gas Services, LLC | Pontiff Rd | Kilgore | 43988 |  | Carroll | P003 | 1,775 hp NG-fired 4SLB Stationary ICE equipped w/catalyst Caterpillar G3606: Serial Number: 4ZS01797 | 2014-12-17 | CC001(Catalytic Converter): Compressor Engine #1 - Oxidation Catalyst; CC002(Catalytic Converter): Compressor Engine #2 - Oxidation Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - Oxidation Catalyst; CC004(Catalytic Converter): Compressor Eng | Alliance Source Testing, Inc. | 1775 | 0.7g/Hp-hr & .71lb/hr | 1598 | 0.03g/Hp-hr & 0.13lb/hr | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y
2014 | 493 | 0210002039 | Kilgore Compressor Station-Utica Gas Services, LLC | Pontiff Rd | Kilgore | 43988 |  | Carroll | P004 | 1,775 hp NG-fired 4SLB Stationary ICE equipped w/catalyst Caterpillar G3606: Serial Number: 4ZS01800 | 2014-12-17 | CC001(Catalytic Converter): Compressor Engine #1 - Oxidation Catalyst; CC002(Catalytic Converter): Compressor Engine #2 - Oxidation Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - Oxidation Catalyst; CC004(Catalytic Converter): Compressor Eng | Alliance Source Testing, Inc. | 1775 | 0.7g/Hp-hr & .71lb/hr | 1651 | 0.03g/Hp-hr & 0.12lb/hr | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y
2014 | 497 | 0210002039 | Kilgore Compressor Station-Utica Gas Services, LLC | Pontiff Rd | Kilgore | 43988 |  | Carroll | P005 | 1,775 hp NG-fired 4SLB Stationary ICE equipped w/catalyst Caterpillar G3606: Serial Number: 4ZS01804 | 2014-12-17 | CC001(Catalytic Converter): Compressor Engine #1 - Oxidation Catalyst; CC002(Catalytic Converter): Compressor Engine #2 - Oxidation Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - Oxidation Catalyst; CC004(Catalytic Converter): Compressor Eng | Alliance Source Testing, Inc. | 1775 | 0.7g/Hp-hr & .71lb/hr | 1604 | 0.03g/Hp-hr & 0.11lb/hr | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y
2014 | 500 | 0210002039 | Kilgore Compressor Station-Utica Gas Services, LLC | Pontiff Rd | Kilgore | 43988 |  | Carroll | P006 | 1,775 hp NG-fired 4SLB Stationary ICE equipped w/catalyst Caterpillar G3606: Serial Number: 4ZS01805 | 2014-12-17 | CC001(Catalytic Converter): Compressor Engine #1 - Oxidation Catalyst; CC002(Catalytic Converter): Compressor Engine #2 - Oxidation Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - Oxidation Catalyst; CC004(Catalytic Converter): Compressor Eng | Alliance Source Testing, Inc. | 1775 | 0.7g/Hp-hr & .71lb/hr | 1604 | 0.03g/Hp-hr & 0.10lb/hr | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y
2014 | 502 | 0210002039 | Kilgore Compressor Station-Utica Gas Services, LLC | Pontiff Rd | Kilgore | 43988 |  | Carroll | P007 | 1,775 hp NG-fired 4SLB Stationary ICE equipped w/catalyst Caterpillar G3606: Serial Number: 4ZS01807 | 2014-12-17 | CC001(Catalytic Converter): Compressor Engine #1 - Oxidation Catalyst; CC002(Catalytic Converter): Compressor Engine #2 - Oxidation Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - Oxidation Catalyst; CC004(Catalytic Converter): Compressor Eng | Alliance Source Testing, Inc. | 1775 | 0.7g/Hp-hr & .71lb/hr | 1610 | 0.03g/Hp-hr & 0.09lb/hr | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y
2014 | 506 | 0210002039 | Kilgore Compressor Station-Utica Gas Services, LLC | Pontiff Rd | Kilgore | 43988 |  | Carroll | P008 | 1,775 hp NG-fired 4SLB Stationary ICE equipped w/catalyst Caterpillar G3606: Serial Number: 4ZS01808 | 2014-12-17 | CC001(Catalytic Converter): Compressor Engine #1 - Oxidation Catalyst; CC002(Catalytic Converter): Compressor Engine #2 - Oxidation Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - Oxidation Catalyst; CC004(Catalytic Converter): Compressor Eng | Alliance Source Testing, Inc. | 1775 | 0.7g/Hp-hr & .71lb/hr | 1687 | 0.03g/Hp-hr & 0.12lb/hr | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y
2014 | 510 | 0210002039 | Kilgore Compressor Station-Utica Gas Services, LLC | Pontiff Rd | Kilgore | 43988 |  | Carroll | P009 | 1,775 hp NG-fired 4SLB Stationary ICE equipped w/catalyst Caterpillar G3606: Serial Number: 4ZS01776 | 2014-12-17 | CC001(Catalytic Converter): Compressor Engine #1 - Oxidation Catalyst; CC002(Catalytic Converter): Compressor Engine #2 - Oxidation Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - Oxidation Catalyst; CC004(Catalytic Converter): Compressor Eng | Alliance Source Testing, Inc. | 1775 | 0.7g/Hp-hr & .71lb/hr | 1616 | 0.03g/Hp-hr & 0.11lb/hr | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y
2014 | 511 | 0210002039 | Kilgore Compressor Station-Utica Gas Services, LLC | Pontiff Rd | Kilgore | 43988 |  | Carroll | P010 | 1,775 hp NG-fired 4SLB Stationary ICE equipped w/catalyst Caterpillar G3606: Serial Number: 4ZS01814 | 2014-12-17 | CC001(Catalytic Converter): Compressor Engine #1 - Oxidation Catalyst; CC002(Catalytic Converter): Compressor Engine #2 - Oxidation Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - Oxidation Catalyst; CC004(Catalytic Converter): Compressor Eng | Alliance Source Testing, Inc. | 1775 | 0.7g/Hp-hr & .71lb/hr | 1616 | 0.03g/Hp-hr & 0.09lb/hr | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y
2014 | 516 | 0210002047 | Chesapeake Exploration LLC - Hutchison 33-15-5 Pad | Moccasin Road NE | Augusta Twp. | 44615 |  | Carroll | P002 | Natural Gas Engines | 2014-07-01 | Catalyst | Alliance Source Testing, Inc. | 211 Hp | 60ppmvd@15%O2 | 150 hp or 71% | 1.9ppmvd@15%O2 | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y | Unit not tested at 90% of Max
2014 | 519 | 0210002056 | Chesapeake Exploration LLC - Bryan Shaw 21-13-5 Pad | Perron Rd SE | Harlem Springs | 43903 |  | Carroll | P002 | One or multiple stationary natural gas-fired spark ignition (SI) internal combustion engines (ICE) with a combined total horsepower (HP) of no more than 1,800 HP for the site. Includes 2007 and later model year engines manufactured after the applicable effective date identified in 40 CFR 60.4230(a)(3) and engines manufactured before the NSPS effective date where compliance with the Part 60 Subpart JJJJ emissions standards for the same size engine can be demonstrated through stack testing. | 2014-10-09 | Catalyst | Alliance Source Testing, Inc. | 185 Bhp | NMEVOC-60 ppmvd @ 15% O2 | 167 Bhp | 0.4 ppmvd | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y | G6X08444 185 Bhp site rate engine tested
2014 | 521 | 0210002057 | Chesapeake Exploration LLC - Javersak 28-12-5 Pad | Saber Road | Kilgore | 43903 |  | Carroll | P002 | One or multiple stationary natural gas-fired spark ignition (SI) internal combustion engines (ICE) with a combined total horsepower (HP) of no more than 1,800 HP for the site.* Includes 2007 and later model year engines manufactured after the applicable effective date identified in 40 CFR 60.4230(a)(3); and engines manufactured before the effective date of the NSPS, where compliance with the Part 60 Subpart JJJJ emissions standards for the same size engine can be met by retrofitting the engine with a control device and demonstrated through stack testing. | 2014-11-13 | Catalyst | Alliance Source Testing | 174 Site rate 211 Max | 60 ppmvd @15%O2 | 167 96% of Site Rate | 0.3 ppmvd @15%O2 | 25A | Total Hydrocarbons | PASS | NA | Y
2014 | 523 | 0210012002 | Utica Gas Services, LLC-Carrollton Compressor Facility | 2098 Panda Road SE | Carrollton | 44615 |  | Carroll | P004 | 1,775 HP natural gas-fired Caterpillar G3606 engine #1 equipped with an oxidation catalyst. | 2014-02-10 | Oxid. Cat.(Catalytic Converter): Oxidative Catalyst | Air Hygiene Services | 1775 HP | 86ppmvd@15%O2, 0.82lbs/hr, 1.0g/hp-hr | 1684 HP | 5.22ppmvd@15%O2, 0.20lbs/hr, 0.05g/hp-hr | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y
2014 | 526 | 0210012002 | Utica Gas Services, LLC-Carrollton Compressor Facility | 2098 Panda Road SE | Carrollton | 44615 |  | Carroll | P005 | 1,775 HP natural gas-fired Caterpillar G3606 engine #2 equipped with an oxidation catalyst | 2014-02-10 | Oxid. Cat.(Catalytic Converter): Oxidative Catalyst | Air Hygiene Services | 1775 HP | 86ppmvd@15%O2, 0.82lbs/hr, 1.0g/hp-hr | 1666 HP | 5.36ppmvd@15%O2, 0.20lbs/hr, 0.05g/hp-hr | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y
2014 | 530 | 0210012002 | Utica Gas Services, LLC-Carrollton Compressor Facility | 2098 Panda Road SE | Carrollton | 44615 |  | Carroll | P006 | 1,775 HP natural gas-fired Caterpillar G3606 engine #3 equipped with an oxidation catalyst | 2014-02-10 | Oxid. Cat.(Catalytic Converter): Oxidative Catalyst | Air Hygiene Services | 1775 HP | 60ppmvd@15%O2, 0.82lbs/hr, 0.07g/hp-hr | 1617 HP | 4.26ppmvd@15%O2, 0.15lbs/hr, 0.04g/hp-hr | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y
2014 | 533 | 0210012002 | Utica Gas Services, LLC-Carrollton Compressor Facility | 2098 Panda Road SE | Carrollton | 44615 |  | Carroll | P007 | 1,775 HP natural gas-fired Caterpillar G3606 engine #4 equipped with an oxidation catalyst | 2014-02-10 | Oxid. Cat.(Catalytic Converter): Oxidative Catalyst | Air Hygiene Services | 1775 HP | 60ppmvd@15%O2, 0.82lbs/hr, 0.07g/hp-hr | 1613 HP | 4.49ppmvd@15%O2, 0.16lbs/hr, 0.04g/hp-hr | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y
2014 | 537 | 0210012002 | Utica Gas Services, LLC-Carrollton Compressor Facility | 2098 Panda Road SE | Carrollton | 44615 |  | Carroll | P008 | 1,775 HP natural gas-fired Caterpillar G3606 engine #5 equipped with an oxidation catalyst | 2014-02-10 | Oxid. Cat.(Catalytic Converter): Oxidative Catalyst | Air Hygiene Services | 1775 HP | 60ppmvd@15%O2, 0.82lbs/hr, 0.07g/hp-hr | 1622 HP | 4.14ppmvd@15%O2, 0.14lbs/hr, 0.04g/hp-hr | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y
2014 | 538 | 0210012002 | Utica Gas Services, LLC-Carrollton Compressor Facility | 2098 Panda Road SE | Carrollton | 44615 |  | Carroll | P009 | 1,775 HP natural gas-fired Caterpillar G3606 engine #6 equipped with an oxidation catalyst | 2014-02-10 | Oxid. Cat.(Catalytic Converter): Oxidative Catalyst | Air Hygiene Services | 1775 HP | 60ppmvd@15%O2, 0.82lbs/hr, 0.07g/hp-hr | 1623 HP | 3.95ppmvd@15%O2, 0.13lbs/hr, 0.04g/hp-hr | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y
2014 | 543 | 0210012002 | Utica Gas Services, LLC-Carrollton Compressor Facility | 2098 Panda Road SE | Carrollton | 44615 |  | Carroll | P010 | 1,775 HP natural gas-fired Caterpillar G3606 engine #7 equipped with an oxidation catalyst | 2014-02-10 | Oxid. Cat.(Catalytic Converter): Oxidative Catalyst | Air Hygiene Services | 1775 HP | 60ppmvd@15%O2, 0.82lbs/hr, 0.07g/hp-hr | 1615 HP | 4.36ppmvd@15%O2, 0.15lbs/hr, 0.04g/hp-hr | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y
2014 | 544 | 0210012002 | Utica Gas Services, LLC-Carrollton Compressor Facility | 2098 Panda Road SE | Carrollton | 44615 |  | Carroll | P011 | 1,775 HP natural gas-fired Caterpillar G3606 engine #8 equipped with an oxidation catalyst | 2014-02-10 | Oxid. Cat.(Catalytic Converter): Oxidative Catalyst | Air Hygiene Services | 1775 HP | 60ppmvd@15%O2, 0.82lbs/hr, 0.07g/hp-hr | 1620 HP | 4.58ppmvd@15%O2, 0.16lbs/hr, 0.04g/hp-hr | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y
2014 | 548 | 0210012002 | Utica Gas Services, LLC-Carrollton Compressor Facility | 2098 Panda Road SE | Carrollton | 44615 |  | Carroll | P012 | 1,775 HP natural gas-fired Caterpillar G3606 engine #9 equipped with an oxidation catalyst | 2014-02-10 | Oxid. Cat.(Catalytic Converter): Oxidative Catalyst | Air Hygiene Services | 1775 HP | 60ppmvd@15%O2, 0.82lbs/hr, 0.07g/hp-hr | 1643 HP | 4.96ppmvd@15%O2, 0.19lbs/hr, 0.05g/hp-hr | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y
2014 | 552 | 0210012002 | Utica Gas Services, LLC-Carrollton Compressor Facility | 2098 Panda Road SE | Carrollton | 44615 |  | Carroll | P013 | 1,775 HP natural gas-fired Caterpillar G3606 engine #10equipped with an oxidation catalyst | 2014-02-10 | Oxid. Cat.(Catalytic Converter): Oxidative Catalyst | Air Hygiene Services | 1775 HP | 60ppmvd@15%O2, 0.82lbs/hr, 0.07g/hp-hr | 1593 HP | 3.16ppmvd@15%O2, 0.10lbs/hr, 0.03g/hp-hr | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y
2014 | 554 | 0210012002 | Utica Gas Services, LLC-Carrollton Compressor Facility | 2098 Panda Road SE | Carrollton | 44615 |  | Carroll | P004 | 1,775 HP natural gas-fired Caterpillar G3606 engine #1 equipped with an oxidation catalyst. | 2014-02-11 | Oxid. Cat.(Catalytic Converter): Oxidative Catalyst | Air Hygiene Services | 1775 HP | 86ppmvd@15%O2, 0.82lbs/hr, 1.0g/hp-hr | 1684 HP | 5.22ppmvd@15%O2, 0.20lbs/hr, 0.05g/hp-hr | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y
2014 | 558 | 0210012002 | Utica Gas Services, LLC-Carrollton Compressor Facility | 2098 Panda Road SE | Carrollton | 44615 |  | Carroll | P005 | 1,775 HP natural gas-fired Caterpillar G3606 engine #2 equipped with an oxidation catalyst | 2014-02-11 | Oxid. Cat.(Catalytic Converter): Oxidative Catalyst | Air Hygiene Services | 1775 HP | 86ppmvd@15%O2, 0.82lbs/hr, 1.0g/hp-hr | 1666 HP | 5.36ppmvd@15%O2, 0.20lbs/hr, 0.05g/hp-hr | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y
2014 | 560 | 0210012002 | Utica Gas Services, LLC-Carrollton Compressor Facility | 2098 Panda Road SE | Carrollton | 44615 |  | Carroll | P006 | 1,775 HP natural gas-fired Caterpillar G3606 engine #3 equipped with an oxidation catalyst | 2014-02-11 | Oxid. Cat.(Catalytic Converter): Oxidative Catalyst | Air Hygiene Services | 1775 HP | 60ppmvd@15%O2, 0.82lbs/hr, 0.07g/hp-hr | 1617 HP | 4.26ppmvd@15%O2, 0.15lbs/hr, 0.04g/hp-hr | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y
2014 | 563 | 0210012002 | Utica Gas Services, LLC-Carrollton Compressor Facility | 2098 Panda Road SE | Carrollton | 44615 |  | Carroll | P007 | 1,775 HP natural gas-fired Caterpillar G3606 engine #4 equipped with an oxidation catalyst | 2014-02-11 | Oxid. Cat.(Catalytic Converter): Oxidative Catalyst | Air Hygiene Services | 1775 HP | 60ppmvd@15%O2, 0.82lbs/hr, 0.07g/hp-hr | 1613 HP | 4.49ppmvd@15%O2, 0.16lbs/hr, 0.04g/hp-hr | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y
2014 | 565 | 0210012002 | Utica Gas Services, LLC-Carrollton Compressor Facility | 2098 Panda Road SE | Carrollton | 44615 |  | Carroll | P008 | 1,775 HP natural gas-fired Caterpillar G3606 engine #5 equipped with an oxidation catalyst | 2014-02-11 | Oxid. Cat.(Catalytic Converter): Oxidative Catalyst | Air Hygiene Services | 1775 HP | 60ppmvd@15%O2, 0.82lbs/hr, 0.07g/hp-hr | 1622 HP | 4.14ppmvd@15%O2, 0.14lbs/hr, 0.04g/hp-hr | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y
2014 | 569 | 0210012002 | Utica Gas Services, LLC-Carrollton Compressor Facility | 2098 Panda Road SE | Carrollton | 44615 |  | Carroll | P009 | 1,775 HP natural gas-fired Caterpillar G3606 engine #6 equipped with an oxidation catalyst | 2014-02-11 | Oxid. Cat.(Catalytic Converter): Oxidative Catalyst | Air Hygiene Services | 1775 HP | 60ppmvd@15%O2, 0.82lbs/hr, 0.07g/hp-hr | 1623 HP | 3.95ppmvd@15%O2, 0.13lbs/hr, 0.04g/hp-hr | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y
2014 | 572 | 0210012002 | Utica Gas Services, LLC-Carrollton Compressor Facility | 2098 Panda Road SE | Carrollton | 44615 |  | Carroll | P010 | 1,775 HP natural gas-fired Caterpillar G3606 engine #7 equipped with an oxidation catalyst | 2014-02-11 | Oxid. Cat.(Catalytic Converter): Oxidative Catalyst | Air Hygiene Services | 1775 HP | 60ppmvd@15%O2, 0.82lbs/hr, 0.07g/hp-hr | 1615 HP | 4.36ppmvd@15%O2, 0.15lbs/hr, 0.04g/hp-hr | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y
2014 | 576 | 0210012002 | Utica Gas Services, LLC-Carrollton Compressor Facility | 2098 Panda Road SE | Carrollton | 44615 |  | Carroll | P011 | 1,775 HP natural gas-fired Caterpillar G3606 engine #8 equipped with an oxidation catalyst | 2014-02-11 | Oxid. Cat.(Catalytic Converter): Oxidative Catalyst | Air Hygiene Services | 1775 HP | 60ppmvd@15%O2, 0.82lbs/hr, 0.07g/hp-hr | 1620 HP | 4.58ppmvd@15%O2, 0.16lbs/hr, 0.04g/hp-hr | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y
2014 | 579 | 0210012002 | Utica Gas Services, LLC-Carrollton Compressor Facility | 2098 Panda Road SE | Carrollton | 44615 |  | Carroll | P012 | 1,775 HP natural gas-fired Caterpillar G3606 engine #9 equipped with an oxidation catalyst | 2014-02-11 | Oxid. Cat.(Catalytic Converter): Oxidative Catalyst | Air Hygiene Services | 1775 HP | 60ppmvd@15%O2, 0.82lbs/hr, 0.07g/hp-hr | 1643 HP | 4.96ppmvd@15%O2, 0.19lbs/hr, 0.05g/hp-hr | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y
2014 | 580 | 0210012002 | Utica Gas Services, LLC-Carrollton Compressor Facility | 2098 Panda Road SE | Carrollton | 44615 |  | Carroll | P013 | 1,775 HP natural gas-fired Caterpillar G3606 engine #10equipped with an oxidation catalyst | 2014-02-11 | Oxid. Cat.(Catalytic Converter): Oxidative Catalyst | Air Hygiene Services | 1775 HP | 60ppmvd@15%O2, 0.82lbs/hr, 0.07g/hp-hr | 1593 HP | 3.16ppmvd@15%O2, 0.10lbs/hr, 0.03g/hp-hr | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y
2014 | 585 | 0210012002 | Utica Gas Services, LLC-Carrollton Compressor Facility | 2098 Panda Road SE | Carrollton | 44615 |  | Carroll | P004 | 1,775 HP natural gas-fired Caterpillar G3606 engine #1 equipped with an oxidation catalyst. | 2014-02-12 | Oxid. Cat.(Catalytic Converter): Oxidative Catalyst | Air Hygiene Services | 1775 HP | 86ppmvd@15%O2, 0.82lbs/hr, 1.0g/hp-hr | 1684 HP | 5.22ppmvd@15%O2, 0.20lbs/hr, 0.05g/hp-hr | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y
2014 | 586 | 0210012002 | Utica Gas Services, LLC-Carrollton Compressor Facility | 2098 Panda Road SE | Carrollton | 44615 |  | Carroll | P005 | 1,775 HP natural gas-fired Caterpillar G3606 engine #2 equipped with an oxidation catalyst | 2014-02-12 | Oxid. Cat.(Catalytic Converter): Oxidative Catalyst | Air Hygiene Services | 1775 HP | 86ppmvd@15%O2, 0.82lbs/hr, 1.0g/hp-hr | 1666 HP | 5.36ppmvd@15%O2, 0.20lbs/hr, 0.05g/hp-hr | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y
2014 | 591 | 0210012002 | Utica Gas Services, LLC-Carrollton Compressor Facility | 2098 Panda Road SE | Carrollton | 44615 |  | Carroll | P006 | 1,775 HP natural gas-fired Caterpillar G3606 engine #3 equipped with an oxidation catalyst | 2014-02-12 | Oxid. Cat.(Catalytic Converter): Oxidative Catalyst | Air Hygiene Services | 1775 HP | 60ppmvd@15%O2, 0.82lbs/hr, 0.07g/hp-hr | 1617 HP | 4.26ppmvd@15%O2, 0.15lbs/hr, 0.04g/hp-hr | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y
2014 | 594 | 0210012002 | Utica Gas Services, LLC-Carrollton Compressor Facility | 2098 Panda Road SE | Carrollton | 44615 |  | Carroll | P007 | 1,775 HP natural gas-fired Caterpillar G3606 engine #4 equipped with an oxidation catalyst | 2014-02-12 | Oxid. Cat.(Catalytic Converter): Oxidative Catalyst | Air Hygiene Services | 1775 HP | 60ppmvd@15%O2, 0.82lbs/hr, 0.07g/hp-hr | 1613 HP | 4.49ppmvd@15%O2, 0.16lbs/hr, 0.04g/hp-hr | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y
2014 | 596 | 0210012002 | Utica Gas Services, LLC-Carrollton Compressor Facility | 2098 Panda Road SE | Carrollton | 44615 |  | Carroll | P008 | 1,775 HP natural gas-fired Caterpillar G3606 engine #5 equipped with an oxidation catalyst | 2014-02-12 | Oxid. Cat.(Catalytic Converter): Oxidative Catalyst | Air Hygiene Services | 1775 HP | 60ppmvd@15%O2, 0.82lbs/hr, 0.07g/hp-hr | 1622 HP | 4.14ppmvd@15%O2, 0.14lbs/hr, 0.04g/hp-hr | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y
2014 | 600 | 0210012002 | Utica Gas Services, LLC-Carrollton Compressor Facility | 2098 Panda Road SE | Carrollton | 44615 |  | Carroll | P009 | 1,775 HP natural gas-fired Caterpillar G3606 engine #6 equipped with an oxidation catalyst | 2014-02-12 | Oxid. Cat.(Catalytic Converter): Oxidative Catalyst | Air Hygiene Services | 1775 HP | 60ppmvd@15%O2, 0.82lbs/hr, 0.07g/hp-hr | 1623 HP | 3.95ppmvd@15%O2, 0.13lbs/hr, 0.04g/hp-hr | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y
2014 | 601 | 0210012002 | Utica Gas Services, LLC-Carrollton Compressor Facility | 2098 Panda Road SE | Carrollton | 44615 |  | Carroll | P010 | 1,775 HP natural gas-fired Caterpillar G3606 engine #7 equipped with an oxidation catalyst | 2014-02-12 | Oxid. Cat.(Catalytic Converter): Oxidative Catalyst | Air Hygiene Services | 1775 HP | 60ppmvd@15%O2, 0.82lbs/hr, 0.07g/hp-hr | 1615 HP | 4.36ppmvd@15%O2, 0.15lbs/hr, 0.04g/hp-hr | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y
2014 | 605 | 0210012002 | Utica Gas Services, LLC-Carrollton Compressor Facility | 2098 Panda Road SE | Carrollton | 44615 |  | Carroll | P011 | 1,775 HP natural gas-fired Caterpillar G3606 engine #8 equipped with an oxidation catalyst | 2014-02-12 | Oxid. Cat.(Catalytic Converter): Oxidative Catalyst | Air Hygiene Services | 1775 HP | 60ppmvd@15%O2, 0.82lbs/hr, 0.07g/hp-hr | 1620 HP | 4.58ppmvd@15%O2, 0.16lbs/hr, 0.04g/hp-hr | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y
2014 | 609 | 0210012002 | Utica Gas Services, LLC-Carrollton Compressor Facility | 2098 Panda Road SE | Carrollton | 44615 |  | Carroll | P012 | 1,775 HP natural gas-fired Caterpillar G3606 engine #9 equipped with an oxidation catalyst | 2014-02-12 | Oxid. Cat.(Catalytic Converter): Oxidative Catalyst | Air Hygiene Services | 1775 HP | 60ppmvd@15%O2, 0.82lbs/hr, 0.07g/hp-hr | 1643 HP | 4.96ppmvd@15%O2, 0.19lbs/hr, 0.05g/hp-hr | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y
2014 | 611 | 0210012002 | Utica Gas Services, LLC-Carrollton Compressor Facility | 2098 Panda Road SE | Carrollton | 44615 |  | Carroll | P013 | 1,775 HP natural gas-fired Caterpillar G3606 engine #10equipped with an oxidation catalyst | 2014-02-12 | Oxid. Cat.(Catalytic Converter): Oxidative Catalyst | Air Hygiene Services | 1775 HP | 60ppmvd@15%O2, 0.82lbs/hr, 0.07g/hp-hr | 1593 HP | 3.16ppmvd@15%O2, 0.10lbs/hr, 0.03g/hp-hr | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y
2014 | 617 | 0210012004 | Augusta Compressor Facility- Utica Gas Services, L.L.C. | 8034 Bane Rd NE | East Twp. | 44427 |  | Carroll | P006 | 1,775-hp Caterpillar G3606 Compressor Engine w/ Oxidation Catalyst | 2014-09-16 | Oxid. Cat. 3(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 4(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 5(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 6(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 7(Catalytic Converter): | Great Plains Analytical Services | 1775 Hp | 0.54 lbs/hr, 0.7 g/hp/hr, 60ppmvd@15%O2 | 1831 | 0.36 lbs/hr, 0.09 g/hp/hr, 8.91 ppmvd@15%O2 | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y
2014 | 620 | 0210012004 | Augusta Compressor Facility- Utica Gas Services, L.L.C. | 8034 Bane Rd NE | East Twp. | 44427 |  | Carroll | P007 | 1,775-hp Caterpillar G3606 Compressor Engine w/ Oxidation Catalyst | 2014-09-16 | Oxid. Cat. 3(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 4(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 5(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 6(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 7(Catalytic Converter): | Great Plains Analytical Services | 1775 Hp | 0.54 lbs/hr, 0.7 g/hp/hr, 60ppmvd@15%O2 | 1839 | 0.34 lbs/hr, 0.08 g/hp/hr, 8.16 ppmvd@15%O2 | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y
2014 | 622 | 0210012004 | Augusta Compressor Facility- Utica Gas Services, L.L.C. | 8034 Bane Rd NE | East Twp. | 44427 |  | Carroll | P008 | 1,775-hp Caterpillar G3606 Compressor Engine w/ Oxidation Catalyst | 2014-09-16 | Oxid. Cat. 3(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 4(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 5(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 6(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 7(Catalytic Converter): | Great Plains Analytical Services | 1775 Hp | 0.54 lbs/hr, 0.7 g/hp/hr, 60ppmvd@15%O2 | 1809 | 0.27 lbs/hr, 0.06 g/hp/hr, 6.8 ppmvd@15%O2 | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y
2014 | 626 | 0210012004 | Augusta Compressor Facility- Utica Gas Services, L.L.C. | 8034 Bane Rd NE | East Twp. | 44427 |  | Carroll | P009 | 1,775-hp Caterpillar G3606 Compressor Engine w/ Oxidation Catalyst | 2014-09-16 | Oxid. Cat. 3(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 4(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 5(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 6(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 7(Catalytic Converter): | Great Plains Analytical Services | 1775 Hp | 0.54 lbs/hr, 0.7 g/hp/hr, 60ppmvd@15%O2 | 1788 | 0.41 lbs/hr, 0.10 g/hp/hr, 10.27ppmvd@15%O2 | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y
2014 | 630 | 0210012004 | Augusta Compressor Facility- Utica Gas Services, L.L.C. | 8034 Bane Rd NE | East Twp. | 44427 |  | Carroll | P010 | 1,775-hp Caterpillar G3606 Compressor Engine w/ Oxidation Catalyst | 2014-09-16 | Oxid. Cat. 3(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 4(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 5(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 6(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 7(Catalytic Converter): | Great Plains Analytical Services | 1775 Hp | 0.54 lbs/hr, 0.7 g/hp/hr, 60ppmvd@15%O2 | 1819 | 0.46 lbs/hr, 0.11 g/hp/hr, 11.11ppmvd@15%O2 | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y
2014 | 633 | 0210012004 | Augusta Compressor Facility- Utica Gas Services, L.L.C. | 8034 Bane Rd NE | East Twp. | 44427 |  | Carroll | P011 | 1,775-hp Caterpillar G3606 Compressor Engine w/ Oxidation Catalyst | 2014-09-16 | Oxid. Cat. 3(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 4(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 5(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 6(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 7(Catalytic Converter): | Great Plains Analytical Services | 1775 Hp | 0.54 lbs/hr, 0.7 g/hp/hr, 60ppmvd@15%O2 | 1821 | 0.35 lbs/hr, 0.08 g/hp/hr, 9.44ppmvd@15%O2 | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y
2014 | 635 | 0210012004 | Augusta Compressor Facility- Utica Gas Services, L.L.C. | 8034 Bane Rd NE | East Twp. | 44427 |  | Carroll | P012 | 1,775-hp Caterpillar G3606 Compressor Engine w/ Oxidation Catalyst | 2014-09-16 | Oxid. Cat. 3(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 4(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 5(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 6(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 7(Catalytic Converter): | Great Plains Analytical Services | 1775 Hp | 0.54 lbs/hr, 0.7 g/hp/hr, 60ppmvd@15%O2 | 1817 | 0.49 lbs/hr, 0.12 g/hp/hr, 11.91ppmvd@15%O2 | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y
2014 | 638 | 0210012004 | Augusta Compressor Facility- Utica Gas Services, L.L.C. | 8034 Bane Rd NE | East Twp. | 44427 |  | Carroll | P013 | 1,775-hp Caterpillar G3606 Compressor Engine w/ Oxidation Catalyst | 2014-09-16 | Oxid. Cat. 3(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 4(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 5(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 6(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 7(Catalytic Converter): | Great Plains Analytical Services | 1775 Hp | 0.54 lbs/hr, 0.7 g/hp/hr, 60ppmvd@15%O2 | 1780 | 0.47 lbs/hr, 0.12g/hp/hr, 11.59ppmvd@15%O2 | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y
2014 | 642 | 0210012004 | Augusta Compressor Facility- Utica Gas Services, L.L.C. | 8034 Bane Rd NE | East Twp. | 44427 |  | Carroll | P006 | 1,775-hp Caterpillar G3606 Compressor Engine w/ Oxidation Catalyst | 2014-09-17 | Oxid. Cat. 3(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 4(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 5(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 6(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 7(Catalytic Converter): | Great Plains Analytical Services | 1775 Hp | 0.54 lbs/hr, 0.7 g/hp/hr, 60ppmvd@15%O2 | 1831 | 0.36 lbs/hr, 0.09 g/hp/hr, 8.91 ppmvd@15%O2 | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y
2014 | 645 | 0210012004 | Augusta Compressor Facility- Utica Gas Services, L.L.C. | 8034 Bane Rd NE | East Twp. | 44427 |  | Carroll | P007 | 1,775-hp Caterpillar G3606 Compressor Engine w/ Oxidation Catalyst | 2014-09-17 | Oxid. Cat. 3(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 4(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 5(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 6(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 7(Catalytic Converter): | Great Plains Analytical Services | 1775 Hp | 0.54 lbs/hr, 0.7 g/hp/hr, 60ppmvd@15%O2 | 1839 | 0.34 lbs/hr, 0.08 g/hp/hr, 8.16 ppmvd@15%O2 | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y
2014 | 648 | 0210012004 | Augusta Compressor Facility- Utica Gas Services, L.L.C. | 8034 Bane Rd NE | East Twp. | 44427 |  | Carroll | P008 | 1,775-hp Caterpillar G3606 Compressor Engine w/ Oxidation Catalyst | 2014-09-17 | Oxid. Cat. 3(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 4(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 5(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 6(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 7(Catalytic Converter): | Great Plains Analytical Services | 1775 Hp | 0.54 lbs/hr, 0.7 g/hp/hr, 60ppmvd@15%O2 | 1809 | 0.27 lbs/hr, 0.06 g/hp/hr, 6.8 ppmvd@15%O2 | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y
2014 | 650 | 0210012004 | Augusta Compressor Facility- Utica Gas Services, L.L.C. | 8034 Bane Rd NE | East Twp. | 44427 |  | Carroll | P009 | 1,775-hp Caterpillar G3606 Compressor Engine w/ Oxidation Catalyst | 2014-09-17 | Oxid. Cat. 3(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 4(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 5(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 6(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 7(Catalytic Converter): | Great Plains Analytical Services | 1775 Hp | 0.54 lbs/hr, 0.7 g/hp/hr, 60ppmvd@15%O2 | 1788 | 0.41 lbs/hr, 0.10 g/hp/hr, 10.27ppmvd@15%O2 | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y
2014 | 652 | 0210012004 | Augusta Compressor Facility- Utica Gas Services, L.L.C. | 8034 Bane Rd NE | East Twp. | 44427 |  | Carroll | P010 | 1,775-hp Caterpillar G3606 Compressor Engine w/ Oxidation Catalyst | 2014-09-17 | Oxid. Cat. 3(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 4(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 5(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 6(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 7(Catalytic Converter): | Great Plains Analytical Services | 1775 Hp | 0.54 lbs/hr, 0.7 g/hp/hr, 60ppmvd@15%O2 | 1819 | 0.46 lbs/hr, 0.11 g/hp/hr, 11.11ppmvd@15%O2 | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y
2014 | 655 | 0210012004 | Augusta Compressor Facility- Utica Gas Services, L.L.C. | 8034 Bane Rd NE | East Twp. | 44427 |  | Carroll | P011 | 1,775-hp Caterpillar G3606 Compressor Engine w/ Oxidation Catalyst | 2014-09-17 | Oxid. Cat. 3(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 4(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 5(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 6(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 7(Catalytic Converter): | Great Plains Analytical Services | 1775 Hp | 0.54 lbs/hr, 0.7 g/hp/hr, 60ppmvd@15%O2 | 1821 | 0.35 lbs/hr, 0.08 g/hp/hr, 9.44ppmvd@15%O2 | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y
2014 | 659 | 0210012004 | Augusta Compressor Facility- Utica Gas Services, L.L.C. | 8034 Bane Rd NE | East Twp. | 44427 |  | Carroll | P012 | 1,775-hp Caterpillar G3606 Compressor Engine w/ Oxidation Catalyst | 2014-09-17 | Oxid. Cat. 3(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 4(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 5(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 6(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 7(Catalytic Converter): | Great Plains Analytical Services | 1775 Hp | 0.54 lbs/hr, 0.7 g/hp/hr, 60ppmvd@15%O2 | 1817 | 0.49 lbs/hr, 0.12 g/hp/hr, 11.91ppmvd@15%O2 | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y
2014 | 661 | 0210012004 | Augusta Compressor Facility- Utica Gas Services, L.L.C. | 8034 Bane Rd NE | East Twp. | 44427 |  | Carroll | P009 | 1,775-hp Caterpillar G3606 Compressor Engine w/ Oxidation Catalyst | 2014-09-18 | Oxid. Cat. 3(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 4(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 5(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 6(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 7(Catalytic Converter): | Great Plains Analytical Services | 1775 Hp | 0.54 lbs/hr, 0.7 g/hp/hr, 60ppmvd@15%O2 | 1788 | 0.41 lbs/hr, 0.10 g/hp/hr, 10.27ppmvd@15%O2 | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y
2014 | 666 | 0210012004 | Augusta Compressor Facility- Utica Gas Services, L.L.C. | 8034 Bane Rd NE | East Twp. | 44427 |  | Carroll | P010 | 1,775-hp Caterpillar G3606 Compressor Engine w/ Oxidation Catalyst | 2014-09-18 | Oxid. Cat. 3(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 4(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 5(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 6(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 7(Catalytic Converter): | Great Plains Analytical Services | 1775 Hp | 0.54 lbs/hr, 0.7 g/hp/hr, 60ppmvd@15%O2 | 1819 | 0.46 lbs/hr, 0.11 g/hp/hr, 11.11ppmvd@15%O2 | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y
2014 | 668 | 0210012004 | Augusta Compressor Facility- Utica Gas Services, L.L.C. | 8034 Bane Rd NE | East Twp. | 44427 |  | Carroll | P011 | 1,775-hp Caterpillar G3606 Compressor Engine w/ Oxidation Catalyst | 2014-09-18 | Oxid. Cat. 3(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 4(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 5(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 6(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 7(Catalytic Converter): | Great Plains Analytical Services | 1775 Hp | 0.54 lbs/hr, 0.7 g/hp/hr, 60ppmvd@15%O2 | 1821 | 0.35 lbs/hr, 0.08 g/hp/hr, 9.44ppmvd@15%O2 | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y
2014 | 670 | 0210012004 | Augusta Compressor Facility- Utica Gas Services, L.L.C. | 8034 Bane Rd NE | East Twp. | 44427 |  | Carroll | P012 | 1,775-hp Caterpillar G3606 Compressor Engine w/ Oxidation Catalyst | 2014-09-18 | Oxid. Cat. 3(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 4(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 5(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 6(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 7(Catalytic Converter): | Great Plains Analytical Services | 1775 Hp | 0.54 lbs/hr, 0.7 g/hp/hr, 60ppmvd@15%O2 | 1817 | 0.49 lbs/hr, 0.12 g/hp/hr, 11.91ppmvd@15%O2 | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y
2014 | 673 | 0210012004 | Augusta Compressor Facility- Utica Gas Services, L.L.C. | 8034 Bane Rd NE | East Twp. | 44427 |  | Carroll | P013 | 1,775-hp Caterpillar G3606 Compressor Engine w/ Oxidation Catalyst | 2014-09-18 | Oxid. Cat. 3(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 4(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 5(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 6(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 7(Catalytic Converter): | Great Plains Analytical Services | 1775 Hp | 0.54 lbs/hr, 0.7 g/hp/hr, 60ppmvd@15%O2 | 1780 | 0.47 lbs/hr, 0.12g/hp/hr, 11.59ppmvd@15%O2 | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y
2014 | 685 | 0210012022 | Chesapeake Exploration LLC - Krichbaum 2-14-5 Pad | County Highway 21 | Carrollton | 44615 |  | Carroll | P002 | Natural Gas Engines | 2014-03-04 | Catalyst | Alliance Source Testing, Inc. | 211 hp | 60 ppmvd @ 15% O2 | 168 HP | 1.1 ppmvd@15% O2 | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y
2014 | 692 | 0210012030 | Blue Racer Midstream LLC - Carroll Co Field Station #1 | Cobbler Rd NE | Carrollton | 44615 |  | Carroll | P001 | 1,340 HP Caterpillar G3516LE 4SLB Compressor Engine #1 with Oxidation Catalyst. Engine model year: 2013. | 2014-09-24 | CC-1(Catalytic Converter): Oxidation Catalyst 1; CC-2(Catalytic Converter): Oxidation Catalyst 2 | Air/ Compliance Consultants | 1380 Hp | 60 ppmvd @15%O2 & 0.7 g/bhp-hr | 1159 Hp or 83.9 % | 60 ppmvd @15%O2 & 0.7 g/bhp-hr | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y | Testing at a lower rate than 90% of Maximum was allowed because they were barely able to achieve each of these loads independently of the other engine, without taking the other engine down. 90% of the time the engines operate at 50% or lower and they have records to show that. Utilized Method 320 in conjunction with 25A to eliminate NMOC's
2014 | 694 | 0210012030 | Blue Racer Midstream LLC - Carroll Co Field Station #1 | Cobbler Rd NE | Carrollton | 44615 |  | Carroll | P002 | 1,340 HP Caterpillar G3516LE 4SLB Compressor Engine #2 with Oxidation Catalyst. Engine model year: 2013. | 2014-09-24 | CC-1(Catalytic Converter): Oxidation Catalyst 1; CC-2(Catalytic Converter): Oxidation Catalyst 2 | Air/ Compliance Consultants | 1380 Hp | 60 ppmvd @15%O2 & 0.7 g/bhp-hr | 1006 Hp or 72.8% | 60 ppmvd @15%O2 & 0.7 g/bhp-hr | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y | Testing at a lower rate than 90% of Maximum was allowed because they were barely able to achieve each of these loads independently of the other engine, without taking the other engine down. 90% of the time the engines operate at 50% or lower and they have records to show that. Utilized Method 320 in conjunction with 25A to eliminate NMOC's
2014 | 699 | 0210012038 | Chesapeake Exploration LLC - GF Farms 25-14-5 Pad | Steubenville Rd SE | Carrollton | 44615 |  | Carroll | P002 | Natural Gas Engines | 2014-11-12 | Catalyst | Alliance Source Testing | 174 Site Rate 211 Max | 60 ppmvd @ 15% O2 | 167 96% of site Rate | 0.4 ppmvd @ 15% O2 | 25A | Total Hydrocarbons | PASS | NA | Y
2014 | 702 | 0210012045 | Chesapeake Exploration LLC - Stanton 29-13-5 Pad | Canyon Road SE | Carrollton | 44615 |  | Carroll | P002 | One or multiple stationary natural gas-fired spark ignition (SI) internal combustion engines (ICE) with a combined total horsepower (HP) of no more than 1,800 HP for the site.* Includes 2007 and later model year engines manufactured after the applicable effective date identified in 40 CFR 60.4230(a)(3); and engines manufactured before the effective date of the NSPS, where compliance with the Part 60 Subpart JJJJ emissions standards for the same size engine can be met by retrofitting the engine with a control device and demonstrated through stack testing. | 2014-12-22 | Catalyst | Alliance Source Testing | 211 HP MAX 195 Site rate HP | NMEVOC-60 ppmvd @ 15% O2 | 175 Hp | 0.6 ppmvd @ 15% O2 | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y
2014 | 704 | 0210032001 | Chesapeake Exploration LLC - Edie 17-13-6 Pad | Amsterdam Road SW | Leesville | 44639 |  | Carroll | P002 | Natural Gas Engines | 2014-04-07 | Catalyst | Alliance Source Testing | 211 HP | 60 ppmvd@15%O2 | 155 HP or 73.5% of Max | 0.2 ppmvd@15%O2 | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y | Engine will require a retest if engine exceeds 10% of the tested rate.
2014 | 722 | 0215112002 | Chesapeake Exploration LLC - Pitts 22-14-4 Pad | Nature Rd SE (Carroll Rd) | Summitville | 43962 |  | Columbiana | P002 | Natural Gas Engines | 2014-12-22 | Catalyst | Alliance Source Testing | 211 HP MAX 195 Site rate HP | NMEVOC-60 ppmvd @ 15% O2 | 193 HP | 0.3 ppmvd @ 15% O2 | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y
2014 | 1008 | 0250002027 | Poland-CLL Production Facility | East of Cowden Rd and Moore Rd | Poland Twp. | 44436 |  | Mahoning | P002 | 1,340-hp Caterpillar G3516LE natural gas-fired compressor engine with oxidation catalyst, manufactured on 5/31/2007 | 2014-07-01 | Catalytic Co(Catalytic Converter): Catalytic Converter | Alliance Source Testing, Inc. | 1340 Hp | 60 ppmvd@15%O2 and 0.7 g/bhp-hr | 590 hp or 44.0% | 13.0 ppmvd @15%O2 and 0.19g/bhp-hr | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y | NSPS JJJJ Required test The facility was aware of the fact that they were well below the 90% threshold and are aware that they will have to test again if they run at a rate of 10% greater than the tested.
2014 | 1157 | 0285000366 | East Ohio Gas - Chippewa Station | 17045 Galehouse Road | Doylestown | 44230 |  | Wayne | B010 | 2,370 hp 4SLB SI ICE; CAT G3608 | 2014-06-02 | Engine 5 Converter(Catalytic Converter): Engine #5; Cat B010(Catalytic Converter): Catalytic Converter for B010, engine #6; Catalytic(Catalytic Converter): Engine 7 Catalytic converter | Air/Compliance Consultants, Inc. | 2370 Hp | 86 ppm@15% O2 or 1.0g/bhp-hr | 2315 Hp | 6.3 ppm@15% O2 and 0.076g/bhp-hr | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y | B009-2.8 Catalyst Pressure and 853 degF Catalyst temp, B010-2.16 Catalyst Pressure and 908 degF Catalyst temp, B014-1.0 Catalyst Pressure and 851 degF Catalyst Temperature
2014 | 1162 | 0285000366 | East Ohio Gas - Chippewa Station | 17045 Galehouse Road | Doylestown | 44230 |  | Wayne | B014 | 2,370 hp 4SLB SI ICE: CAT 3608 w/catalyst | 2014-06-02 | Engine 5 Converter(Catalytic Converter): Engine #5; Cat B010(Catalytic Converter): Catalytic Converter for B010, engine #6; Catalytic(Catalytic Converter): Engine 7 Catalytic converter | Air/Compliance Consultants, Inc. | 2370 Hp | 60 ppm @15%O2 or 0.7 g/bhp-hr | 2362 Hp | 7.0ppm @15%O2 and 0.084g/bhp-hr | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y | B009-2.8 Catalyst Pressure and 853 degF Catalyst temp, B010-2.16 Catalyst Pressure and 908 degF Catalyst temp, B014-1.0 Catalyst Pressure and 851 degF Catalyst Temperature
2014 | 1166 | 0285000366 | East Ohio Gas - Chippewa Station | 17045 Galehouse Road | Doylestown | 44230 |  | Wayne | B010 | 2,370 hp 4SLB SI ICE; CAT G3608 | 2014-06-03 | Engine 5 Converter(Catalytic Converter): Engine #5; Cat B010(Catalytic Converter): Catalytic Converter for B010, engine #6; Catalytic(Catalytic Converter): Engine 7 Catalytic converter | Air/Compliance Consultants, Inc. | 2370 Hp | 86 ppm@15% O2 or 1.0g/bhp-hr | 2315 Hp | 6.3 ppm@15% O2 and 0.076g/bhp-hr | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y | B009-2.8 Catalyst Pressure and 853 degF Catalyst temp, B010-2.16 Catalyst Pressure and 908 degF Catalyst temp, B014-1.0 Catalyst Pressure and 851 degF Catalyst Temperature
2014 | 1168 | 0285000366 | East Ohio Gas - Chippewa Station | 17045 Galehouse Road | Doylestown | 44230 |  | Wayne | B014 | 2,370 hp 4SLB SI ICE: CAT 3608 w/catalyst | 2014-06-03 | Engine 5 Converter(Catalytic Converter): Engine #5; Cat B010(Catalytic Converter): Catalytic Converter for B010, engine #6; Catalytic(Catalytic Converter): Engine 7 Catalytic converter | Air/Compliance Consultants, Inc. | 2370 Hp | 60 ppm @15%O2 or 0.7 g/bhp-hr | 2362 Hp | 7.0ppm @15%O2 and 0.084g/bhp-hr | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y | B009-2.8 Catalyst Pressure and 853 degF Catalyst temp, B010-2.16 Catalyst Pressure and 908 degF Catalyst temp, B014-1.0 Catalyst Pressure and 851 degF Catalyst Temperature
2014 | 1171 | 0285000388 | East Ohio Gas Company - Paint | STATE RTE 250 | Wooster | 44624 |  | Wayne | B002 | Natural gas fired Internal Combustion Engine with max input capacity of 11.9 MMBtu/hr - Caterpillar G3516TALE with 1340 HP, 4-stroke, selective catalytic reduction (SCR) | 2014-07-26 | Three way Catalyst; CatOx(Catalytic Converter): Catalytic oxidizer for Engine 2 | Air/Compliance Consultants | 1340 HP | 1.0 g/bhp-hr or 86ppmvd@ 15% O2 | 1207 Hp or 90.1% | 0.13 g/bhp-hr or 9.6 ppmvd@ 15% O2 | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y
2014 | 1426 | 0630005012 | Gulfport Energy- Groh Well Pad | 19667 Cadiz Rd | Quaker City | 42773 |  | Guernsey | P002 | One 50-hp Zenith ZPP416 and one 203-hp Caterpillar G3306B NA natural gas-fired engines for compressors. One or multiple stationary natural gas-fired spark ignition (SI) internal combustion engines (ICE) wiht a combined total horsepower (HP) or no more than 1,800 HP for the site. | 2014-08-07 | none | BCMJ Controls Inc. | 145 Hp | 1.0 g/Hp-hr | 128 Hp | 0.03 g/Hp-hr | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y
2014 | 1430 | 0630005024 | Gulfport Energy Corporation - Karen 23-9-7 Pad | Oxford Rd | Quaker City | 43773 |  | Guernsey | P002 | One or multiple stationary natural gas-fired spark ignition (SI) internal combustion engines (ICE) with a combined total horsepower (HP) of no more than 1,800 HP for the site. Includes 2007 and later model year engines manufactured after the applicable effective date identified in 40 CFR 60.4230(a)(3) and engines manufactured before the NSPS effective date where compliance with the Part 60 Subpart JJJJ emissions standards for the same size engine can be demonstrated through stack testing. | 2014-08-08 | catalyst | BCMJ Controls, Inc | 118 Hp | 1.0 g/Hp-hr | 52 Hp | 0.22 g/Hp-hr | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y
2014 | 1431 | 0630005024 | Gulfport Energy Corporation - Karen 23-9-7 Pad | Oxford Rd | Quaker City | 43773 |  | Guernsey | P002 | One or multiple stationary natural gas-fired spark ignition (SI) internal combustion engines (ICE) with a combined total horsepower (HP) of no more than 1,800 HP for the site. Includes 2007 and later model year engines manufactured after the applicable effective date identified in 40 CFR 60.4230(a)(3) and engines manufactured before the NSPS effective date where compliance with the Part 60 Subpart JJJJ emissions standards for the same size engine can be demonstrated through stack testing. | 2014-12-04 | none | Great Plains Analytical Services | 116 Hp | 1.0 g/Hp-hr | 63 Hp | 0.174 g/Hp-hr | 25B | VOC - Volatile Organic Compounds | PASS | NA | Y | method 25B not used. methods 1-3a and ASTM 6348-03 FTIR
2014 | 1435 | 0656005010 | Dominion East Ohio - Switzerland Compressor Station | German Ridge Road | Switzerland Twp. | 43942 |  | Monroe | P001 | 3550 Hp Natural gas-fired (4SLB) Caterpillar model 3612 LE DM5309-06 compressor engines equipped with catalytic reduction (three-way). | 2014-11-11 | catalytic reduction | Air Compliance Consultants | 3550 Hp | 0.26 g/Hp-hr | 3408 Hp | 0.089 g/Hp-hr | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y
2014 | 1438 | 0656005010 | Dominion East Ohio - Switzerland Compressor Station | German Ridge Road | Switzerland Twp. | 43942 |  | Monroe | P003 | 3550 Hp Natural gas-fired (4SLB) Caterpillar model 3612 LE DM5309-06 compressor engines equipped with catalytic reduction (three-way). | 2014-11-11 | catalytic reduction | Air Compliance Consultants | 3550 Hp | 0.26 g/Hp-hr | 3242 Hp | 0.066 g/Hp-hr | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y
2014 | 1627 | 0607005015 | Morristown Compressor Station | Between Hwys 100 and 203 | Union Twp. | 43713 |  | Belmont | P001 | compressor engine | 2014-11-20 | CC001(Catalytic Converter): Compressor Engine #1 Catalytic Converter; CC002(Catalytic Converter): Compressor Engine #2 Catalytic Converter; CC003(Catalytic Converter): Compressor Engine #3 Catalytic Converter; CC004(Catalytic Converter): Compressor Engine | Air Hygiene, Inc. | 2,370 hp | 0.70 g/hp-hr | 2,236 hp | 0.14 g/hp-hr | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y
2014 | 1632 | 0607005015 | Morristown Compressor Station | Between Hwys 100 and 203 | Union Twp. | 43713 |  | Belmont | P002 | compressor engine | 2014-11-20 | CC001(Catalytic Converter): Compressor Engine #1 Catalytic Converter; CC002(Catalytic Converter): Compressor Engine #2 Catalytic Converter; CC003(Catalytic Converter): Compressor Engine #3 Catalytic Converter; CC004(Catalytic Converter): Compressor Engine | Air Hygiene, Inc. | 2,370 hp | 0.70 g/hp-hr | 2,299 hp | 0.14 g/hp-hr | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y
2014 | 1634 | 0607005015 | Morristown Compressor Station | Between Hwys 100 and 203 | Union Twp. | 43713 |  | Belmont | P003 | compressor engine | 2014-11-20 | CC001(Catalytic Converter): Compressor Engine #1 Catalytic Converter; CC002(Catalytic Converter): Compressor Engine #2 Catalytic Converter; CC003(Catalytic Converter): Compressor Engine #3 Catalytic Converter; CC004(Catalytic Converter): Compressor Engine | Air Hygiene, Inc. | 2,370 hp | 0.70 g/hp-hr | 2,236 hp | 0.12 g/hp-hr | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y
2014 | 1638 | 0607005015 | Morristown Compressor Station | Between Hwys 100 and 203 | Union Twp. | 43713 |  | Belmont | P004 | compressor engine | 2014-11-20 | CC001(Catalytic Converter): Compressor Engine #1 Catalytic Converter; CC002(Catalytic Converter): Compressor Engine #2 Catalytic Converter; CC003(Catalytic Converter): Compressor Engine #3 Catalytic Converter; CC004(Catalytic Converter): Compressor Engine | Air Hygiene, Inc. | 2,370 hp | 0.70 g/hp-hr | 2,283 hp | 0.17 g/hp-hr | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y
2014 | 1641 | 0607005015 | Morristown Compressor Station | Between Hwys 100 and 203 | Union Twp. | 43713 |  | Belmont | P005 | compressor engine | 2014-11-20 | CC001(Catalytic Converter): Compressor Engine #1 Catalytic Converter; CC002(Catalytic Converter): Compressor Engine #2 Catalytic Converter; CC003(Catalytic Converter): Compressor Engine #3 Catalytic Converter; CC004(Catalytic Converter): Compressor Engine | Air Hygiene, Inc. | 2,370 hp | 0.70 g/hp-hr | 2,212 hp | 0.21 g/hp-hr | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y
2014 | 1644 | 0607005015 | Morristown Compressor Station | Between Hwys 100 and 203 | Union Twp. | 43713 |  | Belmont | P006 | compressor engine | 2014-11-20 | CC001(Catalytic Converter): Compressor Engine #1 Catalytic Converter; CC002(Catalytic Converter): Compressor Engine #2 Catalytic Converter; CC003(Catalytic Converter): Compressor Engine #3 Catalytic Converter; CC004(Catalytic Converter): Compressor Engine | Air Hygiene, Inc. | 2,370 hp | 0.70 g/hp-hr | 2,140 hp | 0.16 g/hp-hr | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y
2014 | 1646 | 0607005015 | Morristown Compressor Station | Between Hwys 100 and 203 | Union Twp. | 43713 |  | Belmont | P001 | compressor engine | 2014-11-21 | CC001(Catalytic Converter): Compressor Engine #1 Catalytic Converter; CC002(Catalytic Converter): Compressor Engine #2 Catalytic Converter; CC003(Catalytic Converter): Compressor Engine #3 Catalytic Converter; CC004(Catalytic Converter): Compressor Engine | Air Hygiene, Inc. | 2,370 hp | 0.70 g/hp-hr | 2,236 hp | 0.14 g/hp-hr | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y
2014 | 1648 | 0607005015 | Morristown Compressor Station | Between Hwys 100 and 203 | Union Twp. | 43713 |  | Belmont | P002 | compressor engine | 2014-11-21 | CC001(Catalytic Converter): Compressor Engine #1 Catalytic Converter; CC002(Catalytic Converter): Compressor Engine #2 Catalytic Converter; CC003(Catalytic Converter): Compressor Engine #3 Catalytic Converter; CC004(Catalytic Converter): Compressor Engine | Air Hygiene, Inc. | 2,370 hp | 0.70 g/hp-hr | 2,299 hp | 0.14 g/hp-hr | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y
2014 | 1653 | 0607005015 | Morristown Compressor Station | Between Hwys 100 and 203 | Union Twp. | 43713 |  | Belmont | P003 | compressor engine | 2014-11-21 | CC001(Catalytic Converter): Compressor Engine #1 Catalytic Converter; CC002(Catalytic Converter): Compressor Engine #2 Catalytic Converter; CC003(Catalytic Converter): Compressor Engine #3 Catalytic Converter; CC004(Catalytic Converter): Compressor Engine | Air Hygiene, Inc. | 2,370 hp | 0.70 g/hp-hr | 2,236 hp | 0.12 g/hp-hr | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y
2014 | 1654 | 0607005015 | Morristown Compressor Station | Between Hwys 100 and 203 | Union Twp. | 43713 |  | Belmont | P004 | compressor engine | 2014-11-21 | CC001(Catalytic Converter): Compressor Engine #1 Catalytic Converter; CC002(Catalytic Converter): Compressor Engine #2 Catalytic Converter; CC003(Catalytic Converter): Compressor Engine #3 Catalytic Converter; CC004(Catalytic Converter): Compressor Engine | Air Hygiene, Inc. | 2,370 hp | 0.70 g/hp-hr | 2,283 hp | 0.17 g/hp-hr | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y
2014 | 1657 | 0607005015 | Morristown Compressor Station | Between Hwys 100 and 203 | Union Twp. | 43713 |  | Belmont | P005 | compressor engine | 2014-11-21 | CC001(Catalytic Converter): Compressor Engine #1 Catalytic Converter; CC002(Catalytic Converter): Compressor Engine #2 Catalytic Converter; CC003(Catalytic Converter): Compressor Engine #3 Catalytic Converter; CC004(Catalytic Converter): Compressor Engine | Air Hygiene, Inc. | 2,370 hp | 0.70 g/hp-hr | 2,212 hp | 0.21 g/hp-hr | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y
2014 | 1661 | 0607005015 | Morristown Compressor Station | Between Hwys 100 and 203 | Union Twp. | 43713 |  | Belmont | P006 | compressor engine | 2014-11-21 | CC001(Catalytic Converter): Compressor Engine #1 Catalytic Converter; CC002(Catalytic Converter): Compressor Engine #2 Catalytic Converter; CC003(Catalytic Converter): Compressor Engine #3 Catalytic Converter; CC004(Catalytic Converter): Compressor Engine | Air Hygiene, Inc. | 2,370 hp | 0.70 g/hp-hr | 2,140 hp | 0.16 g/hp-hr | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y
2014 | 1663 | 0607015001 | Tri-County Compressor Station (MarkWest / Ohio Oil Gath | North of intersection of Hwy 379 and Town | Barnesville | 43713 |  | Belmont | P003 | Compressor Engine #3 - 1980 HP (15.43 MMBtu/hr) Waukesha P9390 - natural gas-fired four-stroke rich burn internal combustion engine equipped with a three-way oxidation catalyst controlling CH2O, CO, NOx, & VOCs by 80, 97, 98.5 & 66 percent respectively | 2014-11-11 | CC002(Catalytic Converter): Compressor Engine #2 - 3-way Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - 3-way Catalyst; CC004(Catalytic Converter): Compressor Engine #4 - 3-way Catalyst; CC005(Catalytic Converter): Compressor Engine #5 - 3-w | Air Hygiene, Inc | 1,980 hp | 0.7 g/hp-hr | 1,526 hp | 0 g/hp-hr | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y
2014 | 1666 | 0607015001 | Tri-County Compressor Station (MarkWest / Ohio Oil Gath | North of intersection of Hwy 379 and Town | Barnesville | 43713 |  | Belmont | P004 | Compressor Engine #4 - 1980 HP (15.43 MMBtu/hr) Waukesha P9390 - natural gas-fired four-stroke rich burn internal combustion engine equipped with a three-way oxidation catalyst controlling CH2O, CO, NOx, & VOCs by 80, 97, 98.5 & 66 percent respectively | 2014-11-11 | CC002(Catalytic Converter): Compressor Engine #2 - 3-way Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - 3-way Catalyst; CC004(Catalytic Converter): Compressor Engine #4 - 3-way Catalyst; CC005(Catalytic Converter): Compressor Engine #5 - 3-w | Air Hygiene, Inc | 1,980 hp | 0.7 g/hp-hr | 1,525 hp | 0 g/hp-hr | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y
2014 | 1669 | 0607015001 | Tri-County Compressor Station (MarkWest / Ohio Oil Gath | North of intersection of Hwy 379 and Town | Barnesville | 43713 |  | Belmont | P005 | Compressor Engine #5 - 1980 HP (15.43 MMBtu/hr) Waukesha P9390 - natural gas-fired four-stroke rich burn internal combustion engine equipped with a three-way oxidation catalyst controlling CH2O, CO, NOx, & VOCs by 80, 97, 98.5 & 66 percent respectively | 2014-11-11 | CC002(Catalytic Converter): Compressor Engine #2 - 3-way Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - 3-way Catalyst; CC004(Catalytic Converter): Compressor Engine #4 - 3-way Catalyst; CC005(Catalytic Converter): Compressor Engine #5 - 3-w | Air Hygiene, Inc | 1,980 hp | 0.7 g/hp-hr | 1,482 hp | 0 g/hp-hr | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y
2014 | 1672 | 0607015001 | Tri-County Compressor Station (MarkWest / Ohio Oil Gath | North of intersection of Hwy 379 and Town | Barnesville | 43713 |  | Belmont | P006 | Compressor Engine #6 - 1980 HP (15.43 MMBtu/hr) Waukesha P9390 - natural gas-fired four-stroke rich burn internal combustion engine equipped with a three-way oxidation catalyst controlling CH2O, CO, NOx, & VOCs by 80, 97, 98.5 & 66 percent respectively | 2014-11-11 | CC002(Catalytic Converter): Compressor Engine #2 - 3-way Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - 3-way Catalyst; CC004(Catalytic Converter): Compressor Engine #4 - 3-way Catalyst; CC005(Catalytic Converter): Compressor Engine #5 - 3-w | Air Hygiene, Inc | 1,980 hp | 0.7 g/hp-hr | 1,794 hp | 0 g/hp-hr | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y
2014 | 1676 | 0607015001 | Tri-County Compressor Station (MarkWest / Ohio Oil Gath | North of intersection of Hwy 379 and Town | Barnesville | 43713 |  | Belmont | P003 | Compressor Engine #3 - 1980 HP (15.43 MMBtu/hr) Waukesha P9390 - natural gas-fired four-stroke rich burn internal combustion engine equipped with a three-way oxidation catalyst controlling CH2O, CO, NOx, & VOCs by 80, 97, 98.5 & 66 percent respectively | 2014-11-12 | CC002(Catalytic Converter): Compressor Engine #2 - 3-way Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - 3-way Catalyst; CC004(Catalytic Converter): Compressor Engine #4 - 3-way Catalyst; CC005(Catalytic Converter): Compressor Engine #5 - 3-w | Air Hygiene, Inc | 1,980 hp | 0.7 g/hp-hr | 1,526 hp | 0 g/hp-hr | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y
2014 | 1678 | 0607015001 | Tri-County Compressor Station (MarkWest / Ohio Oil Gath | North of intersection of Hwy 379 and Town | Barnesville | 43713 |  | Belmont | P004 | Compressor Engine #4 - 1980 HP (15.43 MMBtu/hr) Waukesha P9390 - natural gas-fired four-stroke rich burn internal combustion engine equipped with a three-way oxidation catalyst controlling CH2O, CO, NOx, & VOCs by 80, 97, 98.5 & 66 percent respectively | 2014-11-12 | CC002(Catalytic Converter): Compressor Engine #2 - 3-way Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - 3-way Catalyst; CC004(Catalytic Converter): Compressor Engine #4 - 3-way Catalyst; CC005(Catalytic Converter): Compressor Engine #5 - 3-w | Air Hygiene, Inc | 1,980 hp | 0.7 g/hp-hr | 1,525 hp | 0 g/hp-hr | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y
2014 | 1683 | 0607015001 | Tri-County Compressor Station (MarkWest / Ohio Oil Gath | North of intersection of Hwy 379 and Town | Barnesville | 43713 |  | Belmont | P005 | Compressor Engine #5 - 1980 HP (15.43 MMBtu/hr) Waukesha P9390 - natural gas-fired four-stroke rich burn internal combustion engine equipped with a three-way oxidation catalyst controlling CH2O, CO, NOx, & VOCs by 80, 97, 98.5 & 66 percent respectively | 2014-11-12 | CC002(Catalytic Converter): Compressor Engine #2 - 3-way Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - 3-way Catalyst; CC004(Catalytic Converter): Compressor Engine #4 - 3-way Catalyst; CC005(Catalytic Converter): Compressor Engine #5 - 3-w | Air Hygiene, Inc | 1,980 hp | 0.7 g/hp-hr | 1,482 hp | 0 g/hp-hr | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y
2014 | 1685 | 0607015001 | Tri-County Compressor Station (MarkWest / Ohio Oil Gath | North of intersection of Hwy 379 and Town | Barnesville | 43713 |  | Belmont | P006 | Compressor Engine #6 - 1980 HP (15.43 MMBtu/hr) Waukesha P9390 - natural gas-fired four-stroke rich burn internal combustion engine equipped with a three-way oxidation catalyst controlling CH2O, CO, NOx, & VOCs by 80, 97, 98.5 & 66 percent respectively | 2014-11-12 | CC002(Catalytic Converter): Compressor Engine #2 - 3-way Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - 3-way Catalyst; CC004(Catalytic Converter): Compressor Engine #4 - 3-way Catalyst; CC005(Catalytic Converter): Compressor Engine #5 - 3-w | Air Hygiene, Inc | 1,980 hp | 0.7 g/hp-hr | 1,794 hp | 0 g/hp-hr | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y
2014 | 1689 | 0607015001 | Tri-County Compressor Station (MarkWest / Ohio Oil Gath | North of intersection of Hwy 379 and Town | Barnesville | 43713 |  | Belmont | P003 | Compressor Engine #3 - 1980 HP (15.43 MMBtu/hr) Waukesha P9390 - natural gas-fired four-stroke rich burn internal combustion engine equipped with a three-way oxidation catalyst controlling CH2O, CO, NOx, & VOCs by 80, 97, 98.5 & 66 percent respectively | 2014-11-29 | CC002(Catalytic Converter): Compressor Engine #2 - 3-way Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - 3-way Catalyst; CC004(Catalytic Converter): Compressor Engine #4 - 3-way Catalyst; CC005(Catalytic Converter): Compressor Engine #5 - 3-w | Air Hygiene, Inc | 1,980 hp | 0.7 g/hp-hr | 1,526 hp | 0 g/hp-hr | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y
2014 | 1690 | 0607015001 | Tri-County Compressor Station (MarkWest / Ohio Oil Gath | North of intersection of Hwy 379 and Town | Barnesville | 43713 |  | Belmont | P004 | Compressor Engine #4 - 1980 HP (15.43 MMBtu/hr) Waukesha P9390 - natural gas-fired four-stroke rich burn internal combustion engine equipped with a three-way oxidation catalyst controlling CH2O, CO, NOx, & VOCs by 80, 97, 98.5 & 66 percent respectively | 2014-11-29 | CC002(Catalytic Converter): Compressor Engine #2 - 3-way Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - 3-way Catalyst; CC004(Catalytic Converter): Compressor Engine #4 - 3-way Catalyst; CC005(Catalytic Converter): Compressor Engine #5 - 3-w | Air Hygiene, Inc | 1,980 hp | 0.7 g/hp-hr | 1,525 hp | 0 g/hp-hr | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y
2014 | 1694 | 0607015001 | Tri-County Compressor Station (MarkWest / Ohio Oil Gath | North of intersection of Hwy 379 and Town | Barnesville | 43713 |  | Belmont | P005 | Compressor Engine #5 - 1980 HP (15.43 MMBtu/hr) Waukesha P9390 - natural gas-fired four-stroke rich burn internal combustion engine equipped with a three-way oxidation catalyst controlling CH2O, CO, NOx, & VOCs by 80, 97, 98.5 & 66 percent respectively | 2014-11-29 | CC002(Catalytic Converter): Compressor Engine #2 - 3-way Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - 3-way Catalyst; CC004(Catalytic Converter): Compressor Engine #4 - 3-way Catalyst; CC005(Catalytic Converter): Compressor Engine #5 - 3-w | Air Hygiene, Inc | 1,980 hp | 0.7 g/hp-hr | 1,482 hp | 0 g/hp-hr | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y
2014 | 1697 | 0607015001 | Tri-County Compressor Station (MarkWest / Ohio Oil Gath | North of intersection of Hwy 379 and Town | Barnesville | 43713 |  | Belmont | P006 | Compressor Engine #6 - 1980 HP (15.43 MMBtu/hr) Waukesha P9390 - natural gas-fired four-stroke rich burn internal combustion engine equipped with a three-way oxidation catalyst controlling CH2O, CO, NOx, & VOCs by 80, 97, 98.5 & 66 percent respectively | 2014-11-29 | CC002(Catalytic Converter): Compressor Engine #2 - 3-way Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - 3-way Catalyst; CC004(Catalytic Converter): Compressor Engine #4 - 3-way Catalyst; CC005(Catalytic Converter): Compressor Engine #5 - 3-w | Air Hygiene, Inc | 1,980 hp | 0.7 g/hp-hr | 1,794 hp | 0 g/hp-hr | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y
2014 | 1734 | 0634005027 | Arrowhead Compressor Station | E of Clements Rd and S of Jockey Hollow | Athens Twp. | 43977 |  | Harrison | P006 | Compressor Engine #3 - Caterpillar G3608 - natural gas fired four-stroke, lean burn internal combustion engine rated at an operating capacity of 2,370 horsepower equipped with a catalytic convertor. | 2014-05-01 | CC003(Catalytic Converter): Compressor Engine #3 Catalytic Convertor | Air Hygiene | 2,370 hp | 0.28 g/hp-hr | 2,212 hp | 0.38 g/hp-hr | 25A | VOC - Volatile Organic Compounds | FAIL | NA | Y
2014 | 1736 | 0634005027 | Arrowhead Compressor Station | E of Clements Rd and S of Jockey Hollow | Athens Twp. | 43977 |  | Harrison | P007 | Compressor Engine #4 - Caterpillar G3608 - natural gas fired four-stroke, lean burn internal combustion engine rated at an operating capacity of 2,370 horsepower equipped with a catalytic convertor | 2014-06-18 | CC004(Catalytic Converter): Compressor Engine #4 Catalytic Convertor | Air Hygiene | 2,370 hp | 0.28 g/hp-hr | 2,165 hp | 0.44 g/hp-hr | 25A | VOC - Volatile Organic Compounds | FAIL | NA | Y
2014 | 1740 | 0634005027 | Arrowhead Compressor Station | E of Clements Rd and S of Jockey Hollow | Athens Twp. | 43977 |  | Harrison | P006 | Compressor Engine #3 - Caterpillar G3608 - natural gas fired four-stroke, lean burn internal combustion engine rated at an operating capacity of 2,370 horsepower equipped with a catalytic convertor. | 2014-09-12 | CC003(Catalytic Converter): Compressor Engine #3 Catalytic Convertor; CC004(Catalytic Converter): Compressor Engine #4 Catalytic Convertor | Air Hygeine International | 2370 Hp | 0.28 g/Hp-hr | 2243 Hp | 0.18 g/Hp-hr | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y
2014 | 1743 | 0634005027 | Arrowhead Compressor Station | E of Clements Rd and S of Jockey Hollow | Athens Twp. | 43977 |  | Harrison | P007 | Compressor Engine #4 - Caterpillar G3608 - natural gas fired four-stroke, lean burn internal combustion engine rated at an operating capacity of 2,370 horsepower equipped with a catalytic convertor | 2014-09-12 | CC003(Catalytic Converter): Compressor Engine #3 Catalytic Convertor; CC004(Catalytic Converter): Compressor Engine #4 Catalytic Convertor | Air Hygeine International | 2370 Hp | 0.28 g/Hp-hr | 2185 Hp | 0.18 g/Hp-hr | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y
2014 | 1745 | 0634005027 | Arrowhead Compressor Station | E of Clements Rd and S of Jockey Hollow | Athens Twp. | 43977 |  | Harrison | P008 | Compressor Engine #5 - Caterpillar G3608 - natural gas fired four-stroke, lean burn internal combustion engine rated at an operating capacity of 2,370 horsepower equipped with a catalytic convertor | 2014-11-20 | CC005(Catalytic Converter): Compressor Engine #5 Catalytic Convertor | Air Hygiene, Inc. | 2370 Hp | 0.70 g/hp-hr | 2209 Hp | 0.20 g/Hp-hr | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y
2014 | 1750 | 0634005027 | Arrowhead Compressor Station | E of Clements Rd and S of Jockey Hollow | Athens Twp. | 43977 |  | Harrison | P009 | Compressor Engine #6 - Caterpillar G3608 - natural gas fired four-stroke, lean burn internal combustion engine rated at an operating capacity of 2,370 horsepower equipped with a catalytic convertor | 2014-11-20 | CC006(Catalytic Converter): Compressor Engine #6 Catalytic Convertor; CC07(Catalytic Converter): Compressor Engine #7 Catalytic Convertor; CC008(Catalytic Converter): Compressor Engine #8 Catalytic Convertor | Air Hygiene Inc. | 2370 Hp | 0.7 g/Hp-hr | 2207 Hp | 0.18 g/Hp-hr | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y
2014 | 1753 | 0634005027 | Arrowhead Compressor Station | E of Clements Rd and S of Jockey Hollow | Athens Twp. | 43977 |  | Harrison | P010 | Compressor Engine #7 - Caterpillar G3608 - natural gas fired four-stroke, lean burn internal combustion engine rated at an operating capacity of 2,370 horsepower equipped with a catalytic convertor | 2014-11-20 | CC006(Catalytic Converter): Compressor Engine #6 Catalytic Convertor; CC07(Catalytic Converter): Compressor Engine #7 Catalytic Convertor; CC008(Catalytic Converter): Compressor Engine #8 Catalytic Convertor | Air Hygiene Inc. | 2370 Hp | 0.7 g/Hp-hr | 2252 Hp | 0.18 g/Hp-hr | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y
2014 | 1754 | 0634005027 | Arrowhead Compressor Station | E of Clements Rd and S of Jockey Hollow | Athens Twp. | 43977 |  | Harrison | P011 | Compressor Engine #8 - Caterpillar G3608 - natural gas fired four-stroke, lean burn internal combustion engine rated at an operating capacity of 2,370 horsepower equipped with a catalytic convertor | 2014-11-20 | CC006(Catalytic Converter): Compressor Engine #6 Catalytic Convertor; CC07(Catalytic Converter): Compressor Engine #7 Catalytic Convertor; CC008(Catalytic Converter): Compressor Engine #8 Catalytic Convertor | Air Hygiene Inc. | 2370 Hp | 0.7 g/Hp-hr | 2197 Hp | 0.08 g/Hp-hr | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y
2014 | 1760 | 0634005029 | Cadiz Gas Plant | 43071 Industrial Park Rd | Cadiz | 43907 |  | Harrison | P007 | Compressor Engine #7 - 4735 HP Caterpillar G3616 engine (CM-1206-7) - natural gas-fired four-stroke lean burn internal combustion engine equipped with an oxidation catalyst controlling CO, VOC and formaldehyde 95, 75, and 90 percent respectively. | 2014-12-19 | CC007(Catalytic Converter): oxidation catalyst; CC008(Catalytic Converter): oxidation catalyst | Air Hygiene | 4,735 hp | 0.28 g/hp-hr | 4,376 hp | 0.006 g/hp-hr | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y
2014 | 1762 | 0634005029 | Cadiz Gas Plant | 43071 Industrial Park Rd | Cadiz | 43907 |  | Harrison | P008 | Compressor Engine #8 - 4735 HP Caterpillar G3616 engine (CM-1206-8) - natural gas-fired four-stroke lean burn internal combustion engine equipped with an oxidation catalyst controlling CO, VOC and formaldehyde 95, 75, and 90 percent respectively. | 2014-12-19 | CC007(Catalytic Converter): oxidation catalyst; CC008(Catalytic Converter): oxidation catalyst | Air Hygiene | 4,735 hp | 0.28 g/hp-hr | 4,378 hp | 0.001 g/hp-hr | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y
2014 | 1766 | 0634005033 | Harrison West Compressor Station | Possum Hollow Road | Freeport | 43973 |  | Harrison | P004 | Compressor Engine #4 - 1980 HP (15.43 MMBtu/hr) Waukesha P9390 - natural gas-fired four-stroke rich burn internal combustion engine equipped with a three-way oxidation catalyst controlling CH2O, CO, NOx, & VOCs by 80, 97, 98.5 & 66 percent respectively | 2014-04-08 | CC004(Catalytic Converter): Compressor Engine #4 - 3-way Catalyst | Air Hygiene International | 1,980 hp | 0.7 g/hp-hr | 1,782 hp | 0.001 g/hp-hr | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y
2014 | 1767 | 0634005033 | Harrison West Compressor Station | Possum Hollow Road | Freeport | 43973 |  | Harrison | P005 | Compressor Engine #5 - 1980 HP (15.43 MMBtu/hr) Waukesha P9390 - natural gas-fired four-stroke rich burn internal combustion engine equipped with a three-way oxidation catalyst controlling CH2O, CO, NOx, & VOCs by 80, 97, 98.5 & 66 percent respectively | 2014-04-08 | CC005(Catalytic Converter): Compressor Engine #5 - 3-way Catalyst | Air Hygiene International | 1,980 hp | 0.7 gr/hp-hr | 1,868 hp | 0.001 g/hp-hr | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y
2014 | 1770 | 0634005033 | Harrison West Compressor Station | Possum Hollow Road | Freeport | 43973 |  | Harrison | P006 | Compressor Engine #6 - 1980 HP (15.43 MMBtu/hr) Waukesha P9390 - natural gas-fired four-stroke rich burn internal combustion engine equipped with a three-way oxidation catalyst controlling CH2O, CO, NOx, & VOCs by 80, 97, 98.5 & 66 percent respectively | 2014-04-08 | CC006(Catalytic Converter): Compressor Engine #6 - 3-way Catalyst | Air Hygiene International | 1,980 hp | 0.7 g/hp-hr | 1,840 hp | 0.001 g/hp-hr | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y
2014 | 1773 | 0634005033 | Harrison West Compressor Station | Possum Hollow Road | Freeport | 43973 |  | Harrison | P001 | Compressor Engine #1 - 1480 HP (11.39 MMBtu/hr) Waukesha L7042 - natural gas-fired four-stroke rich burn internal combustion engine equipped with a three-way oxidation catalyst controlling CH2O, CO, NOx, & VOCs by 80, 97, 98.5 & 66 percent respectively | 2014-04-09 | CC001(Catalytic Converter): Compressor Engine #1 - 3-way Catalyst | Air Hygiene International | 1,480 hp | 0.7 g/hp-hr | 1,406 hp | 0.087 g/hp-hr | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y
2014 | 1778 | 0634005033 | Harrison West Compressor Station | Possum Hollow Road | Freeport | 43973 |  | Harrison | P002 | Compressor Engine #2 - 1480 HP (11.39 MMBtu/hr) Waukesha L7042 - natural gas-fired four-stroke rich burn internal combustion engine equipped with a three-way oxidation catalyst controlling CH2O, CO, NOx, & VOCs by 80, 97, 98.5 & 66 percent respectively | 2014-04-09 | CC002(Catalytic Converter): Compressor Engine #2 - 3-way Catalyst | Air Hygiene International | 1,480 hp | 0.7 g/hp-hr | 1,881 hp | 0.015 g/hp-hr | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y
2014 | 1781 | 0634005033 | Harrison West Compressor Station | Possum Hollow Road | Freeport | 43973 |  | Harrison | P007 | Compressor Engine #7 - 1980 HP (15.43 MMBtu/hr) Waukesha P9390 - natural gas-fired four-stroke rich burn internal combustion engine equipped with a three-way oxidation catalyst controlling CH2O, CO, NOx, & VOCs by 80, 97, 98.5 & 66 percent respectively | 2014-04-09 | CC007(Catalytic Converter): Compressor Engine #7 - 3-way Catalyst | Air Hygiene International | 1,980 hp | 0.7 g/hp-hr | 1,822 hp | 0.004 g/hp-hr | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y
2014 | 1784 | 0634005033 | Harrison West Compressor Station | Possum Hollow Road | Freeport | 43973 |  | Harrison | P001 | Compressor Engine #1 - 1480 HP (11.39 MMBtu/hr) Waukesha L7042 - natural gas-fired four-stroke rich burn internal combustion engine equipped with a three-way oxidation catalyst controlling CH2O, CO, NOx, & VOCs by 80, 97, 98.5 & 66 percent respectively | 2014-12-11 | CC001(Catalytic Converter): Compressor Engine #1 - 3-way Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - 3-way Catalyst; CC004(Catalytic Converter): Compressor Engine #4 - 3-way Catalyst; CC007(Catalytic Converter): Compressor Engine #7 - 3-w | Air Hygiene, Inc. | 1,480 hp | 0.28 g/hp-hr | 1,324 hp | 0.067 g/hp-hr | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y
2014 | 1786 | 0634005033 | Harrison West Compressor Station | Possum Hollow Road | Freeport | 43973 |  | Harrison | P003 | Compressor Engine #3 - 1980 HP (15.43 MMBtu/hr) Waukesha P9390 - natural gas-fired four-stroke rich burn internal combustion engine equipped with a three-way oxidation catalyst controlling CH2O, CO, NOx, & VOCs by 80, 97, 98.5 & 66 percent respectively | 2014-12-11 | CC001(Catalytic Converter): Compressor Engine #1 - 3-way Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - 3-way Catalyst; CC004(Catalytic Converter): Compressor Engine #4 - 3-way Catalyst; CC007(Catalytic Converter): Compressor Engine #7 - 3-w | Air Hygiene, Inc. | 1,980 hp | 0.28 g/hp-hr | 1,820 hp | 0.081 g/hp-hr | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y
2014 | 1790 | 0634005033 | Harrison West Compressor Station | Possum Hollow Road | Freeport | 43973 |  | Harrison | P004 | Compressor Engine #4 - 1980 HP (15.43 MMBtu/hr) Waukesha P9390 - natural gas-fired four-stroke rich burn internal combustion engine equipped with a three-way oxidation catalyst controlling CH2O, CO, NOx, & VOCs by 80, 97, 98.5 & 66 percent respectively | 2014-12-11 | CC001(Catalytic Converter): Compressor Engine #1 - 3-way Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - 3-way Catalyst; CC004(Catalytic Converter): Compressor Engine #4 - 3-way Catalyst; CC007(Catalytic Converter): Compressor Engine #7 - 3-w | Air Hygiene, Inc. | 1,980 hp | 0.28 g/hp-hr | 1,824 hp | 0.033 g/hp-hr | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y
2014 | 1793 | 0634005033 | Harrison West Compressor Station | Possum Hollow Road | Freeport | 43973 |  | Harrison | P007 | Compressor Engine #7 - 1980 HP (15.43 MMBtu/hr) Waukesha P9390 - natural gas-fired four-stroke rich burn internal combustion engine equipped with a three-way oxidation catalyst controlling CH2O, CO, NOx, & VOCs by 80, 97, 98.5 & 66 percent respectively | 2014-12-11 | CC001(Catalytic Converter): Compressor Engine #1 - 3-way Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - 3-way Catalyst; CC004(Catalytic Converter): Compressor Engine #4 - 3-way Catalyst; CC007(Catalytic Converter): Compressor Engine #7 - 3-w | Air Hygiene, Inc. | 1,980 hp | 0.28 g/hp-hr | 1,980 hp | 0.026 g/hp-hr | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y
2014 | 1794 | 0634005033 | Harrison West Compressor Station | Possum Hollow Road | Freeport | 43973 |  | Harrison | P001 | Compressor Engine #1 - 1480 HP (11.39 MMBtu/hr) Waukesha L7042 - natural gas-fired four-stroke rich burn internal combustion engine equipped with a three-way oxidation catalyst controlling CH2O, CO, NOx, & VOCs by 80, 97, 98.5 & 66 percent respectively | 2014-12-12 | CC001(Catalytic Converter): Compressor Engine #1 - 3-way Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - 3-way Catalyst; CC004(Catalytic Converter): Compressor Engine #4 - 3-way Catalyst; CC007(Catalytic Converter): Compressor Engine #7 - 3-w | Air Hygiene, Inc. | 1,480 hp | 0.28 g/hp-hr | 1,324 hp | 0.067 g/hp-hr | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y
2014 | 1799 | 0634005033 | Harrison West Compressor Station | Possum Hollow Road | Freeport | 43973 |  | Harrison | P003 | Compressor Engine #3 - 1980 HP (15.43 MMBtu/hr) Waukesha P9390 - natural gas-fired four-stroke rich burn internal combustion engine equipped with a three-way oxidation catalyst controlling CH2O, CO, NOx, & VOCs by 80, 97, 98.5 & 66 percent respectively | 2014-12-12 | CC001(Catalytic Converter): Compressor Engine #1 - 3-way Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - 3-way Catalyst; CC004(Catalytic Converter): Compressor Engine #4 - 3-way Catalyst; CC007(Catalytic Converter): Compressor Engine #7 - 3-w | Air Hygiene, Inc. | 1,980 hp | 0.28 g/hp-hr | 1,820 hp | 0.081 g/hp-hr | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y
2014 | 1801 | 0634005033 | Harrison West Compressor Station | Possum Hollow Road | Freeport | 43973 |  | Harrison | P004 | Compressor Engine #4 - 1980 HP (15.43 MMBtu/hr) Waukesha P9390 - natural gas-fired four-stroke rich burn internal combustion engine equipped with a three-way oxidation catalyst controlling CH2O, CO, NOx, & VOCs by 80, 97, 98.5 & 66 percent respectively | 2014-12-12 | CC001(Catalytic Converter): Compressor Engine #1 - 3-way Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - 3-way Catalyst; CC004(Catalytic Converter): Compressor Engine #4 - 3-way Catalyst; CC007(Catalytic Converter): Compressor Engine #7 - 3-w | Air Hygiene, Inc. | 1,980 hp | 0.28 g/hp-hr | 1,824 hp | 0.033 g/hp-hr | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y
2014 | 1804 | 0634005033 | Harrison West Compressor Station | Possum Hollow Road | Freeport | 43973 |  | Harrison | P007 | Compressor Engine #7 - 1980 HP (15.43 MMBtu/hr) Waukesha P9390 - natural gas-fired four-stroke rich burn internal combustion engine equipped with a three-way oxidation catalyst controlling CH2O, CO, NOx, & VOCs by 80, 97, 98.5 & 66 percent respectively | 2014-12-12 | CC001(Catalytic Converter): Compressor Engine #1 - 3-way Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - 3-way Catalyst; CC004(Catalytic Converter): Compressor Engine #4 - 3-way Catalyst; CC007(Catalytic Converter): Compressor Engine #7 - 3-w | Air Hygiene, Inc. | 1,980 hp | 0.28 g/hp-hr | 1,980 hp | 0.026 g/hp-hr | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y
2014 | 1808 | 0634005034 | Lake Compressor Station | County Highway 21 | Freeport | 43973 |  | Harrison | P003 | Compressor Engine #3 - 1980 HP (15.43 MMBtu/hr) Waukesha P9390 - natural gas-fired four-stroke rich burn internal combustion engine equipped with a three-way oxidation catalyst controlling CH2O, CO, NOx, & VOCs by 80, 97, 98.5 & 66 percent respectively | 2014-04-10 | CC003(Catalytic Converter): Compressor Engine #3 - 3-way Catalyst | Air Hygiene Internatjional | 1,980 hp | 0.7 g/hp-hr | 1,782 hp | 0.018 g/hp-hr | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y
2014 | 1809 | 0634005034 | Lake Compressor Station | County Highway 21 | Freeport | 43973 |  | Harrison | P004 | Compressor Engine #4 - 1980 HP (15.43 MMBtu/hr) Waukesha P9390 - natural gas-fired four-stroke rich burn internal combustion engine equipped with a three-way oxidation catalyst controlling CH2O, CO, NOx, & VOCs by 80, 97, 98.5 & 66 percent respectively | 2014-04-10 | CC004(Catalytic Converter): Compressor Engine #4 - 3-way Catalyst | Air Hygiene International | 1,980 hp | 0.7 g/hp-hr | 1,782 hp | 0.006 g/hp-hr | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y
2014 | 1813 | 0634005034 | Lake Compressor Station | County Highway 21 | Freeport | 43973 |  | Harrison | P005 | Compressor Engine #5 - 1980 HP (15.43 MMBtu/hr) Waukesha P9390 - natural gas-fired four-stroke rich burn internal combustion engine equipped with a three-way oxidation catalyst controlling CH2O, CO, NOx, & VOCs by 80, 97, 98.5 & 66 percent respectively | 2014-04-10 | CC005(Catalytic Converter): Compressor Engine #5 - 3-way Catalyst | Air Hygiene International | 1,980 hp | 0.7 g/hp-hr | 1,441 hp | 0.018 g/hp-hr | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y
2014 | 1815 | 0634005034 | Lake Compressor Station | County Highway 21 | Freeport | 43973 |  | Harrison | P001 | Compressor Engine #1 - 1480 HP (11.39 MMBtu/hr) Waukesha L7042 - natural gas-fired four-stroke rich burn internal combustion engine equipped with a three-way oxidation catalyst controlling CH2O, CO, NOx, & VOCs by 80, 97, 98.5 & 66 percent respectively | 2014-04-11 | CC001(Catalytic Converter): Compressor Engine #1 - 3-way Catalyst | Air Hygiene International | 1,480 hp | 0.7 g/hp-hr | 1,480 hp | 0.081 g/hp-hr | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y
2014 | 1820 | 0634005034 | Lake Compressor Station | County Highway 21 | Freeport | 43973 |  | Harrison | P002 | Compressor Engine #2 - 1480 HP (11.39 MMBtu/hr) Waukesha L7042 - natural gas-fired four-stroke rich burn internal combustion engine equipped with a three-way oxidation catalyst controlling CH2O, CO, NOx, & VOCs by 80, 97, 98.5 & 66 percent respectively | 2014-04-11 | CC002(Catalytic Converter): Compressor Engine #2 - 3-way Catalyst | Air Hygiene International | 1,480 hp | 0.7 g/hp-hr | 1,480 hp | 0.74 g/hp-hr | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y
2014 | 1822 | 0634005034 | Lake Compressor Station | County Highway 21 | Freeport | 43973 |  | Harrison | P002 | Compressor Engine #2 - 1480 HP (11.39 MMBtu/hr) Waukesha L7042 - natural gas-fired four-stroke rich burn internal combustion engine equipped with a three-way oxidation catalyst controlling CH2O, CO, NOx, & VOCs by 80, 97, 98.5 & 66 percent respectively | 2014-12-15 | CC002(Catalytic Converter): Compressor Engine #2 - 3-way Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - 3-way Catalyst; CC004(Catalytic Converter): Compressor Engine #4 - 3-way Catalyst; CC005(Catalytic Converter): CC011(Catalytic Converter | Air Hygiene, Inc | 1,480 hp | 0.28 g/hp-hr | 1,151 hp | 0.054 g/hp-hr | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y
2014 | 1825 | 0634005034 | Lake Compressor Station | County Highway 21 | Freeport | 43973 |  | Harrison | P003 | Compressor Engine #3 - 1980 HP (15.43 MMBtu/hr) Waukesha P9390 - natural gas-fired four-stroke rich burn internal combustion engine equipped with a three-way oxidation catalyst controlling CH2O, CO, NOx, & VOCs by 80, 97, 98.5 & 66 percent respectively | 2014-12-15 | CC002(Catalytic Converter): Compressor Engine #2 - 3-way Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - 3-way Catalyst; CC004(Catalytic Converter): Compressor Engine #4 - 3-way Catalyst; CC005(Catalytic Converter): CC011(Catalytic Converter | Air Hygiene, Inc | 1,980 hp | 0.28 g/hp-hr | 1,571 hp | 0.007 g/hp-hr | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y
2014 | 1828 | 0634005034 | Lake Compressor Station | County Highway 21 | Freeport | 43973 |  | Harrison | P004 | Compressor Engine #4 - 1980 HP (15.43 MMBtu/hr) Waukesha P9390 - natural gas-fired four-stroke rich burn internal combustion engine equipped with a three-way oxidation catalyst controlling CH2O, CO, NOx, & VOCs by 80, 97, 98.5 & 66 percent respectively | 2014-12-15 | CC002(Catalytic Converter): Compressor Engine #2 - 3-way Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - 3-way Catalyst; CC004(Catalytic Converter): Compressor Engine #4 - 3-way Catalyst; CC005(Catalytic Converter): CC011(Catalytic Converter | Air Hygiene, Inc | 1,980 hp | 0.28 g/hp-hr | 1,677 hp | 0.004 g/hp-hr | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y
2014 | 1830 | 0634005034 | Lake Compressor Station | County Highway 21 | Freeport | 43973 |  | Harrison | P011 | Compressor Engine #9 - Waukesha L7042 - natural gas fired four-stroke, rich burn internal combustion engine rated at an operating capacity of 1,480 horsepower equipped with a three-way oxidation catalyst. | 2014-12-15 | CC002(Catalytic Converter): Compressor Engine #2 - 3-way Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - 3-way Catalyst; CC004(Catalytic Converter): Compressor Engine #4 - 3-way Catalyst; CC005(Catalytic Converter): CC011(Catalytic Converter | Air Hygiene, Inc | 1,480 hp | 0.28 g/hp-hr | 1,014 hp | 0.031 g/hp-hr | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y
2014 | 1835 | 0634005034 | Lake Compressor Station | County Highway 21 | Freeport | 43973 |  | Harrison | P002 | Compressor Engine #2 - 1480 HP (11.39 MMBtu/hr) Waukesha L7042 - natural gas-fired four-stroke rich burn internal combustion engine equipped with a three-way oxidation catalyst controlling CH2O, CO, NOx, & VOCs by 80, 97, 98.5 & 66 percent respectively | 2014-12-16 | CC002(Catalytic Converter): Compressor Engine #2 - 3-way Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - 3-way Catalyst; CC004(Catalytic Converter): Compressor Engine #4 - 3-way Catalyst; CC005(Catalytic Converter): CC011(Catalytic Converter | Air Hygiene, Inc | 1,480 hp | 0.28 g/hp-hr | 1,151 hp | 0.054 g/hp-hr | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y
2014 | 1836 | 0634005034 | Lake Compressor Station | County Highway 21 | Freeport | 43973 |  | Harrison | P003 | Compressor Engine #3 - 1980 HP (15.43 MMBtu/hr) Waukesha P9390 - natural gas-fired four-stroke rich burn internal combustion engine equipped with a three-way oxidation catalyst controlling CH2O, CO, NOx, & VOCs by 80, 97, 98.5 & 66 percent respectively | 2014-12-16 | CC002(Catalytic Converter): Compressor Engine #2 - 3-way Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - 3-way Catalyst; CC004(Catalytic Converter): Compressor Engine #4 - 3-way Catalyst; CC005(Catalytic Converter): CC011(Catalytic Converter | Air Hygiene, Inc | 1,980 hp | 0.28 g/hp-hr | 1,571 hp | 0.007 g/hp-hr | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y
2014 | 1840 | 0634005034 | Lake Compressor Station | County Highway 21 | Freeport | 43973 |  | Harrison | P004 | Compressor Engine #4 - 1980 HP (15.43 MMBtu/hr) Waukesha P9390 - natural gas-fired four-stroke rich burn internal combustion engine equipped with a three-way oxidation catalyst controlling CH2O, CO, NOx, & VOCs by 80, 97, 98.5 & 66 percent respectively | 2014-12-16 | CC002(Catalytic Converter): Compressor Engine #2 - 3-way Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - 3-way Catalyst; CC004(Catalytic Converter): Compressor Engine #4 - 3-way Catalyst; CC005(Catalytic Converter): CC011(Catalytic Converter | Air Hygiene, Inc | 1,980 hp | 0.28 g/hp-hr | 1,677 hp | 0.004 g/hp-hr | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y
2014 | 1843 | 0634005034 | Lake Compressor Station | County Highway 21 | Freeport | 43973 |  | Harrison | P011 | Compressor Engine #9 - Waukesha L7042 - natural gas fired four-stroke, rich burn internal combustion engine rated at an operating capacity of 1,480 horsepower equipped with a three-way oxidation catalyst. | 2014-12-16 | CC002(Catalytic Converter): Compressor Engine #2 - 3-way Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - 3-way Catalyst; CC004(Catalytic Converter): Compressor Engine #4 - 3-way Catalyst; CC005(Catalytic Converter): CC011(Catalytic Converter | Air Hygiene, Inc | 1,480 hp | 0.28 g/hp-hr | 1,014 hp | 0.031 g/hp-hr | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y
2014 | 1847 | 0634005037 | Chesapeake Exploration LLC - Gotshall 14-12-5 Pad | Burrier Rd | Scio | 43986 |  | Harrison | P002 | Flash gas compressor equipped with catalyst, 211 hp, CAT G3306TA (Spark Ignition Internal Combustion Engine, P002) | 2014-04-09 | none | Alliance Source Testing | 211 hp | 86.0 ppm | 175 hp | 1.3 ppm | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y
2014 | 1850 | 0634005040 | Archer Compressor Facility | County Highway 45 | Cadiz | 43907 |  | Harrison | P001 | Compressor Engine #1 - 1775 HP Caterpillar G3606 (4S-LB) - natural gas-fired four-cycle lean burn internal combustion engine rated equipped with an oxidation catalyst controlling CO and VOC emissions. | 2014-11-10 | OxidCat-101(Catalytic Converter): Oxidative Catalyst | EcoTest Energy Inc. | 1608 Hp | 0.7 g/Hp-hr | 1608 Hp | 0.13 g/Hp-hr | 25B | VOC - Volatile Organic Compounds | PASS | NA | Y | Method 25B not used. Method 205, 320 and ASTM 6348-3 used. FTIR
2014 | 1851 | 0634005040 | Archer Compressor Facility | County Highway 45 | Cadiz | 43907 |  | Harrison | P002 | Compressor Engine #2 - 1775 HP Caterpillar G3606 (4S-LB) - natural gas-fired four-cycle lean burn internal combustion engine rated equipped with an oxidation catalyst controlling CO and VOC emissions. | 2014-11-10 | OxidCat-102(Catalytic Converter): Oxidative Catalyst | EcoTest Energy Services | 1775 Hp | 0.7 g/Hp-hr | 1600 Hp | 0.12 g/Hp-hr | 25B | VOC - Volatile Organic Compounds | PASS | NA | Y | Method 25B not used. Method 205, 320 and ASTM 6348-3 FTIR
2014 | 1855 | 0634005040 | Archer Compressor Facility | County Highway 45 | Cadiz | 43907 |  | Harrison | P003 | Compressor Engine #3 - 1775 HP Caterpillar G3606 (4S-LB) - natural gas-fired four-cycle lean burn internal combustion engine rated equipped with an oxidation catalyst controlling CO and VOC emissions. | 2014-11-10 | OxidCat-103(Catalytic Converter): Oxidative Catalyst | EcoTest Energy Services | 1775 Hp | 0.7 g/Hp-hr | 1627 Hp | 0.07 g/Hp-hr | 25B | VOC - Volatile Organic Compounds | PASS | NA | Y | Method 25 B not used. Method 205, 320 and ASTM 6348-3 used. FTIR
2014 | 1859 | 0634005040 | Archer Compressor Facility | County Highway 45 | Cadiz | 43907 |  | Harrison | P004 | Compressor Engine #4 - 1775 HP Caterpillar G3606 (4S-LB) - natural gas-fired four-cycle lean burn internal combustion engine rated equipped with an oxidation catalyst controlling CO and VOC emissions. | 2014-11-10 | OxidCat-104(Catalytic Converter): Oxidative Catalyst | EcoTest Energy Services | 1775 Hp | 0.7 g/Hp-hr | 1642 Hp | 0.1 g/Hp-hr | 25B | VOC - Volatile Organic Compounds | PASS | NA | Y | Method 25B not used. Methods 205, 320 and ASTM 6348-3 FTIR
2014 | 1861 | 0634005040 | Archer Compressor Facility | County Highway 45 | Cadiz | 43907 |  | Harrison | P005 | Compressor Engine #5 - 1775 HP Caterpillar G3606 (4S-LB) - natural gas-fired four-cycle lean burn internal combustion engine rated equipped with an oxidation catalyst controlling CO and VOC emissions. | 2014-11-11 | OxidCat-105(Catalytic Converter): Oxidative Catalyst | EcoTest Energy Services | 1775 Hp | 0.7 g/Hp-hr | 1638 Hp | 0.1 g/Hp-hr | 25B | VOC - Volatile Organic Compounds | PASS | NA | Y | Method 25B not used. Methods 205, 320 and ASTM 6348-3 FTIR
2014 | 1863 | 0634005040 | Archer Compressor Facility | County Highway 45 | Cadiz | 43907 |  | Harrison | P006 | Compressor Engine #6 - 1775 HP Caterpillar G3606 (4S-LB) - natural gas-fired four-cycle lean burn internal combustion engine rated equipped with an oxidation catalyst controlling CO and VOC emissions. | 2014-11-11 | OxidCat-106(Catalytic Converter): Oxidative Catalyst | EcoTest Services | 1775 Hp | 0.7 g/Hp-hr | 1683 Hp | 0.2 g/Hp-hr | 25B | VOC - Volatile Organic Compounds | PASS | NA | Y | Method 25B not used. Method 205, 320 and ASTM 6348-3 FTIR
2014 | 1867 | 0634005040 | Archer Compressor Facility | County Highway 45 | Cadiz | 43907 |  | Harrison | P007 | Compressor Engine #7 - 1775 HP Caterpillar G3606 (4S-LB) - natural gas-fired four-cycle lean burn internal combustion engine rated equipped with an oxidation catalyst controlling CO and VOC emissions. | 2014-11-12 | OxidCat-107(Catalytic Converter): Oxidative Catalyst | EcoTest Services | 1775 Hp | 0.1 g/Hp-hr | 1703 Hp | 0.7 g/Hp-hr | 25B | VOC - Volatile Organic Compounds | PASS | NA | Y | Method 25 B not used. Method 205, 320 and ASSTM 6348-3 FTIR
2014 | 1869 | 0634005040 | Archer Compressor Facility | County Highway 45 | Cadiz | 43907 |  | Harrison | P008 | Compressor Engine #8 - 1775 HP Caterpillar G3606 (4S-LB) - natural gas-fired four-cycle lean burn internal combustion engine rated equipped with an oxidation catalyst controlling CO and VOC emissions. | 2014-11-12 | OxidCat-108(Catalytic Converter): Oxidative Catalyst | EcoTest Energy Services | 1775 Hp | 0.70 g/Hp-hr | 1608 Hp | 0.043 g/Hp-hr | 25B | VOC - Volatile Organic Compounds | PASS | NA | Y | Method 25B not used. Methods 205, 320 and ASTM 6348-3 FTIR
2014 | 1873 | 0634005043 | Gulfport Energy- BK Stephens | 75501 Tyson Road | Cadiz | 43907 |  | Harrison | P002 | One or multiple stationary natural gas-fired spark ignition (SI) internal combustion engines (ICE) wiht a combined total horsepower (HP) of no more than 1,800 HP for the site. | 2014-07-02 | none | BCMJ Control Inc | 400 Hp | 1.0 g/Hp-hr | 280 Hp | 0.67 g/Hp-hr | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y | 400 Hp Waukesha engine-Serial #-C-17249/1-results above 203 Hp Caterpillar engine-Serial #4FD18737- tested rate: 0.16 g/Hp-hr NOX 0.1 g/Hp-hr CO 0.13 g/Hp-hr VOC allowable rate: 2.0 g/Hp-hr NOX 4.0 g/Hp-hr CO 1.0 g/Hp-hr VOC
2014 | 1875 | 0634005045 | Gulfport Energy- Clay Well Pad | 31501 Morrison Road | Freeport | 43973 |  | Harrison | P002 | One or multiple stationary natural gas-fired spark ignition (SI) internal combustion engines (ICE) with a combined total horsepower (HP) of no more than 1,800 HP for the site. Includes 2007 and later model year engines manufactured after the applicable effective date identified in 40 CFR 60.4230(a)(3) and engines manufactured before the NSPS effective date where compliance with the Part 60 Subpart JJJJ emissions standards for the same size engine can be demonstrated through stack testing. | 2014-07-08 | none-carbureted air fuel mix to control emissions | BCMJ Control, Inc. | 145 Hp | 1.0 g/Hp-hr | 53 Hp | 0.21 g/Hp-hr | 25B | VOC - Volatile Organic Compounds | PASS | NA | Y | P002 (second engine) Serial # 9TG00298 1.0 g/Hp-hr 630 Hp 0.39 g/Hp-hr 350 Hp Method 320
2014 | 1879 | 0634005048 | Gulfport Energy- Boy Scout Well Pad | 79900 Adams Rd | Tippecanoe | 44699 |  | Harrison | P002 | One 60 hp Waukesha 310 and one 64 hp HEC 3491-OPV natural gas engines for compressors | 2014-07-02 | none | BCMJ Controls, Inc | 400 Hp | 86.0 ppm | 217 Hp | 81.8 ppm | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y | 118 hp Cummins engine 0.18 g/Hp-hr VOC allowable rate-1.0 g/Hp-hr VOC 145 Hp Caterpillar engine (one hour run only) 0.79 g/Hp-hr VOC allowable rate-1.0 g/Hp-hr VOC
2014 | 1883 | 0634005049 | Gulfport Energy- Ryser #1-25H Well Pad | 77100 Scott Hill Road | Flushing | 43977 |  | Harrison | P002 | One or multiple stationary natural gas-fired spark ignition (SI) internal combustion engines (ICE) with a combined total horsepower (HP) of no more than 1,800 HP for the site. | 2014-07-07 | catalytic reduction | BCMJ Control, Inc | 325 Hp Caterpillar S # 4FD00578 | 1.0 g/Hp-hr | 134 Hp | 0.06 g/Hp-hr | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y | 215 Hp Caterpillar engine-NOX 1.0 g/Hp-hr 215 Hp 0.06 g/Hp-hr 36 Hp Serial # G6X00951
2014 | 1886 | 0634005054 | Gulfport Energy - Lyons Well Pad | 27650 Friendly Ridge Rd | Tippecanoe | 44699 |  | Harrison | P002 | Two 50-hp Blackmer 942 natural gas-fired engines for compressors. | 2014-08-06 | non selective catalytic reduction | BCMJ Controls, Inc | 380 Hp | 1.0 g/Hp-hr | 296 Hp | 0.05 g/Hp-hr | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y
2014 | 1889 | 0634005056 | Scio Compressor Station | 37650 Bower Rd | Scio | 43988 |  | Harrison | P005 | Compressor Engine #5 - 1,775 HP Caterpillar G3606 (4S-LB) - natural gas-fired four-cycle lean burn internal combustion engine equipped with an oxidation catalyst controlling CO & VOC emissions | 2014-06-23 | CC005(Catalytic Converter): Compressor Engine #5 - Oxidation Catalyst | Alliance Source Testing | 1,627 Hp | 0.14 g/Hp-hr 60 ppm | 1,627 Hp | 0.07 g/Hp-hr 6.7 ppm | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y
2014 | 1890 | 0634005056 | Scio Compressor Station | 37650 Bower Rd | Scio | 43988 |  | Harrison | P006 | Compressor Engine #6 - 1,775 HP Caterpillar G3606 (4S-LB) - natural gas-fired four-cycle lean burn internal combustion engine equipped with an oxidation catalyst controlling CO & VOC emissions | 2014-06-23 | CC006(Catalytic Converter): Compressor Engine #6 - Oxidation Catalyst | Alliance Source Testing | 1,775 Hp | 0.14 g/Hp-hr 60 ppm | 1,630 Hp | 0.02 g/Hp-hr 2.4 ppm | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y
2014 | 1895 | 0634005056 | Scio Compressor Station | 37650 Bower Rd | Scio | 43988 |  | Harrison | P001 | Compressor Engine #1 - 1,775 HP Caterpillar G3606 (4S-LB) - natural gas-fired four-cycle lean burn internal combustion engine equipped with an oxidation catalyst controlling CO & VOC emissions. | 2014-06-24 | CC001(Catalytic Converter): Compressor Engine #1 - Oxidation Catalyst | Alliance Source Testing | 1,775 Hp | 0.14 g/Hp-hr 60 ppm | 1,650 Hp | 0.10 g/Hp-hr 9.7 ppm | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y
2014 | 1897 | 0634005056 | Scio Compressor Station | 37650 Bower Rd | Scio | 43988 |  | Harrison | P002 | Compressor Engine #2 - 1,775 HP Caterpillar G3606 (4S-LB) - natural gas-fired four-cycle lean burn internal combustion engine equipped with an oxidation catalyst controlling CO & VOC emissions | 2014-06-24 | CC002(Catalytic Converter): Compressor Engine #2 - Oxidation Catalyst | Alliance Source Testing | 1,775 Hp | 0.14 g/Hp-hr 60 ppm | 1,659 Hp | 0.1 g/Hp-hr 7.6 ppm | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y
2014 | 1900 | 0634005056 | Scio Compressor Station | 37650 Bower Rd | Scio | 43988 |  | Harrison | P003 | Compressor Engine #3 - 1,775 HP Caterpillar G3606 (4S-LB) - natural gas-fired four-cycle lean burn internal combustion engine equipped with an oxidation catalyst controlling CO & VOC emissions | 2014-06-24 | CC003(Catalytic Converter): Compressor Engine #3 - Oxidation Catalyst | Alliance Source Testing | 1,775 Hp | 0.14 g/Hp-hr 60 ppm | 1,616 Hp | 0.02 g/Hp-hr 1.5 ppm | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y
2014 | 1903 | 0634005056 | Scio Compressor Station | 37650 Bower Rd | Scio | 43988 |  | Harrison | P004 | Compressor Engine #4 - 1,775 HP Caterpillar G3606 (4S-LB) - natural gas-fired four-cycle lean burn internal combustion engine equipped with an oxidation catalyst controlling CO & VOC emissions | 2014-06-24 | CC004(Catalytic Converter): Compressor Engine #4 - Oxidation Catalyst | Alliance Source Testing | 1,775 Hp | 0.14 g/Hp-hr 60 ppm | 1,651 | 0.10 g/Hp-hr 8.3 ppm | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y
2014 | 1907 | 0634005056 | Scio Compressor Station | 37650 Bower Rd | Scio | 43988 |  | Harrison | P007 | Compressor Engine #7 - 1,775 HP Caterpillar G3606 (4S-LB) - natural gas-fired four-cycle lean burn internal combustion engine equipped with an oxidation catalyst controlling CO & VOC emissions | 2014-06-25 | CC007(Catalytic Converter): Compressor Engine #7 - Oxidation Catalyst | Alliance Source Testing | 1,775 Hp | 0.14 g/Hp-hr 60 ppm | 1,605 Hp | 0.1 g/Hp-hr 8.4 ppm | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y
2014 | 1910 | 0634005056 | Scio Compressor Station | 37650 Bower Rd | Scio | 43988 |  | Harrison | P008 | Compressor Engine #8 - 1,775 HP Caterpillar G3606 (4S-LB) - natural gas-fired four-cycle lean burn internal combustion engine equipped with an oxidation catalyst controlling CO & VOC emissions | 2014-06-25 | CC008(Catalytic Converter): Compressor Engine #8 - Oxidation Catalyst | Alliance Source Testing | 1,775 Hp | 0.14 g/Hp-hr 60 ppm | 1,615 Hp | 0.08 g/Hp-hr 6.9 ppm | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y
2014 | 1913 | 0634005056 | Scio Compressor Station | 37650 Bower Rd | Scio | 43988 |  | Harrison | P009 | Compressor Engine #9 - 1,775 HP Caterpillar G3606 (4S-LB) - natural gas-fired four-cycle lean burn internal combustion engine equipped with an oxidation catalyst controlling CO & VOC emissions | 2014-06-25 | CC009(Catalytic Converter): Compressor Engine #9 - Oxidation Catalyst | Alliance Source Testing | 1,775 Hp | 0.14 g/Hp-hr 60 ppm | 1,613 Hp | 0.1 g/Hp-hr 8.7 ppm | 25A | VOC - Volatile Organic Compounds | PASS | Y | Y
2014 | 1916 | 0634005056 | Scio Compressor Station | 37650 Bower Rd | Scio | 43988 |  | Harrison | P010 | Compressor Engine #10 - 1,775 HP Caterpillar G3606 (4S-LB) - natural gas-fired four-cycle lean burn internal combustion engine equipped with an oxidation catalyst controlling CO & VOC emissions | 2014-06-25 | CC010(Catalytic Converter): Compressor Engine #10 - Oxidation Catalyst | Alliance Source Testing | 1,775 Hp | 0.14 g/Hp-hr 60 ppm | 1,602 Hp | 0.08 g/Hp-hr 6.9 ppm | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y
2014 | 1926 | 0634005058 | Atlas Noble, LLC - Cramblett Well Pad | Bowers Road | North Twp. | 43988 |  | Harrison | P002 | 415 Hp Caterpillar G379 TA natural gas fired recovery compressor engine equipped with a catalytic converter. (non JJJJ engine). 68 Hp Caterpillar VRG330 natural gas fired vapor recovery unit equipped with a catalytic convertor. | 2014-03-04 | none | Air Compliance Consultants | 415 hp | 86 ppm | 204 hp | 1.1 ppm | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y
2014 | 1932 | 0634005059 | Chesapeake Exploration LLC - Kidd 21-12-6 Pad | Township Highway 219 - Beagle Club Rd | Scio | 43988 |  | Harrison | P002 | One or multiple stationary natural gas-fired spark ignition (SI) internal combustion engines (ICE) with a combined total horsepower (HP) of no more than 1,800 HP for the site.* Includes 2007 and later model year engines manufactured after the applicable effective date identified in 40 CFR 60.4230(a)(3) and engines manufactured before the NSPS effective date where compliance with the Part 60 Subpart JJJJ emissions standards for the same size engine can be demonstrated through stack testing. | 2014-06-30 | none | Alliance Source Testing | 211 Hp | 1.0 g/Hp-hr | 143 Hp | 0.2 g/Hp-hr | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y
2014 | 1937 | 0634005072 | Gulfport Energy - Milliken | 31255 Cadiz-Piedmont Rd | Freeport | 43973 |  | Harrison | P002 | One or multiple stationary natural gas-fired spark ignition (SI) internal combustion engines (ICE) wiht a combined total horsepower (HP) of no more than 1,800 HP for the site. | 2014-08-12 | catalytic | BCMJ Controls Inc | 145 Hp Caterpillar S# 07Y05427 | 1.0 g/Hp-hr | 122 Hp | 0.03 g/Hp-hr | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y | 60 Hp HEC engine 1.0 g/Hp-hr 60 Hp 0.17 g/Hp-hr 30 Hp
2014 | 1940 | 0634005077 | Gulfport Energy - Michael Well Pad | 75096 Tyson Rd | Flushing | 43977 |  | Harrison | P002 | One or multiple stationary natural gas-fired spark ignition (SI) internal combustion engines (ICE) wiht a combined total horsepower (HP) of no more than 1,800 HP for the site. | 2014-12-03 | none | Great Plains Analytical Services | 118 Hp | 1.0 g/Hp-hr | 53 Hp | 0.095 g/Hp-hr | 25B | VOC - Volatile Organic Compounds | PASS | NA | Y | method 25B not used. Method 1-3A and ASTM 6348-03 used
2014 | 1999 | 0656005010 | Dominion East Ohio - Switzerland Compressor Station | German Ridge Road | Switzerland Twp. | 43942 |  | Monroe | P001 | 3550 Hp Natural gas-fired (4SLB) Caterpillar model 3612 LE DM5309-06 compressor engines equipped with catalytic reduction (three-way). | 2014-11-12 | catalytic reduction | Air Compliance Consultants | 3550 Hp | 0.26 g/Hp-hr | 3408 Hp | 0.089 g/Hp-hr | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y
2014 | 2001 | 0656005010 | Dominion East Ohio - Switzerland Compressor Station | German Ridge Road | Switzerland Twp. | 43942 |  | Monroe | P003 | 3550 Hp Natural gas-fired (4SLB) Caterpillar model 3612 LE DM5309-06 compressor engines equipped with catalytic reduction (three-way). | 2014-11-12 | catalytic reduction | Air Compliance Consultants | 3550 Hp | 0.26 g/Hp-hr | 3242 Hp | 0.066 g/Hp-hr | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y
2014 | 2010 | 0656005011 | Ormet Production Facility | 43879 St Rte 7 | Hannibal | 43931 |  | Monroe | P001 | CAT 3516BLE SI combustion engine 1380 bhp | 2014-10-30 | none in facility profile | EcoTest Energy Services | 1,380 Hp | 0.69 g/Hp-hr | 1,250 Hp | 0.10 g/Hp-hr | 6348 03 | VOC - Volatile Organic Compounds | PASS | NA | Y | Method 320 used-not ASTM 6348-03
2014 | 2011 | 0656005011 | Ormet Production Facility | 43879 St Rte 7 | Hannibal | 43931 |  | Monroe | P001 | CAT 3516BLE SI combustion engine 1380 bhp | 2014-10-30 | none | EcoTest Energy Services | 1,380 Hp | 0.69 g/Hp-hr | 1,250 Hp | 0.10 g/Hp-hr | 25B | VOC - Volatile Organic Compounds | PASS | NA | Y | method 25B not used. method 320
2014 | 2013 | 0656105005 | E2 Appalachian Compression LLC - Reusser | Twp Hwy 68 and Twp Hwy 66 | Woodsfield | 43793 |  | Monroe | P003 | 1680 Hp. natural gas rich burn compressor engine - Waukesha L7044GSI | 2014-12-08 | C-3(Catalytic Converter): Engine #3 Catalyst; C-4(Catalytic Converter): Engine #4 Catalyst; C-5(Catalytic Converter): Engine #5 Catalyst; C-6(Catalytic Converter): Engine #6Catalyst; C-8(Catalytic Converter): Engine #8 Catalyst | E2 Energy Services | 1,680 hp | 0.22 lb/hr | 1,551 hp | 0.58 lb/hr | 6348 03 | VOC - Volatile Organic Compounds | FAIL | NA | Y
2014 | 2015 | 0656105005 | E2 Appalachian Compression LLC - Reusser | Twp Hwy 68 and Twp Hwy 66 | Woodsfield | 43793 |  | Monroe | P004 | 1680 Hp. natural gas rich burn compressor engine - Waukesha L7044GSI | 2014-12-08 | C-3(Catalytic Converter): Engine #3 Catalyst; C-4(Catalytic Converter): Engine #4 Catalyst; C-5(Catalytic Converter): Engine #5 Catalyst; C-6(Catalytic Converter): Engine #6Catalyst; C-8(Catalytic Converter): Engine #8 Catalyst | E2 Energy Services | 1,680 hp | 0.22 lb/hr | 1,590 hp | 0.01 lb/hr | 6348 03 | VOC - Volatile Organic Compounds | PASS | NA | Y
2014 | 2018 | 0656105005 | E2 Appalachian Compression LLC - Reusser | Twp Hwy 68 and Twp Hwy 66 | Woodsfield | 43793 |  | Monroe | P005 | 1680 Hp. natural gas rich burn compressor engine - Waukesha L7044GSI | 2014-12-08 | C-3(Catalytic Converter): Engine #3 Catalyst; C-4(Catalytic Converter): Engine #4 Catalyst; C-5(Catalytic Converter): Engine #5 Catalyst; C-6(Catalytic Converter): Engine #6Catalyst; C-8(Catalytic Converter): Engine #8 Catalyst | E2 Energy Services | 1,680 hp | 0.22 lb/hr | 1,557 hp | 0.02 lb/hr | 6348 03 | VOC - Volatile Organic Compounds | PASS | NA | Y
2014 | 2022 | 0656105005 | E2 Appalachian Compression LLC - Reusser | Twp Hwy 68 and Twp Hwy 66 | Woodsfield | 43793 |  | Monroe | P006 | 1680 Hp. natural gas rich burn compressor engine - Waukesha L7044GSI | 2014-12-08 | C-3(Catalytic Converter): Engine #3 Catalyst; C-4(Catalytic Converter): Engine #4 Catalyst; C-5(Catalytic Converter): Engine #5 Catalyst; C-6(Catalytic Converter): Engine #6Catalyst; C-8(Catalytic Converter): Engine #8 Catalyst | E2 Energy Services | 1,680 hp | 0.22 lb/hr | 1,551 hp | 0.02 lb/hr | 6348 03 | VOC - Volatile Organic Compounds | PASS | NA | Y
2014 | 2026 | 0656105005 | E2 Appalachian Compression LLC - Reusser | Twp Hwy 68 and Twp Hwy 66 | Woodsfield | 43793 |  | Monroe | P008 | 1680 Hp. natural gas rich burn compressor engine - Waukesha L7044GSI | 2014-12-08 | C-3(Catalytic Converter): Engine #3 Catalyst; C-4(Catalytic Converter): Engine #4 Catalyst; C-5(Catalytic Converter): Engine #5 Catalyst; C-6(Catalytic Converter): Engine #6Catalyst; C-8(Catalytic Converter): Engine #8 Catalyst | E2 Energy Services | 1,680 hp | 0.22 lb/hr | 1,551 hp | 0.02 lb/hr | 6348 03 | VOC - Volatile Organic Compounds | PASS | NA | Y
2014 | 2029 | 0656105005 | E2 Appalachian Compression LLC - Reusser | Twp Hwy 68 and Twp Hwy 66 | Woodsfield | 43793 |  | Monroe | P003 | 1680 Hp. natural gas rich burn compressor engine - Waukesha L7044GSI | 2014-12-10 | C-3(Catalytic Converter): Engine #3 Catalyst; C-4(Catalytic Converter): Engine #4 Catalyst; C-5(Catalytic Converter): Engine #5 Catalyst; C-6(Catalytic Converter): Engine #6Catalyst; C-8(Catalytic Converter): Engine #8 Catalyst | E2 Energy Services | 1,680 hp | 0.22 lb/hr | 1,551 hp | 0.58 lb/hr | 6348 03 | VOC - Volatile Organic Compounds | FAIL | NA | Y
2014 | 2030 | 0656105005 | E2 Appalachian Compression LLC - Reusser | Twp Hwy 68 and Twp Hwy 66 | Woodsfield | 43793 |  | Monroe | P004 | 1680 Hp. natural gas rich burn compressor engine - Waukesha L7044GSI | 2014-12-10 | C-3(Catalytic Converter): Engine #3 Catalyst; C-4(Catalytic Converter): Engine #4 Catalyst; C-5(Catalytic Converter): Engine #5 Catalyst; C-6(Catalytic Converter): Engine #6Catalyst; C-8(Catalytic Converter): Engine #8 Catalyst | E2 Energy Services | 1,680 hp | 0.22 lb/hr | 1,590 hp | 0.01 lb/hr | 6348 03 | VOC - Volatile Organic Compounds | PASS | NA | Y
2014 | 2034 | 0656105005 | E2 Appalachian Compression LLC - Reusser | Twp Hwy 68 and Twp Hwy 66 | Woodsfield | 43793 |  | Monroe | P005 | 1680 Hp. natural gas rich burn compressor engine - Waukesha L7044GSI | 2014-12-10 | C-3(Catalytic Converter): Engine #3 Catalyst; C-4(Catalytic Converter): Engine #4 Catalyst; C-5(Catalytic Converter): Engine #5 Catalyst; C-6(Catalytic Converter): Engine #6Catalyst; C-8(Catalytic Converter): Engine #8 Catalyst | E2 Energy Services | 1,680 hp | 0.22 lb/hr | 1,557 hp | 0.02 lb/hr | 6348 03 | VOC - Volatile Organic Compounds | PASS | NA | Y
2014 | 2037 | 0656105005 | E2 Appalachian Compression LLC - Reusser | Twp Hwy 68 and Twp Hwy 66 | Woodsfield | 43793 |  | Monroe | P006 | 1680 Hp. natural gas rich burn compressor engine - Waukesha L7044GSI | 2014-12-10 | C-3(Catalytic Converter): Engine #3 Catalyst; C-4(Catalytic Converter): Engine #4 Catalyst; C-5(Catalytic Converter): Engine #5 Catalyst; C-6(Catalytic Converter): Engine #6Catalyst; C-8(Catalytic Converter): Engine #8 Catalyst | E2 Energy Services | 1,680 hp | 0.22 lb/hr | 1,551 hp | 0.02 lb/hr | 6348 03 | VOC - Volatile Organic Compounds | PASS | NA | Y
2014 | 2040 | 0656105005 | E2 Appalachian Compression LLC - Reusser | Twp Hwy 68 and Twp Hwy 66 | Woodsfield | 43793 |  | Monroe | P008 | 1680 Hp. natural gas rich burn compressor engine - Waukesha L7044GSI | 2014-12-10 | C-3(Catalytic Converter): Engine #3 Catalyst; C-4(Catalytic Converter): Engine #4 Catalyst; C-5(Catalytic Converter): Engine #5 Catalyst; C-6(Catalytic Converter): Engine #6Catalyst; C-8(Catalytic Converter): Engine #8 Catalyst | E2 Energy Services | 1,680 hp | 0.22 lb/hr | 1,551 hp | 0.02 lb/hr | 6348 03 | VOC - Volatile Organic Compounds | PASS | NA | Y
2014 | 2044 | 0656105005 | E2 Appalachian Compression LLC - Reusser | Twp Hwy 68 and Twp Hwy 66 | Woodsfield | 43793 |  | Monroe | P003 | 1680 Hp. natural gas rich burn compressor engine - Waukesha L7044GSI | 2014-12-11 | C-3(Catalytic Converter): Engine #3 Catalyst; C-4(Catalytic Converter): Engine #4 Catalyst; C-5(Catalytic Converter): Engine #5 Catalyst; C-6(Catalytic Converter): Engine #6Catalyst; C-8(Catalytic Converter): Engine #8 Catalyst | E2 Energy Services | 1,680 hp | 0.22 lb/hr | 1,551 hp | 0.58 lb/hr | 6348 03 | VOC - Volatile Organic Compounds | FAIL | NA | Y
2014 | 2046 | 0656105005 | E2 Appalachian Compression LLC - Reusser | Twp Hwy 68 and Twp Hwy 66 | Woodsfield | 43793 |  | Monroe | P004 | 1680 Hp. natural gas rich burn compressor engine - Waukesha L7044GSI | 2014-12-11 | C-3(Catalytic Converter): Engine #3 Catalyst; C-4(Catalytic Converter): Engine #4 Catalyst; C-5(Catalytic Converter): Engine #5 Catalyst; C-6(Catalytic Converter): Engine #6Catalyst; C-8(Catalytic Converter): Engine #8 Catalyst | E2 Energy Services | 1,680 hp | 0.22 lb/hr | 1,590 hp | 0.01 lb/hr | 6348 03 | VOC - Volatile Organic Compounds | PASS | NA | Y
2014 | 2050 | 0656105005 | E2 Appalachian Compression LLC - Reusser | Twp Hwy 68 and Twp Hwy 66 | Woodsfield | 43793 |  | Monroe | P005 | 1680 Hp. natural gas rich burn compressor engine - Waukesha L7044GSI | 2014-12-11 | C-3(Catalytic Converter): Engine #3 Catalyst; C-4(Catalytic Converter): Engine #4 Catalyst; C-5(Catalytic Converter): Engine #5 Catalyst; C-6(Catalytic Converter): Engine #6Catalyst; C-8(Catalytic Converter): Engine #8 Catalyst | E2 Energy Services | 1,680 hp | 0.22 lb/hr | 1,557 hp | 0.02 lb/hr | 6348 03 | VOC - Volatile Organic Compounds | PASS | NA | Y
2014 | 2051 | 0656105005 | E2 Appalachian Compression LLC - Reusser | Twp Hwy 68 and Twp Hwy 66 | Woodsfield | 43793 |  | Monroe | P006 | 1680 Hp. natural gas rich burn compressor engine - Waukesha L7044GSI | 2014-12-11 | C-3(Catalytic Converter): Engine #3 Catalyst; C-4(Catalytic Converter): Engine #4 Catalyst; C-5(Catalytic Converter): Engine #5 Catalyst; C-6(Catalytic Converter): Engine #6Catalyst; C-8(Catalytic Converter): Engine #8 Catalyst | E2 Energy Services | 1,680 hp | 0.22 lb/hr | 1,551 hp | 0.02 lb/hr | 6348 03 | VOC - Volatile Organic Compounds | PASS | NA | Y
2014 | 2054 | 0656105005 | E2 Appalachian Compression LLC - Reusser | Twp Hwy 68 and Twp Hwy 66 | Woodsfield | 43793 |  | Monroe | P008 | 1680 Hp. natural gas rich burn compressor engine - Waukesha L7044GSI | 2014-12-11 | C-3(Catalytic Converter): Engine #3 Catalyst; C-4(Catalytic Converter): Engine #4 Catalyst; C-5(Catalytic Converter): Engine #5 Catalyst; C-6(Catalytic Converter): Engine #6Catalyst; C-8(Catalytic Converter): Engine #8 Catalyst | E2 Energy Services | 1,680 hp | 0.22 lb/hr | 1,551 hp | 0.02 lb/hr | 6348 03 | VOC - Volatile Organic Compounds | PASS | NA | Y
2014 | 2058 | 0656105006 | Eclipse Resources 1 LP - Tippens Pad | 40417 Eddy Ridge Road | Woodsfield | 43793 |  | Monroe | P002 | One or multiple stationary natural gas-fired spark ignition (SI) internal combustion engines (ICE) with a combined total horsepower (HP) of no more than 1,800 HP for the site.* Includes 2007 and later model year engines manufactured after the applicable effective date identified in 40 CFR 60.4230(a)(3) and engines manufactured before the NSPS effective date where compliance with the Part 60 Subpart JJJJ emissions standards for the same size engine can be demonstrated through stack testing. | 2014-06-25 | none | Windrock, Inc | 225 Hp Cummins engine | 1.0 g/Hp-hr | 173 Hp | 0.003 g/Hp-hr | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y
2014 | 2072 | 0661005002 | Summerfield Compressor Station | between CR-45 and HWY 233 | Caldwell | 43724 |  | Noble | P001 | Natural Gas Engine(1) 1,380 hp engine | 2014-05-01 | Catalyst 1(Catalytic Converter): Oxidation Catalyst 1;; Flare(Flare): FL-1 | Environmental Quality Management | 1,380 hp | 0.7 g/hp-hr | 889 | 0.295 g/hp-hr | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y
2014 | 2075 | 0661005002 | Summerfield Compressor Station | between CR-45 and HWY 233 | Caldwell | 43724 |  | Noble | P002 | Natural Gas Engine (2) 1,380 hp | 2014-05-01 | Catalyst 2(Catalytic Converter): Oxidation Catalyst; Flare(Flare): FL-1 | Environmental Quality Management | 1,380 hp | 0.7 g/hp-hr | 911 hp | 0.574 g/hp-hr | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y
2014 | 2077 | 0661005008 | Seneca Gas Plant | Zep Road | Summerfield | 43788 |  | Noble | P001 | Compressor Engine #1 - Natural gas-fired four-stroke lean burn (4SLB) internal combustion engine rated at an operating capacity of 4,735 horsepower (hp) and equipped with an oxidation catalyst. | 2014-04-07 | CC001(Catalytic Converter): Compressor Engine #1 - Catalyic Convertor | Air Hygiene International | 4,735 hp | 0.7 g/hp-hr | 4,356 hp | 0.10 g/hp-hr | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y
2014 | 2081 | 0661005008 | Seneca Gas Plant | Zep Road | Summerfield | 43788 |  | Noble | P002 | Compressor Engine #2 - Natural gas-fired four-stroke lean burn (4SLB) internal combustion engine rated at an operating capacity of 4,735 horsepower (hp) and equipped with an oxidation catalyst. | 2014-04-07 | CC002(Catalytic Converter): Compressor Engine #2 - Catalytic Convertor | Air Hygiene International | 4,735 hp | 0.7 g/hp-hr | 4,404 hp | 0.136 g/hp-hr | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y
2014 | 2084 | 0661005010 | E2 Appalachian Compression LLC - Upper Hill | Opossum Run Rd and Town Hwy 120 | Sarahsville | 43779 |  | Noble | P009 | 1,680 Hp. Waukesha (L7044GSI) natural gas-fired, rich burn, turbocharged, with oxidation catalyst, compressor engine. | 2014-07-15 | C-9(Catalytic Converter): Engine Catalyst | E2 Energy Services | 1,680 Hp | 0.22 lb/hr | 1,545 Hp | 0.1 lb/hr | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y
2014 | 2087 | 0661005010 | E2 Appalachian Compression LLC - Upper Hill | Opossum Run Rd and Town Hwy 120 | Sarahsville | 43779 |  | Noble | P007 | 1,680 Hp. Waukesha (L7044GSI) natural gas-fired, rich burn, turbocharged, with oxidation catalyst, compressor engine. | 2014-11-06 | C-7(Catalytic Converter): Engine Catalyst; C-8(Catalytic Converter): Engine Catalyst; C-9(Catalytic Converter): Engine Catalyst | E2 Energy Services | 1680 Hp | 0.22 lb/hr | 1528 Hp | 0.02 lb/hr | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y | Method 25A not used. Method 3A and ASTM 6348-03 used
2014 | 2090 | 0661005010 | E2 Appalachian Compression LLC - Upper Hill | Opossum Run Rd and Town Hwy 120 | Sarahsville | 43779 |  | Noble | P008 | 1,680 Hp. Waukesha (L7044GSI) natural gas-fired, rich burn, turbocharged, with oxidation catalyst, compressor engine. | 2014-11-06 | C-7(Catalytic Converter): Engine Catalyst; C-8(Catalytic Converter): Engine Catalyst; C-9(Catalytic Converter): Engine Catalyst | E2 Energy Services | 1680 Hp | 0.22 lb/hr | 1221 Hp | 0.01 lb/hr | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y | Method 25A not used. Method 3A and ASTM 6348-03 used
2014 | 2092 | 0661005010 | E2 Appalachian Compression LLC - Upper Hill | Opossum Run Rd and Town Hwy 120 | Sarahsville | 43779 |  | Noble | P009 | 1,680 Hp. Waukesha (L7044GSI) natural gas-fired, rich burn, turbocharged, with oxidation catalyst, compressor engine. | 2014-11-06 | C-7(Catalytic Converter): Engine Catalyst; C-8(Catalytic Converter): Engine Catalyst; C-9(Catalytic Converter): Engine Catalyst | E2 Energy Services | 1680 Hp | 0.22 lb/hr | 1585 Hp | 0.02 lb/hr | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y | Method 25A not used. Method 3A and ASTM 6348-03 used
2014 | 2096 | 0661005010 | E2 Appalachian Compression LLC - Upper Hill | Opossum Run Rd and Town Hwy 120 | Sarahsville | 43779 |  | Noble | P004 | 1,680 Hp. Waukesha (L7044GSI) natural gas-fired, rich burn, turbocharged, with oxidation catalyst, compressor engine. | 2014-11-10 | C-4(Catalytic Converter): Engine Catalyst | E2 Energy Services | 1680 Hp | 0.22 lb/hr | 1547 Hp | 0.01 lb/hr | 25B | VOC - Volatile Organic Compounds | PASS | NA | Y | Method 25B not used. Method 3a and ASTM 6348-03 used
2014 | 2098 | 0661005010 | E2 Appalachian Compression LLC - Upper Hill | Opossum Run Rd and Town Hwy 120 | Sarahsville | 43779 |  | Noble | P002 | 1,680 Hp. Waukesha (L7044GSI) natural gas-fired, rich burn, turbocharged, with oxidation catalyst, compressor engine. | 2014-11-12 | C-2(Catalytic Converter): Engine Catalyst; C-3(Catalytic Converter): Engine Catalyst | E2 Energy Services | 1680 Hp | 0.22 lb/hr | 1575 Hp | 0.02 lb/hr | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y | Method 25 A not used. Method 3a and ASTM 6348-03 used
2014 | 2100 | 0661005010 | E2 Appalachian Compression LLC - Upper Hill | Opossum Run Rd and Town Hwy 120 | Sarahsville | 43779 |  | Noble | P003 | 1,680 Hp. Waukesha (L7044GSI) natural gas-fired, rich burn, turbocharged, with oxidation catalyst, compressor engine. | 2014-11-12 | C-2(Catalytic Converter): Engine Catalyst; C-3(Catalytic Converter): Engine Catalyst | E2 Energy Services | 1680 Hp | 0.22 lb/hr | 1512 Hp | 0.02 lb/hr | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y | Method 25 A not used. Method 3a and ASTM 6348-03 used
2014 | 2104 | 0661005010 | E2 Appalachian Compression LLC - Upper Hill | Opossum Run Rd and Town Hwy 120 | Sarahsville | 43779 |  | Noble | P002 | 1,680 Hp. Waukesha (L7044GSI) natural gas-fired, rich burn, turbocharged, with oxidation catalyst, compressor engine. | 2014-11-13 | C-2(Catalytic Converter): Engine Catalyst; C-3(Catalytic Converter): Engine Catalyst | E2 Energy Services | 1680 Hp | 0.22 lb/hr | 1575 Hp | 0.02 lb/hr | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y | Method 25 A not used. Method 3a and ASTM 6348-03 used
2014 | 2108 | 0661005010 | E2 Appalachian Compression LLC - Upper Hill | Opossum Run Rd and Town Hwy 120 | Sarahsville | 43779 |  | Noble | P003 | 1,680 Hp. Waukesha (L7044GSI) natural gas-fired, rich burn, turbocharged, with oxidation catalyst, compressor engine. | 2014-11-13 | C-2(Catalytic Converter): Engine Catalyst; C-3(Catalytic Converter): Engine Catalyst | E2 Energy Services | 1680 Hp | 0.22 lb/hr | 1512 Hp | 0.02 lb/hr | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y | Method 25 A not used. Method 3a and ASTM 6348-03 used
2014 | 2426 | 0857103154 | PINNACLE GAS PRODUCERS LLC | 4220 PINNACLE RD | MORAINE | 45439 |  | Montgomery | B001 | 12 MMBtu/hour (1,626 bhp) pipeline quality gas/natural gas-fired compressor engine | 2014-05-20 | N/A | DTE ENERGY | 1200 RPM | N/A | 856 RPM | 16.81 lb THC/hr | 25A | Total Hydrocarbons | PASS | NA | Y | Fuel BTU Content 978. Method 18 samples were collected for methane emission determination. When subtracted from the total hydrocarbons, it appears that engine emissions are composed primarily of methane and no other VOCs were detected. Average gas process rate for the plant on this date 3.54MMSCF/day.
2014 | 2427 | 0857103154 | PINNACLE GAS PRODUCERS LLC | 4220 PINNACLE RD | MORAINE | 45439 |  | Montgomery | B001 | 12 MMBtu/hour (1,626 bhp) pipeline quality gas/natural gas-fired compressor engine | 2014-05-20 | N/A | DTE ENERGY | 1200 RPM | 5.38 lb NMOC | 856 RPM | ND | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y | Fuel BTU Content 978. Method 18 samples were collected for methane emission determination. When subtracted from the total hydrocarbons, it appears that engine emissions are composed primarily of methane and no other VOCs were detected. Average gas process rate for the plant on this date 3.54MMSCF/day.
2015 | 108 | 0210012002 | Utica Gas Services, LLC-Carrollton Compressor Facility | 2098 Panda Road SE | Carrollton | 44615 |  | Carroll | P008 | 1,775 HP natural gas-fired Caterpillar G3606 engine #5 equipped with an oxidation catalyst | 2015-01-20 | Oxid. Cat.(Catalytic Converter): Oxidative Catalyst | Alliance Source Testing | 1775 HP | 0.82lb/hr, 0.7g/hp-hr | 1602 HP | 0.14 lb/hr, 0.04g/hp-hr | 25A | VOC - Volatile Organic Compounds | PP | NA | Y | Our facility descriptions have the engines numbered incorrectly, however the Manufacture dates correspond across both the report and permit. P013 is engine 3 onsite (10 in the permit), P006-P012 onsite are C4-C10, but in the permit 3-9. However if you follow only ***(EU P###)*** everything is accurate.
2015 | 111 | 0210012002 | Utica Gas Services, LLC-Carrollton Compressor Facility | 2098 Panda Road SE | Carrollton | 44615 |  | Carroll | P009 | 1,775 HP natural gas-fired Caterpillar G3606 engine #6 equipped with an oxidation catalyst | 2015-01-20 | Oxid. Cat.(Catalytic Converter): Oxidative Catalyst | Alliance Source Testing | 1775 HP | 0.82lb/hr, 0.7g/hp-hr | 1656 HP | 0.17 lb/hr, 0.10g/hp-hr | 25A | VOC - Volatile Organic Compounds | PP | NA | Y | Our facility descriptions have the engines numbered incorrectly, however the Manufacture dates correspond across both the report and permit. P013 is engine 3 onsite (10 in the permit), P006-P012 onsite are C4-C10, but in the permit 3-9. However if you follow only ***(EU P###)*** everything is accurate.
2015 | 223 | 0210002071 | Chesapeake Exploration LLC - Kennedy 14-13-5 Pad | OH-9 - Germano Rd | Harlem Springs | 43903 |  | Carroll | P002 | One or multiple stationary natural gas-fired spark ignition (SI) internal combustion engines (ICE) with a combined total horsepower (HP) of no more than 1,800 HP for the site.* Includes 2007 and later model year engines manufactured after the applicable effective date identified in 40 CFR 60.4230(a)(3); and engines manufactured before the effective date of the NSPS, where compliance with the Part 60 Subpart JJJJ emissions standards for the same size engine can be met by retrofitting the engine with a control device and demonstrated through stack testing. | 2015-08-11 | Catalyst | Alliance Source Testing | 630 Hp | 86 ppmvd @ 15% O2 | 422 Hp | 86 ppmvd @ 15% O2 | 25A | VOC - Volatile Organic Compounds | PP | NA | Y
2015 | 224 | 0210012002 | Utica Gas Services, LLC-Carrollton Compressor Facility | 2098 Panda Road SE | Carrollton | 44615 |  | Carroll | P004 | 1,775 HP natural gas-fired Caterpillar G3606 engine #1 equipped with an oxidation catalyst. | 2015-01-20 | Oxid. Cat.(Catalytic Converter): Oxidative Catalyst | Alliance Source Testing | 1775 HP | 0.82lb/hr, 1.0g/hp-hr | 1686 HP | 0.11 lb/hr, 0.03g/hp-hr | 25A | VOC - Volatile Organic Compounds | PP | NA | Y | Our facility descriptions have the engines numbered incorrectly, however the Manufacture dates correspond across both the report and permit. P013 is engine 3 onsite (10 in the permit), P006-P012 onsite are C4-C10, but in the permit 3-9. However if you follow only ***(EU P###)*** everything is accurate.
2015 | 229 | 0210012002 | Utica Gas Services, LLC-Carrollton Compressor Facility | 2098 Panda Road SE | Carrollton | 44615 |  | Carroll | P005 | 1,775 HP natural gas-fired Caterpillar G3606 engine #2 equipped with an oxidation catalyst | 2015-01-20 | Oxid. Cat.(Catalytic Converter): Oxidative Catalyst | Alliance Source Testing | 1775 HP | 0.82lb/hr, 1.0g/hp-hr | 1686 HP | 0.09 lb/hr, 0.02g/hp-hr | 25A | VOC - Volatile Organic Compounds | PP | NA | Y | Our facility descriptions have the engines numbered incorrectly, however the Manufacture dates correspond across both the report and permit. P013 is engine 3 onsite (10 in the permit), P006-P012 onsite are C4-C10, but in the permit 3-9. However if you follow only ***(EU P###)*** everything is accurate.
2015 | 232 | 0210012002 | Utica Gas Services, LLC-Carrollton Compressor Facility | 2098 Panda Road SE | Carrollton | 44615 |  | Carroll | P006 | 1,775 HP natural gas-fired Caterpillar G3606 engine #3 equipped with an oxidation catalyst | 2015-01-20 | Oxid. Cat.(Catalytic Converter): Oxidative Catalyst | Alliance Source Testing | 1775 HP | 0.82lb/hr, 0.7g/hp-hr | 1597 HP | 0.14 lb/hr, 0.04g/hp-hr | 25A | VOC - Volatile Organic Compounds | PP | NA | Y | Our facility descriptions have the engines numbered incorrectly, however the Manufacture dates correspond across both the report and permit. P013 is engine 3 onsite (10 in the permit), P006-P012 onsite are C4-C10, but in the permit 3-9. However if you follow only ***(EU P###)*** everything is accurate.
2015 | 233 | 0210012002 | Utica Gas Services, LLC-Carrollton Compressor Facility | 2098 Panda Road SE | Carrollton | 44615 |  | Carroll | P007 | 1,775 HP natural gas-fired Caterpillar G3606 engine #4 equipped with an oxidation catalyst | 2015-01-20 | Oxid. Cat.(Catalytic Converter): Oxidative Catalyst | Alliance Source Testing | 1775 HP | 0.82lb/hr, 0.7g/hp-hr | 1599 HP | 0.13 lb/hr, 0.04g/hp-hr | 25A | VOC - Volatile Organic Compounds | PP | NA | Y | Our facility descriptions have the engines numbered incorrectly, however the Manufacture dates correspond across both the report and permit. P013 is engine 3 onsite (10 in the permit), P006-P012 onsite are C4-C10, but in the permit 3-9. However if you follow only ***(EU P###)*** everything is accurate.
2015 | 236 | 0210012002 | Utica Gas Services, LLC-Carrollton Compressor Facility | 2098 Panda Road SE | Carrollton | 44615 |  | Carroll | P010 | 1,775 HP natural gas-fired Caterpillar G3606 engine #7 equipped with an oxidation catalyst | 2015-01-20 | Oxid. Cat.(Catalytic Converter): Oxidative Catalyst | Alliance Source Testing | 1775 HP | 0.82lb/hr, 0.7g/hp-hr | 1636 HP | 0.15 lb/hr, 0.04g/hp-hr | 25A | VOC - Volatile Organic Compounds | PP | NA | Y | Our facility descriptions have the engines numbered incorrectly, however the Manufacture dates correspond across both the report and permit. P013 is engine 3 onsite (10 in the permit), P006-P012 onsite are C4-C10, but in the permit 3-9. However if you follow only ***(EU P###)*** everything is accurate.
2015 | 241 | 0210012002 | Utica Gas Services, LLC-Carrollton Compressor Facility | 2098 Panda Road SE | Carrollton | 44615 |  | Carroll | P011 | 1,775 HP natural gas-fired Caterpillar G3606 engine #8 equipped with an oxidation catalyst | 2015-01-20 | Oxid. Cat.(Catalytic Converter): Oxidative Catalyst | Alliance Source Testing | 1775 HP | 0.82lb/hr, 0.7g/hp-hr | 1639 HP | 0.12 lb/hr, 0.03g/hp-hr | 25A | VOC - Volatile Organic Compounds | PP | NA | Y | Our facility descriptions have the engines numbered incorrectly, however the Manufacture dates correspond across both the report and permit. P013 is engine 3 onsite (10 in the permit), P006-P012 onsite are C4-C10, but in the permit 3-9. However if you follow only ***(EU P###)*** everything is accurate.
2015 | 243 | 0210012002 | Utica Gas Services, LLC-Carrollton Compressor Facility | 2098 Panda Road SE | Carrollton | 44615 |  | Carroll | P012 | 1,775 HP natural gas-fired Caterpillar G3606 engine #9 equipped with an oxidation catalyst | 2015-01-20 | Oxid. Cat.(Catalytic Converter): Oxidative Catalyst | Alliance Source Testing | 1775 HP | 0.82lb/hr, 0.7g/hp-hr | 1656 HP | 0.12 lb/hr, 0.03g/hp-hr | 25A | VOC - Volatile Organic Compounds | PP | NA | Y | Our facility descriptions have the engines numbered incorrectly, however the Manufacture dates correspond across both the report and permit. P013 is engine 3 onsite (10 in the permit), P006-P012 onsite are C4-C10, but in the permit 3-9. However if you follow only ***(EU P###)*** everything is accurate.
2015 | 246 | 0210012002 | Utica Gas Services, LLC-Carrollton Compressor Facility | 2098 Panda Road SE | Carrollton | 44615 |  | Carroll | P013 | 1,775 HP natural gas-fired Caterpillar G3606 engine #10equipped with an oxidation catalyst | 2015-01-20 | Oxid. Cat.(Catalytic Converter): Oxidative Catalyst | Alliance Source Testing | 1775 HP | 0.82lb/hr, 0.7g/hp-hr | 1660 HP | 0.14 lb/hr, 0.04g/hp-hr | 25A | VOC - Volatile Organic Compounds | PP | NA | Y | Our facility descriptions have the engines numbered incorrectly, however the Manufacture dates correspond across both the report and permit. P013 is engine 3 onsite (10 in the permit), P006-P012 onsite are C4-C10, but in the permit 3-9. However if you follow only ***(EU P###)*** everything is accurate.
2015 | 250 | 0210012002 | Utica Gas Services, LLC-Carrollton Compressor Facility | 2098 Panda Road SE | Carrollton | 44615 |  | Carroll | P004 | 1,775 HP natural gas-fired Caterpillar G3606 engine #1 equipped with an oxidation catalyst. | 2015-01-21 | Oxid. Cat.(Catalytic Converter): Oxidative Catalyst | Alliance Source Testing | 1775 HP | 0.82lb/hr, 1.0g/hp-hr | 1686 HP | 0.11 lb/hr, 0.03g/hp-hr | 25A | VOC - Volatile Organic Compounds | PP | NA | Y | Our facility descriptions have the engines numbered incorrectly, however the Manufacture dates correspond across both the report and permit. P013 is engine 3 onsite (10 in the permit), P006-P012 onsite are C4-C10, but in the permit 3-9. However if you follow only ***(EU P###)*** everything is accurate.
2015 | 251 | 0210012002 | Utica Gas Services, LLC-Carrollton Compressor Facility | 2098 Panda Road SE | Carrollton | 44615 |  | Carroll | P005 | 1,775 HP natural gas-fired Caterpillar G3606 engine #2 equipped with an oxidation catalyst | 2015-01-21 | Oxid. Cat.(Catalytic Converter): Oxidative Catalyst | Alliance Source Testing | 1775 HP | 0.82lb/hr, 1.0g/hp-hr | 1686 HP | 0.09 lb/hr, 0.02g/hp-hr | 25A | VOC - Volatile Organic Compounds | PP | NA | Y | Our facility descriptions have the engines numbered incorrectly, however the Manufacture dates correspond across both the report and permit. P013 is engine 3 onsite (10 in the permit), P006-P012 onsite are C4-C10, but in the permit 3-9. However if you follow only ***(EU P###)*** everything is accurate.
2015 | 256 | 0210012002 | Utica Gas Services, LLC-Carrollton Compressor Facility | 2098 Panda Road SE | Carrollton | 44615 |  | Carroll | P006 | 1,775 HP natural gas-fired Caterpillar G3606 engine #3 equipped with an oxidation catalyst | 2015-01-21 | Oxid. Cat.(Catalytic Converter): Oxidative Catalyst | Alliance Source Testing | 1775 HP | 0.82lb/hr, 0.7g/hp-hr | 1597 HP | 0.14 lb/hr, 0.04g/hp-hr | 25A | VOC - Volatile Organic Compounds | PP | NA | Y | Our facility descriptions have the engines numbered incorrectly, however the Manufacture dates correspond across both the report and permit. P013 is engine 3 onsite (10 in the permit), P006-P012 onsite are C4-C10, but in the permit 3-9. However if you follow only ***(EU P###)*** everything is accurate.
2015 | 258 | 0210012002 | Utica Gas Services, LLC-Carrollton Compressor Facility | 2098 Panda Road SE | Carrollton | 44615 |  | Carroll | P007 | 1,775 HP natural gas-fired Caterpillar G3606 engine #4 equipped with an oxidation catalyst | 2015-01-21 | Oxid. Cat.(Catalytic Converter): Oxidative Catalyst | Alliance Source Testing | 1775 HP | 0.82lb/hr, 0.7g/hp-hr | 1599 HP | 0.13 lb/hr, 0.04g/hp-hr | 25A | VOC - Volatile Organic Compounds | PP | NA | Y | Our facility descriptions have the engines numbered incorrectly, however the Manufacture dates correspond across both the report and permit. P013 is engine 3 onsite (10 in the permit), P006-P012 onsite are C4-C10, but in the permit 3-9. However if you follow only ***(EU P###)*** everything is accurate.
2015 | 260 | 0210012002 | Utica Gas Services, LLC-Carrollton Compressor Facility | 2098 Panda Road SE | Carrollton | 44615 |  | Carroll | P008 | 1,775 HP natural gas-fired Caterpillar G3606 engine #5 equipped with an oxidation catalyst | 2015-01-21 | Oxid. Cat.(Catalytic Converter): Oxidative Catalyst | Alliance Source Testing | 1775 HP | 0.82lb/hr, 0.7g/hp-hr | 1602 HP | 0.14 lb/hr, 0.04g/hp-hr | 25A | VOC - Volatile Organic Compounds | PP | NA | Y | Our facility descriptions have the engines numbered incorrectly, however the Manufacture dates correspond across both the report and permit. P013 is engine 3 onsite (10 in the permit), P006-P012 onsite are C4-C10, but in the permit 3-9. However if you follow only ***(EU P###)*** everything is accurate.
2015 | 264 | 0210012002 | Utica Gas Services, LLC-Carrollton Compressor Facility | 2098 Panda Road SE | Carrollton | 44615 |  | Carroll | P009 | 1,775 HP natural gas-fired Caterpillar G3606 engine #6 equipped with an oxidation catalyst | 2015-01-21 | Oxid. Cat.(Catalytic Converter): Oxidative Catalyst | Alliance Source Testing | 1775 HP | 0.82lb/hr, 0.7g/hp-hr | 1656 HP | 0.17 lb/hr, 0.10g/hp-hr | 25A | VOC - Volatile Organic Compounds | PP | NA | Y | Our facility descriptions have the engines numbered incorrectly, however the Manufacture dates correspond across both the report and permit. P013 is engine 3 onsite (10 in the permit), P006-P012 onsite are C4-C10, but in the permit 3-9. However if you follow only ***(EU P###)*** everything is accurate.
2015 | 268 | 0210012002 | Utica Gas Services, LLC-Carrollton Compressor Facility | 2098 Panda Road SE | Carrollton | 44615 |  | Carroll | P010 | 1,775 HP natural gas-fired Caterpillar G3606 engine #7 equipped with an oxidation catalyst | 2015-01-21 | Oxid. Cat.(Catalytic Converter): Oxidative Catalyst | Alliance Source Testing | 1775 HP | 0.82lb/hr, 0.7g/hp-hr | 1636 HP | 0.15 lb/hr, 0.04g/hp-hr | 25A | VOC - Volatile Organic Compounds | PP | NA | Y | Our facility descriptions have the engines numbered incorrectly, however the Manufacture dates correspond across both the report and permit. P013 is engine 3 onsite (10 in the permit), P006-P012 onsite are C4-C10, but in the permit 3-9. However if you follow only ***(EU P###)*** everything is accurate.
2015 | 269 | 0210012002 | Utica Gas Services, LLC-Carrollton Compressor Facility | 2098 Panda Road SE | Carrollton | 44615 |  | Carroll | P011 | 1,775 HP natural gas-fired Caterpillar G3606 engine #8 equipped with an oxidation catalyst | 2015-01-21 | Oxid. Cat.(Catalytic Converter): Oxidative Catalyst | Alliance Source Testing | 1775 HP | 0.82lb/hr, 0.7g/hp-hr | 1639 HP | 0.12 lb/hr, 0.03g/hp-hr | 25A | VOC - Volatile Organic Compounds | PP | NA | Y | Our facility descriptions have the engines numbered incorrectly, however the Manufacture dates correspond across both the report and permit. P013 is engine 3 onsite (10 in the permit), P006-P012 onsite are C4-C10, but in the permit 3-9. However if you follow only ***(EU P###)*** everything is accurate.
2015 | 272 | 0210012002 | Utica Gas Services, LLC-Carrollton Compressor Facility | 2098 Panda Road SE | Carrollton | 44615 |  | Carroll | P012 | 1,775 HP natural gas-fired Caterpillar G3606 engine #9 equipped with an oxidation catalyst | 2015-01-21 | Oxid. Cat.(Catalytic Converter): Oxidative Catalyst | Alliance Source Testing | 1775 HP | 0.82lb/hr, 0.7g/hp-hr | 1656 HP | 0.12 lb/hr, 0.03g/hp-hr | 25A | VOC - Volatile Organic Compounds | PP | NA | Y | Our facility descriptions have the engines numbered incorrectly, however the Manufacture dates correspond across both the report and permit. P013 is engine 3 onsite (10 in the permit), P006-P012 onsite are C4-C10, but in the permit 3-9. However if you follow only ***(EU P###)*** everything is accurate.
2015 | 275 | 0210012002 | Utica Gas Services, LLC-Carrollton Compressor Facility | 2098 Panda Road SE | Carrollton | 44615 |  | Carroll | P013 | 1,775 HP natural gas-fired Caterpillar G3606 engine #10equipped with an oxidation catalyst | 2015-01-21 | Oxid. Cat.(Catalytic Converter): Oxidative Catalyst | Alliance Source Testing | 1775 HP | 0.82lb/hr, 0.7g/hp-hr | 1660 HP | 0.14 lb/hr, 0.04g/hp-hr | 25A | VOC - Volatile Organic Compounds | PP | NA | Y | Our facility descriptions have the engines numbered incorrectly, however the Manufacture dates correspond across both the report and permit. P013 is engine 3 onsite (10 in the permit), P006-P012 onsite are C4-C10, but in the permit 3-9. However if you follow only ***(EU P###)*** everything is accurate.
2015 | 280 | 0210012002 | Utica Gas Services, LLC-Carrollton Compressor Facility | 2098 Panda Road SE | Carrollton | 44615 |  | Carroll | P004 | 1,775 HP natural gas-fired Caterpillar G3606 engine #1 equipped with an oxidation catalyst. | 2015-01-22 | Oxid. Cat.(Catalytic Converter): Oxidative Catalyst | Alliance Source Testing | 1775 HP | 0.82lb/hr, 1.0g/hp-hr | 1686 HP | 0.11 lb/hr, 0.03g/hp-hr | 25A | VOC - Volatile Organic Compounds | PP | NA | Y | Our facility descriptions have the engines numbered incorrectly, however the Manufacture dates correspond across both the report and permit. P013 is engine 3 onsite (10 in the permit), P006-P012 onsite are C4-C10, but in the permit 3-9. However if you follow only ***(EU P###)*** everything is accurate.
2015 | 283 | 0210012002 | Utica Gas Services, LLC-Carrollton Compressor Facility | 2098 Panda Road SE | Carrollton | 44615 |  | Carroll | P005 | 1,775 HP natural gas-fired Caterpillar G3606 engine #2 equipped with an oxidation catalyst | 2015-01-22 | Oxid. Cat.(Catalytic Converter): Oxidative Catalyst | Alliance Source Testing | 1775 HP | 0.82lb/hr, 1.0g/hp-hr | 1686 HP | 0.09 lb/hr, 0.02g/hp-hr | 25A | VOC - Volatile Organic Compounds | PP | NA | Y | Our facility descriptions have the engines numbered incorrectly, however the Manufacture dates correspond across both the report and permit. P013 is engine 3 onsite (10 in the permit), P006-P012 onsite are C4-C10, but in the permit 3-9. However if you follow only ***(EU P###)*** everything is accurate.
2015 | 284 | 0210012002 | Utica Gas Services, LLC-Carrollton Compressor Facility | 2098 Panda Road SE | Carrollton | 44615 |  | Carroll | P006 | 1,775 HP natural gas-fired Caterpillar G3606 engine #3 equipped with an oxidation catalyst | 2015-01-22 | Oxid. Cat.(Catalytic Converter): Oxidative Catalyst | Alliance Source Testing | 1775 HP | 0.82lb/hr, 0.7g/hp-hr | 1597 HP | 0.14 lb/hr, 0.04g/hp-hr | 25A | VOC - Volatile Organic Compounds | PP | NA | Y | Our facility descriptions have the engines numbered incorrectly, however the Manufacture dates correspond across both the report and permit. P013 is engine 3 onsite (10 in the permit), P006-P012 onsite are C4-C10, but in the permit 3-9. However if you follow only ***(EU P###)*** everything is accurate.
2015 | 288 | 0210012002 | Utica Gas Services, LLC-Carrollton Compressor Facility | 2098 Panda Road SE | Carrollton | 44615 |  | Carroll | P007 | 1,775 HP natural gas-fired Caterpillar G3606 engine #4 equipped with an oxidation catalyst | 2015-01-22 | Oxid. Cat.(Catalytic Converter): Oxidative Catalyst | Alliance Source Testing | 1775 HP | 0.82lb/hr, 0.7g/hp-hr | 1599 HP | 0.13 lb/hr, 0.04g/hp-hr | 25A | VOC - Volatile Organic Compounds | PP | NA | Y | Our facility descriptions have the engines numbered incorrectly, however the Manufacture dates correspond across both the report and permit. P013 is engine 3 onsite (10 in the permit), P006-P012 onsite are C4-C10, but in the permit 3-9. However if you follow only ***(EU P###)*** everything is accurate.
2015 | 292 | 0210012002 | Utica Gas Services, LLC-Carrollton Compressor Facility | 2098 Panda Road SE | Carrollton | 44615 |  | Carroll | P008 | 1,775 HP natural gas-fired Caterpillar G3606 engine #5 equipped with an oxidation catalyst | 2015-01-22 | Oxid. Cat.(Catalytic Converter): Oxidative Catalyst | Alliance Source Testing | 1775 HP | 0.82lb/hr, 0.7g/hp-hr | 1602 HP | 0.14 lb/hr, 0.04g/hp-hr | 25A | VOC - Volatile Organic Compounds | PP | NA | Y | Our facility descriptions have the engines numbered incorrectly, however the Manufacture dates correspond across both the report and permit. P013 is engine 3 onsite (10 in the permit), P006-P012 onsite are C4-C10, but in the permit 3-9. However if you follow only ***(EU P###)*** everything is accurate.
2015 | 293 | 0210012002 | Utica Gas Services, LLC-Carrollton Compressor Facility | 2098 Panda Road SE | Carrollton | 44615 |  | Carroll | P009 | 1,775 HP natural gas-fired Caterpillar G3606 engine #6 equipped with an oxidation catalyst | 2015-01-22 | Oxid. Cat.(Catalytic Converter): Oxidative Catalyst | Alliance Source Testing | 1775 HP | 0.82lb/hr, 0.7g/hp-hr | 1656 HP | 0.17 lb/hr, 0.10g/hp-hr | 25A | VOC - Volatile Organic Compounds | PP | NA | Y | Our facility descriptions have the engines numbered incorrectly, however the Manufacture dates correspond across both the report and permit. P013 is engine 3 onsite (10 in the permit), P006-P012 onsite are C4-C10, but in the permit 3-9. However if you follow only ***(EU P###)*** everything is accurate.
2015 | 296 | 0210012002 | Utica Gas Services, LLC-Carrollton Compressor Facility | 2098 Panda Road SE | Carrollton | 44615 |  | Carroll | P010 | 1,775 HP natural gas-fired Caterpillar G3606 engine #7 equipped with an oxidation catalyst | 2015-01-22 | Oxid. Cat.(Catalytic Converter): Oxidative Catalyst | Alliance Source Testing | 1775 HP | 0.82lb/hr, 0.7g/hp-hr | 1636 HP | 0.15 lb/hr, 0.04g/hp-hr | 25A | VOC - Volatile Organic Compounds | PP | NA | Y | Our facility descriptions have the engines numbered incorrectly, however the Manufacture dates correspond across both the report and permit. P013 is engine 3 onsite (10 in the permit), P006-P012 onsite are C4-C10, but in the permit 3-9. However if you follow only ***(EU P###)*** everything is accurate.
2015 | 301 | 0210012002 | Utica Gas Services, LLC-Carrollton Compressor Facility | 2098 Panda Road SE | Carrollton | 44615 |  | Carroll | P011 | 1,775 HP natural gas-fired Caterpillar G3606 engine #8 equipped with an oxidation catalyst | 2015-01-22 | Oxid. Cat.(Catalytic Converter): Oxidative Catalyst | Alliance Source Testing | 1775 HP | 0.82lb/hr, 0.7g/hp-hr | 1639 HP | 0.12 lb/hr, 0.03g/hp-hr | 25A | VOC - Volatile Organic Compounds | PP | NA | Y | Our facility descriptions have the engines numbered incorrectly, however the Manufacture dates correspond across both the report and permit. P013 is engine 3 onsite (10 in the permit), P006-P012 onsite are C4-C10, but in the permit 3-9. However if you follow only ***(EU P###)*** everything is accurate.
2015 | 302 | 0210012002 | Utica Gas Services, LLC-Carrollton Compressor Facility | 2098 Panda Road SE | Carrollton | 44615 |  | Carroll | P012 | 1,775 HP natural gas-fired Caterpillar G3606 engine #9 equipped with an oxidation catalyst | 2015-01-22 | Oxid. Cat.(Catalytic Converter): Oxidative Catalyst | Alliance Source Testing | 1775 HP | 0.82lb/hr, 0.7g/hp-hr | 1656 HP | 0.12 lb/hr, 0.03g/hp-hr | 25A | VOC - Volatile Organic Compounds | PP | NA | Y | Our facility descriptions have the engines numbered incorrectly, however the Manufacture dates correspond across both the report and permit. P013 is engine 3 onsite (10 in the permit), P006-P012 onsite are C4-C10, but in the permit 3-9. However if you follow only ***(EU P###)*** everything is accurate.
2015 | 307 | 0210012002 | Utica Gas Services, LLC-Carrollton Compressor Facility | 2098 Panda Road SE | Carrollton | 44615 |  | Carroll | P013 | 1,775 HP natural gas-fired Caterpillar G3606 engine #10equipped with an oxidation catalyst | 2015-01-22 | Oxid. Cat.(Catalytic Converter): Oxidative Catalyst | Alliance Source Testing | 1775 HP | 0.82lb/hr, 0.7g/hp-hr | 1660 HP | 0.14 lb/hr, 0.04g/hp-hr | 25A | VOC - Volatile Organic Compounds | PP | NA | Y | Our facility descriptions have the engines numbered incorrectly, however the Manufacture dates correspond across both the report and permit. P013 is engine 3 onsite (10 in the permit), P006-P012 onsite are C4-C10, but in the permit 3-9. However if you follow only ***(EU P###)*** everything is accurate.
2015 | 309 | 0210012046 | Chesapeake Exploration LLC - Bauer 14-14-6 Pad | Autumn Road SW | Carrollton | 44615 |  | Carroll | P002 | Natural Gas Engines | 2015-04-28 | Catalyst | Alliance Source Testing, Inc. | 211 Hp | 60 ppmvd@ 15 % O2 | 194 Hp or 91.9 % | 0.8 ppmvd@ 15 % O2 | 25A | VOC - Volatile Organic Compounds | PP | NA | Y
2015 | 439 | 0250092002 | City of Struthers WWTP | 530 Lowellville Road | Struthers | 44471 |  | Mahoning | P001 | Stationary internal combustion engine | 2015-03-11 | Catalyst | Custom Stack Analysis | 585 HP as permitted | 1.0 g/hp-hr or 80 ppm @ 15%O2 | 271 hp | .75 g/hp-hr & 37.01 ppm | 25A | VOC - Volatile Organic Compounds | PP | NA | Y
2015 | 443 | 0250092002 | City of Struthers WWTP | 530 Lowellville Road | Struthers | 44471 |  | Mahoning | P002 | Waukesha H24GLD Engine | 2015-03-11 | Catalyst | Custom Stack Analysis | 585 HP as permitted | 1.0 g/hp-hr or 80 ppm @ 15%O2 | 264 hp | .43 g/hp-hr & 22.31 ppm | 25A | VOC - Volatile Organic Compounds | PP | NA | Y
2015 | 451 | 0634005033 | Harrison West Compressor Station | Possum Hollow Road | Freeport | 43973 |  | Harrison | P006 | Compressor Engine #6 - 1980 HP (15.43 MMBtu/hr) Waukesha P9390 - natural gas-fired four-stroke rich burn internal combustion engine equipped with a three-way oxidation catalyst controlling CH2O, CO, NOx, & VOCs by 80, 97, 98.5 & 66 percent respectively | 2015-05-28 | CC006(Catalytic Converter): Compressor Engine #6 - 3-way Catalyst | Air Hygiene International, Inc. | 1980 hp | 0.7 g/hp-hr | 1573 hp | 0.08 g/hp-hr | 25A | VOC - Volatile Organic Compounds | PP | NA | Y
2015 | 452 | 0634005033 | Harrison West Compressor Station | Possum Hollow Road | Freeport | 43973 |  | Harrison | P007 | Compressor Engine #7 - 1980 HP (15.43 MMBtu/hr) Waukesha P9390 - natural gas-fired four-stroke rich burn internal combustion engine equipped with a three-way oxidation catalyst controlling CH2O, CO, NOx, & VOCs by 80, 97, 98.5 & 66 percent respectively | 2015-05-28 | CC007(Catalytic Converter): Compressor Engine #7 - 3-way Catalyst | Air Hygiene International, Inc. | 1980 hp | 0.7 g/hp-hr | 1586 hp | 0.05 g/hp-hr | 24A | VOC - Volatile Organic Compounds | PP | NA | Y
2015 | 454 | 0661005020 | Rockies Express Pipeline - Seneca Compressor Station | Seneca Lake Rd | Quaker City | 43773 |  | Noble | P004 | compressor engine | 2015-05-18 | Engine 5(Catalytic Converter): Compressor Engine 5 Catalytic Convertor; Engine 4(Catalytic Converter): Compressor Engine 4 Catalytic Convertor; | Compressor Engineering Cort. | 5000 hp | 0.07 g/hp-hr | 4728 hp | 0.0075 g/hp-hr | 6348 03 | VOC - Volatile Organic Compounds | PP | NA | Y
2015 | 457 | 0661005020 | Rockies Express Pipeline - Seneca Compressor Station | Seneca Lake Rd | Quaker City | 43773 |  | Noble | P005 | compressor engine | 2015-05-18 | Engine 5(Catalytic Converter): Compressor Engine 5 Catalytic Convertor; Engine 4(Catalytic Converter): Compressor Engine 4 Catalytic Convertor; | Compressor Engineering Cort. | 5000 hp | 0.07 g/hp-hr | 4761 hp | 0.0026 g/hp-hr | 6348 03 | VOC - Volatile Organic Compounds | PP | NA | Y
2015 | 475 | 0250092002 | City of Struthers WWTP | 530 Lowellville Road | Struthers | 44471 |  | Mahoning | P001 | Stationary internal combustion engine | 2015-03-12 | Catalyst | Custom Stack Analysis | 585 HP as permitted | 1.0 g/hp-hr or 80 ppm @ 15%O2 | 271 hp | .75 g/hp-hr & 37.01 ppm | 25A | VOC - Volatile Organic Compounds | PP | NA | Y
2015 | 478 | 0250092002 | City of Struthers WWTP | 530 Lowellville Road | Struthers | 44471 |  | Mahoning | P002 | Waukesha H24GLD Engine | 2015-03-12 | Catalyst | Custom Stack Analysis | 585 HP as permitted | 1.0 g/hp-hr or 80 ppm @ 15%O2 | 264 hp | .43 g/hp-hr & 22.31 ppm | 25A | VOC - Volatile Organic Compounds | PP | NA | Y
2015 | 528 | 0285000366 | East Ohio Gas - Chippewa Station | 17045 Galehouse Road | Doylestown | 44230 |  | Wayne | B010 | 2,370 hp 4SLB SI ICE; CAT G3608 | 2015-05-20 | Engine 5 Converter(Catalytic Converter): Engine #5; Cat B010(Catalytic Converter): Catalytic Converter for B010, engine #6; Catalytic(Catalytic Converter): Engine 7 Catalytic converter | Air/Compliance Consultants, Inc. | 2370 Hp | 86 ppm@15% O2 or 1.0g/bhp-hr 93% | 2225 Hp | 47.3 ppm@15% O2 and 0.017g/bhp-hr 94.5 % | 25A | VOC - Volatile Organic Compounds | PP | NA | Y | B009-2.5 Catalyst Pressure and 880 degF Catalyst temp, B010-3.0 Catalyst Pressure and 880 degF Catalyst temp, B014-1.0 Catalyst Pressure and 870 degF Catalyst Temperature
2015 | 532 | 0285000366 | East Ohio Gas - Chippewa Station | 17045 Galehouse Road | Doylestown | 44230 |  | Wayne | B014 | 2,370 hp 4SLB SI ICE: CAT 3608 w/catalyst | 2015-05-20 | Engine 5 Converter(Catalytic Converter): Engine #5; Cat B010(Catalytic Converter): Catalytic Converter for B010, engine #6; Catalytic(Catalytic Converter): Engine 7 Catalytic converter | Air/Compliance Consultants, Inc. | 2370 Hp | 60 ppm @15%O2 or 0.7 g/bhp-hr 93% | 2241 Hp | 41.9 ppm @15%O2 and 0.14 g/bhp-hr 98.4 % | 25A | VOC - Volatile Organic Compounds | PP | NA | Y | B009-2.5 Catalyst Pressure and 880 degF Catalyst temp, B010-3.0 Catalyst Pressure and 880 degF Catalyst temp, B014-1.0 Catalyst Pressure and 870 degF Catalyst Temperature
2015 | 538 | 0285000388 | East Ohio Gas Company - Paint | STATE RTE 250 | Wooster | 44624 |  | Wayne | B002 | Natural gas fired Internal Combustion Engine with max input capacity of 11.9 MMBtu/hr - Caterpillar G3516TALE with 1340 HP, 4-stroke, selective catalytic reduction (SCR) | 2015-07-14 | Three way Catalyst; CatOx(Catalytic Converter): Catalytic oxidizer for Engine 2 | Environmental Quality Management | 1340 HP | 1.0 g/bhp-hr or 86ppmvd@ 15% O2 | 1236 HP or 92.2 | 0.064 g/bhp-hr or 19.7 ppmvd@ 15% O2 | 25A | VOC - Volatile Organic Compounds | PP | NA | Y
2015 | 692 | 0607005016 | Barnesville West Compressor Station | Hwy 801 | Warren Twp. | 43713 |  | Belmont | P006 | Compressor Engine #1 - Natural gas-fired four-stroke lean burn (4SLB) internal combustion engine rated at an operating capacity of 2,370 horsepower (hp) and equipped with an oxidation catalyst | 2015-03-25 | CC001(Catalytic Converter): Compressor Engine #1 Catalytic Converter | Air Hygiene Internatinal, Inc | 2370 hp | 0.28 g/hp-hr | 2179 hp | 0.19 g/hp-hr | 25A | VOC - Volatile Organic Compounds | PP | NA | Y
2015 | 695 | 0607005016 | Barnesville West Compressor Station | Hwy 801 | Warren Twp. | 43713 |  | Belmont | P007 | Compressor Engine #1 - Natural gas-fired four-stroke lean burn (4SLB) internal combustion engine rated at an operating capacity of 2,370 horsepower (hp) and equipped with an oxidation catalyst | 2015-03-25 | CC002(Catalytic Converter): Compressor Engine #2 Catalytic Converter | Air Hygiene International, Inc | 2,370 hp | 0.28 g/hp-hr | 2,199 hp | 0.21 g/hp-hr | 25A | VOC - Volatile Organic Compounds | PP | NA | Y
2015 | 699 | 0607005016 | Barnesville West Compressor Station | Hwy 801 | Warren Twp. | 43713 |  | Belmont | P008 | Compressor Engine #3 - Natural gas-fired four-stroke lean burn (4SLB) internal combustion engine rated at an operating capacity of 2,370 horsepower (hp) and equipped with an oxidation catalyst | 2015-03-26 | CC003(Catalytic Converter): Compressor Engine #3 Catalytic Converter | Air Hygiene International, Inc | 2,370 hp | 0.28 g/hp-hr | 2,174 hp | 0.03 g/hp-hr | 25A | VOC - Volatile Organic Compounds | PP | NA | Y
2015 | 702 | 0607005016 | Barnesville West Compressor Station | Hwy 801 | Warren Twp. | 43713 |  | Belmont | P009 | Compressor Engine #4 - Natural gas-fired four-stroke lean burn (4SLB) internal combustion engine rated at an operating capacity of 2,370 horsepower (hp) and equipped with an oxidation catalyst | 2015-03-26 | CC004(Catalytic Converter): Compressor Engine #4 Catalytic Converter | Air Hygiene International, Inc | 2,370 hp | 0.28 g/hp-hr | 2,188 hp | 0.19 g/hp-hr | 25A | VOC - Volatile Organic Compounds | PP | NA | Y
2015 | 705 | 0607005016 | Barnesville West Compressor Station | Hwy 801 | Warren Twp. | 43713 |  | Belmont | P010 | Compressor Engine #5 - Natural gas-fired four-stroke lean burn (4SLB) internal combustion engine rated at an operating capacity of 2,370 horsepower (hp) and equipped with an oxidation catalyst | 2015-03-27 | CC005(Catalytic Converter): Compressor Engine #5 Catalytic Converter | Air Hygiene International, Inc | 2,370 hp | 0.28 g/hp-hr | 2,204 hp | 0.18 g/hp-hr | 25A | VOC - Volatile Organic Compounds | PP | NA | Y
2015 | 709 | 0607005016 | Barnesville West Compressor Station | Hwy 801 | Warren Twp. | 43713 |  | Belmont | P011 | Compressor Engine #6 - Natural gas-fired four-stroke lean burn (4SLB) internal combustion engine rated at an operating capacity of 2,370 horsepower (hp) and equipped with an oxidation catalyst | 2015-03-27 | CC006(Catalytic Converter): Compressor Engine #6 Catalytic Converter | Air Hygiene International, Inc | 2,370 hp | 0.28 g/hp-hr | 2,309 hp | 0.19 g/hp-hr | 25A | VOC - Volatile Organic Compounds | PP | NA | Y
2015 | 710 | 0607015003 | Gulfport Energy- Shugert 12 Well Pad | 65800 Mt. Olivett Road | Barnesville | 43713 |  | Belmont | P002 | One or multiple stationary natural gas-fired spark ignition (SI) internal combustion engines (ICE) with a combined total horsepower (HP) of no more than 1,800 HP for the site. | 2015-06-25 | none | Great Plains Services | 118 hp | 1.0 g/hp-hr | 91 hp | 0.006 g/hp-hr | 6348 03 | VOC - Volatile Organic Compounds | PP | NA | Y
2015 | 714 | 0607015007 | Humphreys Compressor Station | Johnson Ridge Rd | Barnesville | 43713 |  | Belmont | P001 | Compressor Engine #1 - Caterpillar G3612TA - natural gas fired four-stroke, lean burn internal combustion engine rated at an operating capacity of 3,550 horsepower equipped with a double oxidation catalyst. | 2015-04-14 | CC001(Catalytic Converter): Compressor Engine #1 - Oxidation Catalyst | Air Hygiene, Inc. | 3550 hp | 0.7 g/hp-hr | 3290 hp | 0.06 g/hp-hr | 25A | VOC - Volatile Organic Compounds | PP | NA | Y
2015 | 718 | 0607015007 | Humphreys Compressor Station | Johnson Ridge Rd | Barnesville | 43713 |  | Belmont | P002 | Compressor Engine #1 - Caterpillar G3612TA - natural gas fired four-stroke, lean burn internal combustion engine rated at an operating capacity of 3,550 horsepower equipped with a double oxidation catalyst. | 2015-04-14 | CC002(Catalytic Converter): Compressor Engine #2 - Oxidation Catalyst | Air Hygiene, Inc. | 3550 hp | 0.7 g/hp-hr | 3307 hp | 0.07 g/hp-hr | 25A | VOC - Volatile Organic Compounds | PP | NA | Y
2015 | 720 | 0607015007 | Humphreys Compressor Station | Johnson Ridge Rd | Barnesville | 43713 |  | Belmont | P003 | Compressor Engine #1 - Caterpillar G3612TA - natural gas fired four-stroke, lean burn internal combustion engine rated at an operating capacity of 3,550 horsepower equipped with a double oxidation catalyst. | 2015-04-15 | CC003(Catalytic Converter): Compressor Engine #3 - Oxidation Catalyst | Air Hygiene, Inc. | 3550 hp | 0.7 g/hp-hr | 3294 hp | 0.06 g/hp-hr | 25A | VOC - Volatile Organic Compounds | PP | NA | Y
2015 | 740 | 0630005042 | Gulfport Energy - Miller Well Pad | Jasper Rd | Londonderry Twp. | 43973 |  | Guernsey | P002 | One 50-hp Zenith ZPP416 and one 203-hp Caterpillar G3306B NA natural gas-fired engines for compressors. One or multiple stationary natural gas-fired spark ignition (SI) internal combustion engines (ICE) wiht a combined total horsepower (HP) or no more than 1,800 HP for the site. | 2015-06-26 | catalyst | Great Plains Analytical Services | 118 hp | 1.0 g/hp-hr | 87 hp | 0.015 g/hp-hr | 6348 03 | VOC - Volatile Organic Compounds | PP | NA | N
2015 | 744 | 0630005042 | Gulfport Energy - Miller Well Pad | Jasper Rd | Londonderry Twp. | 43973 |  | Guernsey | P002 | One 50-hp Zenith ZPP416 and one 203-hp Caterpillar G3306B NA natural gas-fired engines for compressors. One or multiple stationary natural gas-fired spark ignition (SI) internal combustion engines (ICE) wiht a combined total horsepower (HP) or no more than 1,800 HP for the site. | 2015-06-27 | catalyst | Great Plains Analytical Services | 118 hp | 1.0 g/hp-hr | 85 hp | 0.105 g/hp-hr | 6348 03 | VOC - Volatile Organic Compounds | PP | NA | N | test date was actually 6-26-2015. To input data for engines that share a P002 number you have to change date or something. If I use 6-26-2015 information will not be accepted because these two engine both are P002 unit numbers-tow engines with hp of less than 1800 hp for site
2015 | 746 | 0630005043 | Gulfport Energy - Ripley Well Pad | Shipley Rd | Londonderry Twp. | 43973 |  | Guernsey | P002 | One 50-hp Zenith ZPP416 and one 203-hp Caterpillar G3306B NA natural gas-fired engines for compressors. One or multiple stationary natural gas-fired spark ignition (SI) internal combustion engines (ICE) wiht a combined total horsepower (HP) or no more than 1,800 HP for the site. | 2015-03-20 | NSCR | Great Plains Analytical Services | 118 hp | 1.0 g/hp-hr | 118 hp | 0.50 g/hp-hr | 6348 03 | VOC - Volatile Organic Compounds | PP | NA | Y
2015 | 756 | 0634005027 | Arrowhead Compressor Station | E of Clements Rd and S of Jockey Hollow | Athens Twp. | 43977 |  | Harrison | P006 | Compressor Engine #3 - Caterpillar G3608 - natural gas fired four-stroke, lean burn internal combustion engine rated at an operating capacity of 2,370 horsepower equipped with a catalytic convertor. | 2015-04-13 | CC003(Catalytic Converter): Compressor Engine #3 Catalytic Convertor; CC004(Catalytic Converter): Compressor Engine #4 Catalytic Convertor | Air Hygiene, Inc. | 2370 hp | 0.28 g/hp-hr | 2223 hp | 0.19 g/hp-hr | 25A | VOC - Volatile Organic Compounds | PP | NA | Y
2015 | 759 | 0634005027 | Arrowhead Compressor Station | E of Clements Rd and S of Jockey Hollow | Athens Twp. | 43977 |  | Harrison | P007 | Compressor Engine #4 - Caterpillar G3608 - natural gas fired four-stroke, lean burn internal combustion engine rated at an operating capacity of 2,370 horsepower equipped with a catalytic convertor | 2015-04-13 | CC003(Catalytic Converter): Compressor Engine #3 Catalytic Convertor; CC004(Catalytic Converter): Compressor Engine #4 Catalytic Convertor | Air Hygiene, Inc. | 2370 hp | 0.28 g/hp-hr | 2180 hp | 0.27 g/hp-hr | 25A | VOC - Volatile Organic Compounds | PP | NA | Y
2015 | 760 | 0634005033 | Harrison West Compressor Station | Possum Hollow Road | Freeport | 43973 |  | Harrison | P001 | Compressor Engine #1 - 1480 HP (11.39 MMBtu/hr) Waukesha L7042 - natural gas-fired four-stroke rich burn internal combustion engine equipped with a three-way oxidation catalyst controlling CH2O, CO, NOx, & VOCs by 80, 97, 98.5 & 66 percent respectively | 2015-05-26 | CC001(Catalytic Converter): Compressor Engine #1 - 3-way Catalyst | Air Hygiene International, Inc. | 1480 hp | 0.7 g/hp-hr | 1165 hp | 0.12 g/hp-hr | 25A | VOC - Volatile Organic Compounds | PP | NA | Y
2015 | 764 | 0634005033 | Harrison West Compressor Station | Possum Hollow Road | Freeport | 43973 |  | Harrison | P003 | Compressor Engine #3 - 1980 HP (15.43 MMBtu/hr) Waukesha P9390 - natural gas-fired four-stroke rich burn internal combustion engine equipped with a three-way oxidation catalyst controlling CH2O, CO, NOx, & VOCs by 80, 97, 98.5 & 66 percent respectively | 2015-05-26 | CC003(Catalytic Converter): Compressor Engine #3 - 3-way Catalyst | Air Hygiene International, Inc. | 1661 hp | 0.7 g/hp-hr | 1661 hp | 0.09 g/hp-hr | 25A | VOC - Volatile Organic Compounds | PP | NA | Y
2015 | 767 | 0634005033 | Harrison West Compressor Station | Possum Hollow Road | Freeport | 43973 |  | Harrison | P004 | Compressor Engine #4 - 1980 HP (15.43 MMBtu/hr) Waukesha P9390 - natural gas-fired four-stroke rich burn internal combustion engine equipped with a three-way oxidation catalyst controlling CH2O, CO, NOx, & VOCs by 80, 97, 98.5 & 66 percent respectively | 2015-05-27 | CC004(Catalytic Converter): Compressor Engine #4 - 3-way Catalyst | Air Hygiene International, Inc. | 1980 hp | 0.7 g/hp-hr | 1636 hp | 0.06 g/hp-hr | 25A | VOC - Volatile Organic Compounds | PP | NA | Y
2015 | 769 | 0634005033 | Harrison West Compressor Station | Possum Hollow Road | Freeport | 43973 |  | Harrison | P005 | Compressor Engine #5 - 1980 HP (15.43 MMBtu/hr) Waukesha P9390 - natural gas-fired four-stroke rich burn internal combustion engine equipped with a three-way oxidation catalyst controlling CH2O, CO, NOx, & VOCs by 80, 97, 98.5 & 66 percent respectively | 2015-05-27 | CC005(Catalytic Converter): Compressor Engine #5 - 3-way Catalyst | Air Hygiene International, Inc. | 1980 hp | 0.7 g/hp-hr | 1636 hp | 0.06 g/hp-hr | 25A | VOC - Volatile Organic Compounds | PP | NA | Y
2015 | 772 | 0634005034 | Lake Compressor Station | County Highway 21 | Freeport | 43973 |  | Harrison | P001 | Compressor Engine #1 - 1480 HP (11.39 MMBtu/hr) Waukesha L7042 - natural gas-fired four-stroke rich burn internal combustion engine equipped with a three-way oxidation catalyst controlling CH2O, CO, NOx, & VOCs by 80, 97, 98.5 & 66 percent respectively | 2015-04-16 | CC001(Catalytic Converter): Compressor Engine #1 - 3-way Catalyst | Air Hygiene, Inc. | 1480 hp | 0.7 g/hp-hr | 1207 hp | 0.09 g/hp-hr | 25A | VOC - Volatile Organic Compounds | PP | NA | Y
2015 | 776 | 0634005034 | Lake Compressor Station | County Highway 21 | Freeport | 43973 |  | Harrison | P005 | Compressor Engine #5 - 1980 HP (15.43 MMBtu/hr) Waukesha P9390 - natural gas-fired four-stroke rich burn internal combustion engine equipped with a three-way oxidation catalyst controlling CH2O, CO, NOx, & VOCs by 80, 97, 98.5 & 66 percent respectively | 2015-04-16 | CC005(Catalytic Converter): Compressor Engine #5 - 3-way Catalyst; | Air Hygiene, Inc. | 1980 hp | 0.7 g/hp-hr | 1617 hp | 0.09 g/hp-hr | 25A | VOC - Volatile Organic Compounds | PP | NA | Y
2015 | 778 | 0634005034 | Lake Compressor Station | County Highway 21 | Freeport | 43973 |  | Harrison | P011 | Compressor Engine #9 - Waukesha L7042 - natural gas fired four-stroke, rich burn internal combustion engine rated at an operating capacity of 1,480 horsepower equipped with a three-way oxidation catalyst. | 2015-04-16 | CC011(Catalytic Converter): Compressor Engine #9 - 3-way Catalyst | Air Hygiene, Inc. | 1480 hp | 0.7 g/hp-hr | 1166 hp | 0.02 g/hp-hr | 25A | VOC - Volatile Organic Compounds | PP | NA | Y
2015 | 781 | 0634005034 | Lake Compressor Station | County Highway 21 | Freeport | 43973 |  | Harrison | P002 | Compressor Engine #2 - 1480 HP (11.39 MMBtu/hr) Waukesha L7042 - natural gas-fired four-stroke rich burn internal combustion engine equipped with a three-way oxidation catalyst controlling CH2O, CO, NOx, & VOCs by 80, 97, 98.5 & 66 percent respectively | 2015-04-17 | CC002(Catalytic Converter): Compressor Engine #2 - 3-way Catalyst | Air Hygiene, Inc. | 1480 hp | 0.7 g/h-hr | 1114 hp | 0.14 g/hp-hr | 25A | VOC - Volatile Organic Compounds | PP | NA | Y
2015 | 783 | 0634005034 | Lake Compressor Station | County Highway 21 | Freeport | 43973 |  | Harrison | P004 | Compressor Engine #4 - 1980 HP (15.43 MMBtu/hr) Waukesha P9390 - natural gas-fired four-stroke rich burn internal combustion engine equipped with a three-way oxidation catalyst controlling CH2O, CO, NOx, & VOCs by 80, 97, 98.5 & 66 percent respectively | 2015-04-17 | CC004(Catalytic Converter): Compressor Engine #4 - 3-way Catalyst | Air Hygiene, Inc. | 1980 hp | 0.7 g/hp-hr | 1626 hp | 0.07 g/hp-hr | 25A | VOC - Volatile Organic Compounds | PP | NA | Y
2015 | 788 | 0634005048 | Gulfport Energy- Boy Scout Well Pad | 79900 Adams Rd | Tippecanoe | 44699 |  | Harrison | P002 | One 60 hp Waukesha 310 and one 64 hp HEC 3491-OPV natural gas engines for compressors | 2015-06-23 | catalyst | Great Plains Analytical Services | 118 hp | 1.0 g/hp-hr | 92 hp | 0.070 g/hp-hr | 6348 03 | VOC - Volatile Organic Compounds | PP | NA | Y | 118 hp Cummins engine, serial number 46639148
2015 | 792 | 0634005049 | Gulfport Energy- Ryser #1-25H Well Pad | 77100 Scott Hill Road | Flushing | 43977 |  | Harrison | P002 | One or multiple stationary natural gas-fired spark ignition (SI) internal combustion engines (ICE) with a combined total horsepower (HP) of no more than 1,800 HP for the site. | 2015-06-24 | catalyst | Great Plains Analytical Services | 425 hp | 1.0 g/hp-hr | 353 hp | 0.795 hp | 6348 03 | VOC - Volatile Organic Compounds | PP | NA | Y
2015 | 795 | 0634005056 | Scio Compressor Station | 37650 Bower Rd | Scio | 43988 |  | Harrison | P003 | Compressor Engine #3 - 1,775 HP Caterpillar G3606 (4S-LB) - natural gas-fired four-cycle lean burn internal combustion engine equipped with an oxidation catalyst controlling CO & VOC emissions | 2015-06-22 | CC003(Catalytic Converter): Compressor Engine #3 - Oxidation Catalyst | Alliance Source Testing | 1775 hp | 0.14 g/hp-hr | 1615 hp | 0.01 g/hp-hr | 25A | VOC - Volatile Organic Compounds | PP | NA | Y
2015 | 799 | 0634005056 | Scio Compressor Station | 37650 Bower Rd | Scio | 43988 |  | Harrison | P006 | Compressor Engine #6 - 1,775 HP Caterpillar G3606 (4S-LB) - natural gas-fired four-cycle lean burn internal combustion engine equipped with an oxidation catalyst controlling CO & VOC emissions | 2015-06-22 | CC006(Catalytic Converter): Compressor Engine #6 - Oxidation Catalyst | Alliance Source Testing | 1775 hp | 0.14 g/hp-hr | 1609 hp | 0.01 g/hp-hr | 25A | VOC - Volatile Organic Compounds | PP | NA | Y
2015 | 800 | 0634005056 | Scio Compressor Station | 37650 Bower Rd | Scio | 43988 |  | Harrison | P002 | Compressor Engine #2 - 1,775 HP Caterpillar G3606 (4S-LB) - natural gas-fired four-cycle lean burn internal combustion engine equipped with an oxidation catalyst controlling CO & VOC emissions | 2015-06-23 | CC002(Catalytic Converter): Compressor Engine #2 - Oxidation Catalyst | Alliance Source Testing | 1775 hp | 0.14 g/hp-hr | 1598 hp | 0.01 g/hp-hr | 25A | VOC - Volatile Organic Compounds | PP | NA | Y
2015 | 804 | 0634005056 | Scio Compressor Station | 37650 Bower Rd | Scio | 43988 |  | Harrison | P008 | Compressor Engine #8 - 1,775 HP Caterpillar G3606 (4S-LB) - natural gas-fired four-cycle lean burn internal combustion engine equipped with an oxidation catalyst controlling CO & VOC emissions | 2015-06-23 | CC008(Catalytic Converter): Compressor Engine #8 - Oxidation Catalyst | Alliance Source Testing | 1775 hp | 0.14 g/hp-hr | 1598 hp | 0.02 g/hp-hr | 25A | VOC - Volatile Organic Compounds | PP | NA | Y
2015 | 806 | 0634005056 | Scio Compressor Station | 37650 Bower Rd | Scio | 43988 |  | Harrison | P010 | Compressor Engine #10 - 1,775 HP Caterpillar G3606 (4S-LB) - natural gas-fired four-cycle lean burn internal combustion engine equipped with an oxidation catalyst controlling CO & VOC emissions | 2015-06-23 | CC010(Catalytic Converter): Compressor Engine #10 - Oxidation Catalyst | Alliance Source Testing | 1775 hp | 0.14 g/hp-hr | 1598 hp | 0.02 g/hp-hr | 25A | VOC - Volatile Organic Compounds | PP | NA | Y
2015 | 809 | 0634005056 | Scio Compressor Station | 37650 Bower Rd | Scio | 43988 |  | Harrison | P004 | Compressor Engine #4 - 1,775 HP Caterpillar G3606 (4S-LB) - natural gas-fired four-cycle lean burn internal combustion engine equipped with an oxidation catalyst controlling CO & VOC emissions | 2015-07-01 | CC004(Catalytic Converter): Compressor Engine #4 - Oxidation Catalyst | Alliance Source Testing | 1775 hp | 0.14 g/hp-hr | 1609 hp | 0.02 g/hp-hr | 25A | VOC - Volatile Organic Compounds | PP | NA | Y
2015 | 812 | 0634005056 | Scio Compressor Station | 37650 Bower Rd | Scio | 43988 |  | Harrison | P005 | Compressor Engine #5 - 1,775 HP Caterpillar G3606 (4S-LB) - natural gas-fired four-cycle lean burn internal combustion engine equipped with an oxidation catalyst controlling CO & VOC emissions | 2015-07-01 | CC005(Catalytic Converter): Compressor Engine #5 - Oxidation Catalyst | Alliance Source Testing | 1775 hp | 0.14 g/hp-hr | 1621 hp | 0.03 g/hp-hr | 25A | VOC - Volatile Organic Compounds | PP | NA | Y
2015 | 815 | 0634005056 | Scio Compressor Station | 37650 Bower Rd | Scio | 43988 |  | Harrison | P007 | Compressor Engine #7 - 1,775 HP Caterpillar G3606 (4S-LB) - natural gas-fired four-cycle lean burn internal combustion engine equipped with an oxidation catalyst controlling CO & VOC emissions | 2015-07-01 | CC007(Catalytic Converter): Compressor Engine #7 - Oxidation Catalyst | Alliance Source Testing | 1775 hp | 0.14 g/hp-hr | 1722 hp | 0.02 g/hp-hr | 25A | VOC - Volatile Organic Compounds | PP | NA | Y
2015 | 820 | 0634005056 | Scio Compressor Station | 37650 Bower Rd | Scio | 43988 |  | Harrison | P009 | Compressor Engine #9 - 1,775 HP Caterpillar G3606 (4S-LB) - natural gas-fired four-cycle lean burn internal combustion engine equipped with an oxidation catalyst controlling CO & VOC emissions | 2015-07-01 | CC009(Catalytic Converter): Compressor Engine #9 - Oxidation Catalyst | Alliance Source Testing | 1775 hp | 0.14 g/hp-hr | 1728 hp | 0.03 g/hp-hr | 25A | VOC - Volatile Organic Compounds | PP | NA | Y
2015 | 823 | 0634005056 | Scio Compressor Station | 37650 Bower Rd | Scio | 43988 |  | Harrison | P001 | Compressor Engine #1 - 1,775 HP Caterpillar G3606 (4S-LB) - natural gas-fired four-cycle lean burn internal combustion engine equipped with an oxidation catalyst controlling CO & VOC emissions. | 2015-07-02 | CC001(Catalytic Converter): Compressor Engine #1 - Oxidation Catalyst | Alliance Source Testing | 1775 hp | 0.14 g/hp-hr | 1745 hp | 0.01 g/hp-hr | 25A | VOC - Volatile Organic Compounds | PP | NA | Y
2015 | 826 | 0634005069 | Gulfport Energy - Arrowhead II - Darla | 65800 Mt. Olivett Road | Flushing | 43977 |  | Harrison | P002 | One or multiple stationary natural gas-fired spark ignition (SI) internal combustion engines (ICE) with a combined total horsepower (HP) of no more than 1,800 HP for the site.* Includes 2007 and later model year engines manufactured after the applicable effective date identified in 40 CFR 60.4230(a)(3) and engines manufactured before the NSPS effective date where compliance with the Part 60 Subpart JJJJ emissions standards for the same size engine can be demonstrated through stack testing. | 2015-03-19 | NSCR | Great Plains Analytical | 118 hp | 1.0 g/hp-hr | 99 hp | 0.015 g/hp-hr | 6348 03 | VOC - Volatile Organic Compounds | PP | NA | Y
2015 | 829 | 0634005070 | Gulfport Energy - County Line II - Gustina-Bear | 34011 Cadiz-Piedmont Rd | Flushing | 43977 |  | Harrison | P002 | One or multiple stationary natural gas-fired spark ignition (SI) internal combustion engines (ICE) wiht a combined total horsepower (HP) of no more than 1,800 HP for the site. | 2015-03-18 | NSCR | Great Plains Analytical Services | 118 hp | 1.0 g/hp-hr | 57 hp | 0.039 g/hp-hr | 6348 03 | VOC - Volatile Organic Compounds | PP | NA | N
2015 | 833 | 0634005071 | Gulfport Energy - County Line - Puskarich | 76015 Moorefield Hill Rd | Flushing | 43977 |  | Harrison | P002 | One or multiple stationary natural gas-fired spark ignition (SI) internal combustion engines (ICE) with a combined total horsepower (HP) of no more than 1,000 HP for the site.* Includes 2007 and later model year engines manufactured after the applicable effective date identified in 40 CFR 60.4230(a)(3); and engines manufactured before the effective date of the NSPS, where compliance with the Part 60 Subpart JJJJ emissions standards for the same size engine can be met by retrofitting the engine with a control device and demonstrated through stack testing. | 2015-03-17 | NSCR | Great Plains Analytical Services | 118 hp | 1.0 g/hp-hr | 103 hp | 0.007 g/hp-hr | 6348 03 | VOC - Volatile Organic Compounds | PP | NA | Y
2015 | 836 | 0634005090 | E2 Ohio Compression LLC - Mizer | 84500 Addy Rd | Cadiz | 43907 |  | Harrison | P002 | One or multiple stationary natural gas-fired spark ignition (SI) internal combustion engines (ICE) with a combined total horsepower (HP) of no more than 1,800 HP for the site. Includes 2007 and later model year engines manufactured after the applicable effective date identified in 40 CFR 60.4230(a)(3) and engines manufactured before the NSPS effective date where compliance with the Part 60 Subpart JJJJ emission standards for the same size engine can be demonstrated through stack testing | 2015-02-12 | Cat01(Catalytic Converter): Oxidation Catalyst for 4SLB RICE | E2 Energy Services | 680 hp | 1.0 g/hp-hr | 675 hp | 0.01 g/hp-hr | 6348 03 | VOC - Volatile Organic Compounds | PP | NA | Y
2015 | 839 | 0634005101 | Chesapeake Exploration LLC - Trushell 8-13-6 Pad | OH-151E Scio Bowerston Rd | Scio | 43988 |  | Harrison | P002 | One or multiple stationary natural gas-fired spark ignition (SI) internal combustion engines (ICE) with a combined total horsepower (HP) of no more than 1,800 HP for the site.* Includes 2007 and later model year engines manufactured after the applicable effective date identified in 40 CFR 60.4230(a)(3); and engines manufactured before the effective date of the NSPS, where compliance with the Part 60 Subpart JJJJ emissions standards for the same size engine can be met by retrofitting the engine with a control device and demonstrated through stack testing. | 2015-04-29 | NSCR | Alliance Source Testing | 211 hp | 1.0 g/hp-hr | 192 hp | 0.01 g/hp-hr | 25A | VOC - Volatile Organic Compounds | PP | NA | Y | alt. method 106 used. method 25A incorporated by reference
2015 | 843 | 0634005103 | Gulfport Energy - Davidson | Possom Hollow Rd | Freeport | 43977 |  | Harrison | P002 | One or multiple stationary natural gas-fired spark ignition (SI) internal combustion engines (ICE) with a combined total horsepower (HP) of no more than 1,000 HP for the site.* Includes 2007 and later model year engines manufactured after the applicable effective date identified in 40 CFR 60.4230(a)(3); and engines manufactured before the effective date of the NSPS, where compliance with the Part 60 Subpart JJJJ emissions standards for the same size engine can be met by retrofitting the engine with a control device and demonstrated through stack testing. | 2015-03-19 | NSCR | Great Plains Analytical Service | 118 hp | 1.0 g/hp-hr | 101 hp | 0.22 g/hp-hr | 6348 03 | VOC - Volatile Organic Compounds | PP | NA | Y
2015 | 844 | 0634005103 | Gulfport Energy - Davidson | Possom Hollow Rd | Freeport | 43977 |  | Harrison | P002 | One or multiple stationary natural gas-fired spark ignition (SI) internal combustion engines (ICE) with a combined total horsepower (HP) of no more than 1,000 HP for the site.* Includes 2007 and later model year engines manufactured after the applicable effective date identified in 40 CFR 60.4230(a)(3); and engines manufactured before the effective date of the NSPS, where compliance with the Part 60 Subpart JJJJ emissions standards for the same size engine can be met by retrofitting the engine with a control device and demonstrated through stack testing. | 2015-06-24 | catalyst | Great Plains Analytical Services | 118 hp | 1.0 g/hp-hr | 83 hp | 0.027 g/hp-hr | 6348 03 | VOC - Volatile Organic Compounds | PP | NA | Y
2015 | 847 | 0634005108 | Gulfport Energy - Vozar | McElhaney Rd | Freeport | 43973 |  | Harrison | P002 | One or multiple stationary natural gas-fired spark ignition (SI) internal combustion engines (ICE) with a combined total horsepower (HP) of no more than 1,000 HP for the site.* Includes 2007 and later model year engines manufactured after the applicable effective date identified in 40 CFR 60.4230(a)(3); and engines manufactured before the effective date of the NSPS, where compliance with the Part 60 Subpart JJJJ emissions standards for the same size engine can be met by retrofitting the engine with a control device and demonstrated through stack testing. | 2015-06-25 | catalyst | Great Plains Analytical | 118 hp | 1.0 g/hp-hr | 92 hp | 0.037 g/hp-hr | 6348 03 | VOC - Volatile Organic Compounds | PP | NA | Y
2015 | 871 | 0656005010 | Dominion East Ohio - Switzerland Compressor Station | German Ridge Road | Switzerland Twp. | 43942 |  | Monroe | P002 | 3550 Hp Natural gas-fired (4SLB) Caterpillar model 3612 LE DM5309-06 compressor engines equipped with catalytic reduction (three-way). | 2015-01-16 | AFR and catalyst controls | Air Compliance Consultants, Inc. | 3,550 hp | 0.26 g/hp-hr | 3,292 hp | 0.063 g/hp-hr | 6348 03 | VOC - Volatile Organic Compounds | PP | NA | Y | Method 320 actually used for testing.
2015 | 875 | 0661005008 | Seneca Gas Plant | Zep Road | Summerfield | 43788 |  | Noble | P001 | Compressor Engine #1 - Natural gas-fired four-stroke lean burn (4SLB) internal combustion engine rated at an operating capacity of 4,735 horsepower (hp) and equipped with an oxidation catalyst. | 2015-04-27 | CC001(Catalytic Converter): Compressor Engine #1 - Catalyic Convertor; CC002(Catalytic Converter): Compressor Engine #2 - Catalytic Convertor | Air Hygiene, Inc | 4735 hp | 0.16 g/hp-hr | 4125 hp | 0.04 g/hp-hr | 25A | VOC - Volatile Organic Compounds | PP | NA | Y
2015 | 878 | 0661005008 | Seneca Gas Plant | Zep Road | Summerfield | 43788 |  | Noble | P002 | Compressor Engine #2 - Natural gas-fired four-stroke lean burn (4SLB) internal combustion engine rated at an operating capacity of 4,735 horsepower (hp) and equipped with an oxidation catalyst. | 2015-04-27 | CC001(Catalytic Converter): Compressor Engine #1 - Catalyic Convertor; CC002(Catalytic Converter): Compressor Engine #2 - Catalytic Convertor | Air Hygiene, Inc | 4735 hp | 0.16 g/hp-hr | 4072 hp | 0.04 g/hp-hr | 25A | VOC - Volatile Organic Compounds | PP | NA | Y
2015 | 881 | 0661005020 | Rockies Express Pipeline - Seneca Compressor Station | Seneca Lake Rd | Quaker City | 43773 |  | Noble | P001 | Natural gas fired 4 stroke rich burn compressor engine, Waukesha VHP-L7042GSI, controlled by air/fuel ratio and nonselective catalytic reduction (NSCR) | 2015-03-03 | Engine 1(Catalytic Converter): Compressor Engine 1 catalytic converter; Engine 2(Catalytic Converter): Compressor Engine 2 catalytic converter | Compressor Engineering Corp. | 1480 hp | 0.07 g/hp-hr | 1574 hp | 0.02 g/hp-hr | 6348 03 | VOC - Volatile Organic Compounds | PP | NA | Y
2015 | 884 | 0661005020 | Rockies Express Pipeline - Seneca Compressor Station | Seneca Lake Rd | Quaker City | 43773 |  | Noble | P002 | Natural gas fired 4 stroke rich burn compressor engine, Waukesha P9394GSI, controlled by air/fuel ratio and nonselective catalytic reduction (NSCR) | 2015-03-03 | Engine 1(Catalytic Converter): Compressor Engine 1 catalytic converter; Engine 2(Catalytic Converter): Compressor Engine 2 catalytic converter | Compressor Engineering Corp. | 2250 hp | 0.07 g/hp-hr | 2237 hp | 0.02 g/hp-hr | 6348 03 | VOC - Volatile Organic Compounds | PP | NA | Y
2015 | 888 | 0661005020 | Rockies Express Pipeline - Seneca Compressor Station | Seneca Lake Rd | Quaker City | 43773 |  | Noble | P003 | compressor engine 3 | 2015-05-19 | Engine 3(Catalytic Converter): Compressor Engine 1 catalytic converter | Compressor Engineering Cort. | 2250 hp | 0.7 g/hp-hr | 2212 hp | 0.0 g/hp-hr | 6348 03 | VOC - Volatile Organic Compounds | PP | NA | Y
2015 | 889 | 0661005027 | E2 Appalachian LLC - Batesville | 58380 St John Rd | Quaker City | 43773 |  | Noble | P001 | 1,680 Hp. Waukesha (L7044GSI) natural gas-fired, rich burn, turbocharged, with oxidation catalyst, compressor engine | 2015-01-26 | C2701C(Catalytic Converter): Engine Catalyst | E2 Energy Services | 1680 hp | 0.7 g/hp-hr | 1400 hp | 0.003 g/hp-hr | 6348 03 | VOC - Volatile Organic Compounds | PP | NA | Y
2015 | 892 | 0661005027 | E2 Appalachian LLC - Batesville | 58380 St John Rd | Quaker City | 43773 |  | Noble | P002 | 1,680 Hp. Waukesha (L7044GSI) natural gas-fired, rich burn, turbocharged, with oxidation catalyst, compressor engine | 2015-01-26 | C2701C(Catalytic Converter): Engine Catalyst | E2 Energy Services | 1680 hp | 0.70 g/hp-hr | 1361 hp | 0.006 g/hp-hr | 6348 03 | VOC - Volatile Organic Compounds | PP | NA | Y
2015 | 896 | 0661005027 | E2 Appalachian LLC - Batesville | 58380 St John Rd | Quaker City | 43773 |  | Noble | P003 | 1,680 Hp. Waukesha (L7044GSI) natural gas-fired, rich burn, turbocharged, with oxidation catalyst, compressor engine | 2015-01-27 | C2701C(Catalytic Converter): Engine Catalyst | E2 Energy Services | 1680 hp | 0.7 g/hp-hr | 1277 hp | 0.008 g/hp-hr | 6348 03 | VOC - Volatile Organic Compounds | PP | NA | Y
2015 | 898 | 0661005027 | E2 Appalachian LLC - Batesville | 58380 St John Rd | Quaker City | 43773 |  | Noble | P007 | 1,680 Hp. Waukesha (L7044GSI) natural gas-fired, rich burn, turbocharged, with oxidation catalyst, compressor engine | 2015-02-19 | C2707C(Catalytic Converter): Engine Catalyst | E2 Energy Services | 1,680 hp | 0.7 g/hp-hr | 1,512 hp | 0.004 g/hp-hr | 6348 03 | VOC - Volatile Organic Compounds | PP | NA | Y
2015 | 901 | 0661005027 | E2 Appalachian LLC - Batesville | 58380 St John Rd | Quaker City | 43773 |  | Noble | P008 | 1,680 Hp. Waukesha (L7044GSI) natural gas-fired, rich burn, turbocharged, with oxidation catalyst, compressor engine | 2015-02-19 | C2708C(Catalytic Converter): Engine Catalyst | E2 Energy Services | 1,680 hp | 0.7 g/hp-hr | 1,512 hp | 0.01 g/hp-hr | 6348 03 | VOC - Volatile Organic Compounds | PP | NA | Y
2015 | 906 | 0661005027 | E2 Appalachian LLC - Batesville | 58380 St John Rd | Quaker City | 43773 |  | Noble | P004 | 1,680 Hp. Waukesha (L7044GSI) natural gas-fired, rich burn, turbocharged, with oxidation catalyst, compressor engine | 2015-02-20 | C2704C(Catalytic Converter): Engine Catalyst | E2 Energy Services | 1,680 hp | 0.7 g/hp-hr | 1,510 hp | 0.004 g/hp-hr | 6348 03 | VOC - Volatile Organic Compounds | PP | NA | Y
2015 | 907 | 0661005027 | E2 Appalachian LLC - Batesville | 58380 St John Rd | Quaker City | 43773 |  | Noble | P005 | 1,680 Hp. Waukesha (L7044GSI) natural gas-fired, rich burn, turbocharged, with oxidation catalyst, compressor engine | 2015-02-27 | C2705C(Catalytic Converter): Engine Catalyst | E2 Energy Services | 1,680 hp | 0.7 g/hp-hr | 1,295 hp | 0.006 g/hp-hr | 6348 03 | VOC - Volatile Organic Compounds | PP | NA | Y
2016 | 414 | 0210012004 | Augusta Compressor Facility- Utica Gas Services, L.L.C. | 8034 Bane Rd NE | East Twp. | 44427 |  | Carroll | P012 | 1,775-hp Caterpillar G3606 Compressor Engine w/ Oxidation Catalyst | 2016-09-08 | Oxid. Cat. 3(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 4(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 5(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 6(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 7(Catalytic Converter): | EcoTest Energy Services | 1775 Hp | 0.54 lbs/hr, 0.7 g/hp/hr, 60ppmvd@15%O2 | 1600 Hp or 90.1% of Max | .34 lbs/hr, 0.1 g/hp/hr, 9 ppmvd@15%O2 | 25A | VOC - Volatile Organic Compounds | PP | Y | NA
2016 | 415 | 0210012004 | Augusta Compressor Facility- Utica Gas Services, L.L.C. | 8034 Bane Rd NE | East Twp. | 44427 |  | Carroll | P013 | 1,775-hp Caterpillar G3606 Compressor Engine w/ Oxidation Catalyst | 2016-09-08 | Oxid. Cat. 3(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 4(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 5(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 6(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 7(Catalytic Converter): | EcoTest Energy Services | 1775 Hp | 0.54 lbs/hr, 0.7 g/hp/hr, 60ppmvd@15%O2 | 1600 Hp or 90.1% of Max | 0.51 lbs/hr, 0.14 g/hp/hr, 13 ppmvd@15%O2 | 25A | VOC - Volatile Organic Compounds | PP | Y | NA
2016 | 420 | 0210012030 | Blue Racer Midstream LLC - Carroll Co Field Station #1 | Cobbler Rd NE | Carrollton | 44615 |  | Carroll | P001 | 1,340 HP Caterpillar G3516LE 4SLB Compressor Engine #1 with Oxidation Catalyst. Engine model year: 2013. | 2016-10-14 | CC-1(Catalytic Converter): Oxidation Catalyst 1; CC-2(Catalytic Converter): Oxidation Catalyst 2; CC-3(Catalytic Converter): Oxidation Catalyst 3 | Montrose Air Quality Services | 1,340 Hp | 60 ppmvd@15% O2 & 0.26 g/bhp-hr | 1,129 HP or 82% | 16.5 ppmvd@15% O2 & 0.23 g/bhp-hr | 320 | VOC - Volatile Organic Compounds | PP | Y | NA
2016 | 421 | 0210012030 | Blue Racer Midstream LLC - Carroll Co Field Station #1 | Cobbler Rd NE | Carrollton | 44615 |  | Carroll | P002 | 1,340 HP Caterpillar G3516LE 4SLB Compressor Engine #2 with Oxidation Catalyst. Engine model year: 2013. | 2016-10-14 | CC-1(Catalytic Converter): Oxidation Catalyst 1; CC-2(Catalytic Converter): Oxidation Catalyst 2; CC-3(Catalytic Converter): Oxidation Catalyst 3 | Montrose Air Quality Services | 1,340 Hp | 60 ppmvd@15% O2 & 0.26 g/bhp-hr | 1,053 HP or 76% | 15.0 ppmvd@15% O2 & 0.21 g/bhp-hr | 320 | VOC - Volatile Organic Compounds | PP | Y | NA
2016 | 448 | 0210002039 | Kilgore Compressor Station-Utica Gas Services, LLC | Pontiff Rd | Kilgore | 43988 |  | Carroll | P001 | 1,775 hp NG-fired 4SLB Stationary ICE equipped w/catalyst Caterpillar G3606 Serial Number: 4ZS01713 | 2016-12-02 | CC001(Catalytic Converter): Compressor Engine #1 - Oxidation Catalyst; CC002(Catalytic Converter): Compressor Engine #2 - Oxidation Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - Oxidation Catalyst; CC004(Catalytic Converter): Compressor Eng | Technical Compliance Solutions LLC | 1775 | 0.7 g/Hp-hr, 0.71 lb/hr | 1703 | 0.003 g/Hp-hr, 0.011 lb/hr | 25A | VOC - Volatile Organic Compounds | PP | Y | NA
2016 | 449 | 0210002039 | Kilgore Compressor Station-Utica Gas Services, LLC | Pontiff Rd | Kilgore | 43988 |  | Carroll | P002 | 1,775 hp NG-fired 4SLB Stationary ICE equipped w/catalyst Caterpillar G3606: Serial Number: 4ZS01796 | 2016-12-02 | CC001(Catalytic Converter): Compressor Engine #1 - Oxidation Catalyst; CC002(Catalytic Converter): Compressor Engine #2 - Oxidation Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - Oxidation Catalyst; CC004(Catalytic Converter): Compressor Eng | Technical Compliance Solutions LLC | 1775 | 0.7 g/Hp-hr, 0.71 lb/hr | 1664 | 0.0 g/Hp-hr, 0.0 lb/hr | 25A | VOC - Volatile Organic Compounds | PP | Y | NA
2016 | 450 | 0210002039 | Kilgore Compressor Station-Utica Gas Services, LLC | Pontiff Rd | Kilgore | 43988 |  | Carroll | P003 | 1,775 hp NG-fired 4SLB Stationary ICE equipped w/catalyst Caterpillar G3606: Serial Number: 4ZS01797 | 2016-12-02 | CC001(Catalytic Converter): Compressor Engine #1 - Oxidation Catalyst; CC002(Catalytic Converter): Compressor Engine #2 - Oxidation Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - Oxidation Catalyst; CC004(Catalytic Converter): Compressor Eng | Technical Compliance Solutions LLC | 1775 | 0.7 g/Hp-hr, 0.71 lb/hr | 1629 | 0.0009 g/Hp-hr, 0.0031 lb/hr | 25A | VOC - Volatile Organic Compounds | PP | Y | NA
2016 | 451 | 0210002039 | Kilgore Compressor Station-Utica Gas Services, LLC | Pontiff Rd | Kilgore | 43988 |  | Carroll | P004 | 1,775 hp NG-fired 4SLB Stationary ICE equipped w/catalyst Caterpillar G3606: Serial Number: 4ZS01800 | 2016-12-02 | CC001(Catalytic Converter): Compressor Engine #1 - Oxidation Catalyst; CC002(Catalytic Converter): Compressor Engine #2 - Oxidation Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - Oxidation Catalyst; CC004(Catalytic Converter): Compressor Eng | Technical Compliance Solutions LLC | 1775 | 0.7 g/Hp-hr, 0.71 lb/hr | 1626 | 0.0 g/Hp-hr, 0.0 lb/hr | 25A | VOC - Volatile Organic Compounds | PP | Y | NA
2016 | 452 | 0210002039 | Kilgore Compressor Station-Utica Gas Services, LLC | Pontiff Rd | Kilgore | 43988 |  | Carroll | P005 | 1,775 hp NG-fired 4SLB Stationary ICE equipped w/catalyst Caterpillar G3606: Serial Number: 4ZS01804 | 2016-12-02 | CC001(Catalytic Converter): Compressor Engine #1 - Oxidation Catalyst; CC002(Catalytic Converter): Compressor Engine #2 - Oxidation Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - Oxidation Catalyst; CC004(Catalytic Converter): Compressor Eng | Technical Compliance Solutions LLC | 1775 | 0.7 g/Hp-hr, 0.71 lb/hr | 1671 | 0.01 g/Hp-hr, 0.029 lb/hr | 25A | VOC - Volatile Organic Compounds | PP | Y | NA
2016 | 453 | 0210002039 | Kilgore Compressor Station-Utica Gas Services, LLC | Pontiff Rd | Kilgore | 43988 |  | Carroll | P006 | 1,775 hp NG-fired 4SLB Stationary ICE equipped w/catalyst Caterpillar G3606: Serial Number: 4ZS01805 | 2016-12-02 | CC001(Catalytic Converter): Compressor Engine #1 - Oxidation Catalyst; CC002(Catalytic Converter): Compressor Engine #2 - Oxidation Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - Oxidation Catalyst; CC004(Catalytic Converter): Compressor Eng | Technical Compliance Solutions LLC | 1775 | 0.7 g/Hp-hr, 0.71 lb/hr | 1615 | 0.0 g/Hp-hr, 0.0 lb/hr | 25A | VOC - Volatile Organic Compounds | PP | Y | NA
2016 | 454 | 0210002039 | Kilgore Compressor Station-Utica Gas Services, LLC | Pontiff Rd | Kilgore | 43988 |  | Carroll | P007 | 1,775 hp NG-fired 4SLB Stationary ICE equipped w/catalyst Caterpillar G3606: Serial Number: 4ZS01807 | 2016-12-02 | CC001(Catalytic Converter): Compressor Engine #1 - Oxidation Catalyst; CC002(Catalytic Converter): Compressor Engine #2 - Oxidation Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - Oxidation Catalyst; CC004(Catalytic Converter): Compressor Eng | Technical Compliance Solutions LLC | 1775 | 0.7 g/Hp-hr, 0.71 lb/hr | 1654 | 0.01 g/Hp-hr, 0.021 lb/hr | 25A | VOC - Volatile Organic Compounds | PP | Y | NA
2016 | 455 | 0210002039 | Kilgore Compressor Station-Utica Gas Services, LLC | Pontiff Rd | Kilgore | 43988 |  | Carroll | P008 | 1,775 hp NG-fired 4SLB Stationary ICE equipped w/catalyst Caterpillar G3606: Serial Number: 4ZS01808 | 2016-12-02 | CC001(Catalytic Converter): Compressor Engine #1 - Oxidation Catalyst; CC002(Catalytic Converter): Compressor Engine #2 - Oxidation Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - Oxidation Catalyst; CC004(Catalytic Converter): Compressor Eng | Technical Compliance Solutions LLC | 1775 | 0.7 g/Hp-hr, 0.71 lb/hr | 1667 | 0.09 g/Hp-hr, 0.33 lb/hr | 25A | VOC - Volatile Organic Compounds | PP | Y | NA
2016 | 456 | 0210002039 | Kilgore Compressor Station-Utica Gas Services, LLC | Pontiff Rd | Kilgore | 43988 |  | Carroll | P009 | 1,775 hp NG-fired 4SLB Stationary ICE equipped w/catalyst Caterpillar G3606: Serial Number: 4ZS01776 | 2016-12-02 | CC001(Catalytic Converter): Compressor Engine #1 - Oxidation Catalyst; CC002(Catalytic Converter): Compressor Engine #2 - Oxidation Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - Oxidation Catalyst; CC004(Catalytic Converter): Compressor Eng | Technical Compliance Solutions LLC | 1775 | 0.7 g/Hp-hr, 0.71 lb/hr | 1679 | 0.0 g/Hp-hr, 0.0 lb/hr | 25A | VOC - Volatile Organic Compounds | PP | Y | NA
2016 | 457 | 0210002039 | Kilgore Compressor Station-Utica Gas Services, LLC | Pontiff Rd | Kilgore | 43988 |  | Carroll | P010 | 1,775 hp NG-fired 4SLB Stationary ICE equipped w/catalyst Caterpillar G3606: Serial Number: 4ZS01814 | 2016-12-02 | CC001(Catalytic Converter): Compressor Engine #1 - Oxidation Catalyst; CC002(Catalytic Converter): Compressor Engine #2 - Oxidation Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - Oxidation Catalyst; CC004(Catalytic Converter): Compressor Eng | Technical Compliance Solutions LLC | 1775 | 0.7 g/Hp-hr, 0.71 lb/hr | 1740 | 0.0 g/Hp-hr, 0.0 lb/hr | 25A | VOC - Volatile Organic Compounds | PP | Y | NA
2016 | 458 | 0210012002 | Utica Gas Services, LLC-Carrollton Compressor Facility | 2098 Panda Road SE | Carrollton | 44615 |  | Carroll | P004 | 1,775 HP natural gas-fired Caterpillar G3606 engine #1 equipped with an oxidation catalyst. | 2016-01-07 | Oxid. Cat.(Catalytic Converter): Oxidative Catalyst | Alliance Source Testing | 1775 HP | 0.82lb/hr, 1.0g/hp-hr | 1644 HP | 0.07 lb/hr, 0.02g/hp-hr | 25A | VOC - Volatile Organic Compounds | PP | Y | NA
2016 | 459 | 0210012002 | Utica Gas Services, LLC-Carrollton Compressor Facility | 2098 Panda Road SE | Carrollton | 44615 |  | Carroll | P005 | 1,775 HP natural gas-fired Caterpillar G3606 engine #2 equipped with an oxidation catalyst | 2016-01-07 | Oxid. Cat.(Catalytic Converter): Oxidative Catalyst | Alliance Source Testing | 1775 HP | 0.82lb/hr, 1.0g/hp-hr | 1737 HP | 0.07 lb/hr, 0.02g/hp-hr | 25A | VOC - Volatile Organic Compounds | PP | Y | NA
2016 | 460 | 0210012002 | Utica Gas Services, LLC-Carrollton Compressor Facility | 2098 Panda Road SE | Carrollton | 44615 |  | Carroll | P006 | 1,775 HP natural gas-fired Caterpillar G3606 engine #4 equipped with an oxidation catalyst | 2016-01-07 | Oxid. Cat.(Catalytic Converter): Oxidative Catalyst | Alliance Source Testing | 1775 HP | 0.82lb/hr, 0.7g/hp-hr | 1627 HP | 0.06 lb/hr, 0.02g/hp-hr | 25A | VOC - Volatile Organic Compounds | PP | Y | NA
2016 | 461 | 0210012002 | Utica Gas Services, LLC-Carrollton Compressor Facility | 2098 Panda Road SE | Carrollton | 44615 |  | Carroll | P007 | 1,775 HP natural gas-fired Caterpillar G3606 engine #4 equipped with an oxidation catalyst | 2016-01-07 | Oxid. Cat.(Catalytic Converter): Oxidative Catalyst | Alliance Source Testing | 1775 HP | 0.82lb/hr, 0.7g/hp-hr | 1710 HP | 0.13 lb/hr, 0.03g/hp-hr | 25A | VOC - Volatile Organic Compounds | PP | Y | NA
2016 | 462 | 0210012002 | Utica Gas Services, LLC-Carrollton Compressor Facility | 2098 Panda Road SE | Carrollton | 44615 |  | Carroll | P008 | 1,775 HP natural gas-fired Caterpillar G3606 engine #5 equipped with an oxidation catalyst | 2016-01-07 | Oxid. Cat.(Catalytic Converter): Oxidative Catalyst | Alliance Source Testing | 1775 HP | 0.82lb/hr, 0.7g/hp-hr | 1710 HP | 0.12 lb/hr, 0.03g/hp-hr | 25A | VOC - Volatile Organic Compounds | PP | Y | NA
2016 | 463 | 0210012002 | Utica Gas Services, LLC-Carrollton Compressor Facility | 2098 Panda Road SE | Carrollton | 44615 |  | Carroll | P009 | 1,775 HP natural gas-fired Caterpillar G3606 engine #6 equipped with an oxidation catalyst | 2016-01-07 | Oxid. Cat.(Catalytic Converter): Oxidative Catalyst | Alliance Source Testing | 1775 HP | 0.82lb/hr, 0.7g/hp-hr | 1656 HP | 0.12 lb/hr, 0.03g/hp-hr | 25A | VOC - Volatile Organic Compounds | PP | Y | NA
2016 | 464 | 0210012002 | Utica Gas Services, LLC-Carrollton Compressor Facility | 2098 Panda Road SE | Carrollton | 44615 |  | Carroll | P010 | 1,775 HP natural gas-fired Caterpillar G3606 engine #7 equipped with an oxidation catalyst | 2016-01-07 | Oxid. Cat.(Catalytic Converter): Oxidative Catalyst | Alliance Source Testing | 1775 HP | 0.82lb/hr, 0.7g/hp-hr | 1636 HP | 0.15 lb/hr, 0.04g/hp-hr | 25A | VOC - Volatile Organic Compounds | PP | Y | NA
2016 | 465 | 0210012002 | Utica Gas Services, LLC-Carrollton Compressor Facility | 2098 Panda Road SE | Carrollton | 44615 |  | Carroll | P011 | 1,775 HP natural gas-fired Caterpillar G3606 engine #8 equipped with an oxidation catalyst | 2016-01-07 | Oxid. Cat.(Catalytic Converter): Oxidative Catalyst | Alliance Source Testing | 1775 HP | 0.82lb/hr, 0.7g/hp-hr | 1657 HP | 0.11 lb/hr, 0.03g/hp-hr | 25A | VOC - Volatile Organic Compounds | PP | Y | NA
2016 | 466 | 0210012002 | Utica Gas Services, LLC-Carrollton Compressor Facility | 2098 Panda Road SE | Carrollton | 44615 |  | Carroll | P012 | 1,775 HP natural gas-fired Caterpillar G3606 engine #9 equipped with an oxidation catalyst | 2016-01-07 | Oxid. Cat.(Catalytic Converter): Oxidative Catalyst | Alliance Source Testing | 1775 HP | 0.82lb/hr, 0.7g/hp-hr | 1716 HP | 0.09 lb/hr, 0.02g/hp-hr | 25A | VOC - Volatile Organic Compounds | PP | Y | NA
2016 | 467 | 0210012002 | Utica Gas Services, LLC-Carrollton Compressor Facility | 2098 Panda Road SE | Carrollton | 44615 |  | Carroll | P013 | 1,775 HP natural gas-fired Caterpillar G3606 engine #10equipped with an oxidation catalyst | 2016-01-07 | Oxid. Cat.(Catalytic Converter): Oxidative Catalyst | Alliance Source Testing | 1775 HP | 0.82lb/hr, 0.7g/hp-hr | 1662 HP | 0.16 lb/hr, 0.04g/hp-hr | 25A | VOC - Volatile Organic Compounds | PP | Y | NA
2016 | 511 | 0210012004 | Augusta Compressor Facility- Utica Gas Services, L.L.C. | 8034 Bane Rd NE | East Twp. | 44427 |  | Carroll | P006 | 1,775-hp Caterpillar G3606 Compressor Engine w/ Oxidation Catalyst | 2016-09-08 | Oxid. Cat. 3(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 4(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 5(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 6(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 7(Catalytic Converter): | EcoTest Energy Services | 1775 Hp | 0.54 lbs/hr, 0.7 g/hp/hr, 60ppmvd@15%O2 | 1600 Hp or 90.1% of Max | 0.50 lbs/hr, 0.14 g/hp/hr, 13ppmvd@15%O2 | 25A | VOC - Volatile Organic Compounds | PP | Y | NA
2016 | 512 | 0210012004 | Augusta Compressor Facility- Utica Gas Services, L.L.C. | 8034 Bane Rd NE | East Twp. | 44427 |  | Carroll | P007 | 1,775-hp Caterpillar G3606 Compressor Engine w/ Oxidation Catalyst | 2016-09-08 | Oxid. Cat. 3(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 4(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 5(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 6(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 7(Catalytic Converter): | EcoTest Energy Services | 1775 Hp | 0.54 lbs/hr, 0.7 g/hp/hr, 60ppmvd@15%O2 | 1600 Hp or 90.1% of Max | 0.43 lbs/hr, 0.12 g/hp/hr, 11ppmvd@15%O2 | 25A | VOC - Volatile Organic Compounds | PP | Y | NA
2016 | 513 | 0210012004 | Augusta Compressor Facility- Utica Gas Services, L.L.C. | 8034 Bane Rd NE | East Twp. | 44427 |  | Carroll | P008 | 1,775-hp Caterpillar G3606 Compressor Engine w/ Oxidation Catalyst | 2016-09-08 | Oxid. Cat. 3(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 4(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 5(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 6(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 7(Catalytic Converter): | EcoTest Energy Services | 1775 Hp | 0.54 lbs/hr, 0.7 g/hp/hr, 60ppmvd@15%O2 | 1628 Hp or 91.7% of Max | 0.33 lbs/hr, 0.09 g/hp/hr, 8 ppmvd@15%O2 | 25A | VOC - Volatile Organic Compounds | PP | Y | NA
2016 | 514 | 0210012004 | Augusta Compressor Facility- Utica Gas Services, L.L.C. | 8034 Bane Rd NE | East Twp. | 44427 |  | Carroll | P009 | 1,775-hp Caterpillar G3606 Compressor Engine w/ Oxidation Catalyst | 2016-09-08 | Oxid. Cat. 3(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 4(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 5(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 6(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 7(Catalytic Converter): | EcoTest Energy Services | 1775 Hp | 0.54 lbs/hr, 0.7 g/hp/hr, 60ppmvd@15%O2 | 1650 Hp or 93% of Max | 0.5 lbs/hr, 0.14 g/hp/hr, 13 ppmvd@15%O2 | 25A | VOC - Volatile Organic Compounds | PP | Y | NA
2016 | 515 | 0210012004 | Augusta Compressor Facility- Utica Gas Services, L.L.C. | 8034 Bane Rd NE | East Twp. | 44427 |  | Carroll | P010 | 1,775-hp Caterpillar G3606 Compressor Engine w/ Oxidation Catalyst | 2016-09-08 | Oxid. Cat. 3(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 4(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 5(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 6(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 7(Catalytic Converter): | EcoTest Energy Services | 1775 Hp | 0.54 lbs/hr, 0.7 g/hp/hr, 60ppmvd@15%O2 | 1600 Hp or 90.1% of Max | .37 lbs/hr, 0.11 g/hp/hr, 9 ppmvd@15%O2 | 25A | VOC - Volatile Organic Compounds | PP | Y | NA
2016 | 516 | 0210012004 | Augusta Compressor Facility- Utica Gas Services, L.L.C. | 8034 Bane Rd NE | East Twp. | 44427 |  | Carroll | P011 | 1,775-hp Caterpillar G3606 Compressor Engine w/ Oxidation Catalyst | 2016-09-08 | Oxid. Cat. 3(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 4(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 5(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 6(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 7(Catalytic Converter): | EcoTest Energy Services | 1775 Hp | 0.54 lbs/hr, 0.7 g/hp/hr, 60ppmvd@15%O2 | 1600 Hp or 90.1% of Max | 0.54 lbs/hr, 0.15 g/hp/hr, 14ppmvd@15%O2 | 25A | VOC - Volatile Organic Compounds | PP | Y | NA
2016 | 518 | 0210012030 | Blue Racer Midstream LLC - Carroll Co Field Station #1 | Cobbler Rd NE | Carrollton | 44615 |  | Carroll | P003 | 1,340 HP Caterpillar G3516LE 4SLB Compressor Engine #3 with Oxidation Catalyst | 2016-10-14 | CC-1(Catalytic Converter): Oxidation Catalyst 1; CC-2(Catalytic Converter): Oxidation Catalyst 2; CC-3(Catalytic Converter): Oxidation Catalyst 3 | Montrose Air Quality Services | 1,340 Hp | 60 ppmvd@15% O2 & 0.26 g/bhp-hr | 1,086 HP or 79% | 12.9 ppmvd@15% O2 & 0.18 g/bhp-hr | 320 | VOC - Volatile Organic Compounds | PP | Y | NA
2016 | 722 | 0285000366 | East Ohio Gas - Chippewa Station | 17045 Galehouse Road | Doylestown | 44230 |  | Wayne | B010 | 2,370 hp 4SLB SI ICE; CAT G3608 | 2016-05-18 | Engine 5 Converter(Catalytic Converter): Engine #5; Cat B010(Catalytic Converter): Catalytic Converter for B010, engine #6; Catalytic(Catalytic Converter): Engine 7 Catalytic converter | Air/Compliance Consultants, Inc. | 2370 Hp | 86 ppm@15% O2 or 1.0g/bhp-hr 93% | 2225 Hp | 52.8 ppm@15% O2 and 0.19 g/bhp-hr, .91 lb/hr | 25A | VOC - Volatile Organic Compounds | PP | Y | NA | B010-2.75 Catalyst Pressure and 860 degF Catalyst temp, B014-1.2 Catalyst Pressure and 874 degF Catalyst Temperature
2016 | 723 | 0285000366 | East Ohio Gas - Chippewa Station | 17045 Galehouse Road | Doylestown | 44230 |  | Wayne | B014 | 2,370 hp 4SLB SI ICE: CAT 3608 w/catalyst | 2016-05-18 | Engine 5 Converter(Catalytic Converter): Engine #5; Cat B010(Catalytic Converter): Catalytic Converter for B010, engine #6; Catalytic(Catalytic Converter): Engine 7 Catalytic converter | Air/Compliance Consultants, Inc. | 2370 Hp | 60 ppm @15%O2 or 0.7 g/bhp-hr 93% | 2241 Hp | 35.9 ppm @15%O2 and 0.13 g/bhp-hr, 0.62 lb/hr | 25A | VOC - Volatile Organic Compounds | PP | Y | NA | B010-2.75 Catalyst Pressure and 860 degF Catalyst temp, B014-1.2 Catalyst Pressure and 874 degF Catalyst Temperature
2016 | 726 | 0285000388 | East Ohio Gas Company - Paint | STATE RTE 250 | Wooster | 44624 |  | Wayne | B002 | Natural gas fired Internal Combustion Engine with max input capacity of 11.9 MMBtu/hr - Caterpillar G3516TALE with 1340 HP, 4-stroke, selective catalytic reduction (SCR) | 2016-07-07 | Three way Catalyst; CatOx(Catalytic Converter): Catalytic oxidizer for Engine 2 | Environmental Quality Management | 1340 HP | 1.0 g/bhp-hr or 86ppmvd@ 15% O2 | 1259 HP or 94% | 0.19 g/bhp-hr or 55.4 ppmvd@ 15% O2 | 25A | VOC - Volatile Organic Compounds | PP | Y | NA
2016 | 881 | 0656105005 | E2 Appalachian Compression LLC - Reusser | Twp Hwy 68 and Twp Hwy 66 | Woodsfield | 43793 |  | Monroe | P003 | 1680 Hp. natural gas rich burn compressor engine - Waukesha L7044GSI | 2016-07-14 | C-1(Catalytic Converter): Engine Catalyst; C-2(Catalytic Converter): Engine Catalyst; C-3(Catalytic Converter): Engine #3 Catalyst; C-4(Catalytic Converter): Engine #4 Catalyst; C-5(Catalytic Converter): Engine #5 Catalyst; C-6(Catalytic Converter): Engin | Alliance Source Testing | 1680 hp | 0.22 lb/hr | 1658 hp | 0.09 lb/hr | 25A | VOC - Volatile Organic Compounds | PP | Y | NA
2016 | 882 | 0656105005 | E2 Appalachian Compression LLC - Reusser | Twp Hwy 68 and Twp Hwy 66 | Woodsfield | 43793 |  | Monroe | P004 | 1680 Hp. natural gas rich burn compressor engine - Waukesha L7044GSI | 2016-07-14 | C-1(Catalytic Converter): Engine Catalyst; C-2(Catalytic Converter): Engine Catalyst; C-3(Catalytic Converter): Engine #3 Catalyst; C-4(Catalytic Converter): Engine #4 Catalyst; C-5(Catalytic Converter): Engine #5 Catalyst; C-6(Catalytic Converter): Engin | Alliance Source Testing | 1680 hp | 0.22 lb/hr | 1680 hp | 0.05 lb/hr | 25A | VOC - Volatile Organic Compounds | PP | Y | NA
2016 | 883 | 0656105005 | E2 Appalachian Compression LLC - Reusser | Twp Hwy 68 and Twp Hwy 66 | Woodsfield | 43793 |  | Monroe | P005 | 1680 Hp. natural gas rich burn compressor engine - Waukesha L7044GSI | 2016-07-14 | C-1(Catalytic Converter): Engine Catalyst; C-2(Catalytic Converter): Engine Catalyst; C-3(Catalytic Converter): Engine #3 Catalyst; C-4(Catalytic Converter): Engine #4 Catalyst; C-5(Catalytic Converter): Engine #5 Catalyst; C-6(Catalytic Converter): Engin | Alliance Source Testing | 1680 hp | 0.22 lb/hr | 1613 hp | 0.03 lb/hr | 25A | VOC - Volatile Organic Compounds | PP | Y | NA
2016 | 884 | 0656105005 | E2 Appalachian Compression LLC - Reusser | Twp Hwy 68 and Twp Hwy 66 | Woodsfield | 43793 |  | Monroe | P006 | 1680 Hp. natural gas rich burn compressor engine - Waukesha L7044GSI | 2016-07-14 | C-1(Catalytic Converter): Engine Catalyst; C-2(Catalytic Converter): Engine Catalyst; C-3(Catalytic Converter): Engine #3 Catalyst; C-4(Catalytic Converter): Engine #4 Catalyst; C-5(Catalytic Converter): Engine #5 Catalyst; C-6(Catalytic Converter): Engin | Alliance Source Testing | 1680 hp | 0.22 lb/hr | 1646 hp | 0.05 lb/hr | 25A | VOC - Volatile Organic Compounds | PP | Y | NA
2016 | 885 | 0656105005 | E2 Appalachian Compression LLC - Reusser | Twp Hwy 68 and Twp Hwy 66 | Woodsfield | 43793 |  | Monroe | P007 | 1680 Hp. natural gas rich burn compressor engine - Waukesha L7044GSI | 2016-07-14 | C-1(Catalytic Converter): Engine Catalyst; C-2(Catalytic Converter): Engine Catalyst; C-3(Catalytic Converter): Engine #3 Catalyst; C-4(Catalytic Converter): Engine #4 Catalyst; C-5(Catalytic Converter): Engine #5 Catalyst; C-6(Catalytic Converter): Engin | Alliance Source Testing | 1680 hp | 0.22 lb/hr | 1680 hp | 0.04 lb/hr | 25A | VOC - Volatile Organic Compounds | PP | Y | NA
2016 | 886 | 0656105005 | E2 Appalachian Compression LLC - Reusser | Twp Hwy 68 and Twp Hwy 66 | Woodsfield | 43793 |  | Monroe | P008 | 1680 Hp. natural gas rich burn compressor engine - Waukesha L7044GSI | 2016-07-14 | C-1(Catalytic Converter): Engine Catalyst; C-2(Catalytic Converter): Engine Catalyst; C-3(Catalytic Converter): Engine #3 Catalyst; C-4(Catalytic Converter): Engine #4 Catalyst; C-5(Catalytic Converter): Engine #5 Catalyst; C-6(Catalytic Converter): Engin | Alliance Source Testing | 1680 hp | 0.22 lb/hr | 1680 hp | 0.02 lb/hr | 25A | VOC - Volatile Organic Compounds | PP | Y | NA
2016 | 887 | 0656105005 | E2 Appalachian Compression LLC - Reusser | Twp Hwy 68 and Twp Hwy 66 | Woodsfield | 43793 |  | Monroe | P009 | 1680 Hp. natural gas rich burn compressor engine - Waukesha L7044GSI | 2016-07-14 | C-1(Catalytic Converter): Engine Catalyst; C-2(Catalytic Converter): Engine Catalyst; C-3(Catalytic Converter): Engine #3 Catalyst; C-4(Catalytic Converter): Engine #4 Catalyst; C-5(Catalytic Converter): Engine #5 Catalyst; C-6(Catalytic Converter): Engin | Alliance Source Testing | 1680 hp | 0.22 lb/hr | 1404 hp | 0.03 lb/hr | 25A | VOC - Volatile Organic Compounds | PP | Y | NA
2016 | 900 | 0661005052 | Long Compressor Station | 55135 Batesville Rd | Quaker City | 43773 |  | Noble | P009 | 1,680 hp Waukesha 7044GSI NG Fired-rich burn-4stroke compressor engine | 2016-01-28 | C-09(Catalytic Converter): Non-selective catalyst reduction device for C-2800 | Technical Compliance Solutions | 1680 hp | 0.07 g/hp-hr | 1617 hp | 0.01 g/hp-hr | 320 | VOC - Volatile Organic Compounds | PP | Y | NA
2016 | 904 | 0661005060 | CNX Gas LLC - Noble 36 Well Pad | 45379 Gurewicz Rd | Summerfield | 43788 |  | Noble | P002 | NOT INSTALLED AT PERMIT ISSUANCE TIME One or multiple stationary natural gas-fired spark ignition (SI) internal combustion engines (ICE) with a combined total horsepower (HP) of no more than 1,000 HP for the site.* Includes 2007 and later model year eng | 2016-04-04 | NSCR | EcoTest Energy Services | VRU-68 hp Flash gas-400 hp0 | 1.0 g/hp-hr | VRU-22 hp Flash gas-100 hp | 0.07 g/hp-hr | 320 | VOC - Volatile Organic Compounds | PP | Y | NA | these two engines combined are permitted as P002
2016 | 1135 | 0546015002 | Bellefontaine Gas Producers, LLC | 2946 US Route 68 North | Bellefontaine | 43311 |  | Logan | P001 | 2275 Hp, 4-stroke lean burn, non-emergency, spark ignition RICE; Ch. 31 modification issued 1/8/2014. | 2016-04-12 | N/A | DTE Energy | 2275 | 1.0 g/bhp-hr | => 2047.5 | ND | 25A | Total Hydrocarbons | PP | Y | Y
2016 | 1153 | 0607005016 | Barnesville West Compressor Station | Hwy 801 | Warren Twp. | 43713 |  | Belmont | P006 | Compressor Engine #1 - Natural gas-fired four-stroke lean burn (4SLB) internal combustion engine rated at an operating capacity of 2,370 horsepower (hp) and equipped with an oxidation catalyst | 2016-03-21 | CC001(Catalytic Converter): Compressor Engine #1 Catalytic Converter; CC002(Catalytic Converter): Compressor Engine #2 Catalytic Converter; CC003(Catalytic Converter): Compressor Engine #3 Catalytic Converter | Air Hygiene, Inc. | 2370 hp | 0.28 g/hp-hr | 2270 hp | 0.17 g/hp-hr | 25A | VOC - Volatile Organic Compounds | PP | Y | NA
2016 | 1154 | 0607005016 | Barnesville West Compressor Station | Hwy 801 | Warren Twp. | 43713 |  | Belmont | P007 | Compressor Engine #1 - Natural gas-fired four-stroke lean burn (4SLB) internal combustion engine rated at an operating capacity of 2,370 horsepower (hp) and equipped with an oxidation catalyst | 2016-03-21 | CC001(Catalytic Converter): Compressor Engine #1 Catalytic Converter; CC002(Catalytic Converter): Compressor Engine #2 Catalytic Converter; CC003(Catalytic Converter): Compressor Engine #3 Catalytic Converter | Air Hygiene, Inc. | 2370 hp | 0.28 g/hp-hr | 2264 hp | 0.19 g/hp-hr | 25A | VOC - Volatile Organic Compounds | PP | Y | NA
2016 | 1155 | 0607005016 | Barnesville West Compressor Station | Hwy 801 | Warren Twp. | 43713 |  | Belmont | P008 | Compressor Engine #3 - Natural gas-fired four-stroke lean burn (4SLB) internal combustion engine rated at an operating capacity of 2,370 horsepower (hp) and equipped with an oxidation catalyst | 2016-03-21 | CC001(Catalytic Converter): Compressor Engine #1 Catalytic Converter; CC002(Catalytic Converter): Compressor Engine #2 Catalytic Converter; CC003(Catalytic Converter): Compressor Engine #3 Catalytic Converter | Air Hygiene, Inc. | 2370 hp | 0.28 g/hp-hr | 2329 hp | 0.18 g/hp-hr | 25A | VOC - Volatile Organic Compounds | PP | Y | NA
2016 | 1162 | 0607005016 | Barnesville West Compressor Station | Hwy 801 | Warren Twp. | 43713 |  | Belmont | P009 | Compressor Engine #4 - Natural gas-fired four-stroke lean burn (4SLB) internal combustion engine rated at an operating capacity of 2,370 horsepower (hp) and equipped with an oxidation catalyst | 2016-03-22 | CC005(Catalytic Converter): Compressor Engine #5 Catalytic Converter; CC004(Catalytic Converter): Compressor Engine #4 Catalytic Converter; CC006(Catalytic Converter): Compressor Engine #6 Catalytic Converter | Air Hygiene, Inc. | 2370 hp | 0.28 g/hp-hr | 2198 hp | 0.19 g/hp-hr | 25A | VOC - Volatile Organic Compounds | PP | Y | NA
2016 | 1163 | 0607005016 | Barnesville West Compressor Station | Hwy 801 | Warren Twp. | 43713 |  | Belmont | P010 | Compressor Engine #5 - Natural gas-fired four-stroke lean burn (4SLB) internal combustion engine rated at an operating capacity of 2,370 horsepower (hp) and equipped with an oxidation catalyst | 2016-03-22 | CC005(Catalytic Converter): Compressor Engine #5 Catalytic Converter; CC004(Catalytic Converter): Compressor Engine #4 Catalytic Converter; CC006(Catalytic Converter): Compressor Engine #6 Catalytic Converter | Air Hygiene, Inc. | 2370 hp | 0.28 g/hp-hr | 2277 hp | 0.21 g/hp-hr | 25A | VOC - Volatile Organic Compounds | PP | Y | NA
2016 | 1164 | 0607005016 | Barnesville West Compressor Station | Hwy 801 | Warren Twp. | 43713 |  | Belmont | P011 | Compressor Engine #6 - Natural gas-fired four-stroke lean burn (4SLB) internal combustion engine rated at an operating capacity of 2,370 horsepower (hp) and equipped with an oxidation catalyst | 2016-03-22 | CC005(Catalytic Converter): Compressor Engine #5 Catalytic Converter; CC004(Catalytic Converter): Compressor Engine #4 Catalytic Converter; CC006(Catalytic Converter): Compressor Engine #6 Catalytic Converter | Air Hygiene, Inc. | 2370 hp | 0.28 g/hp-hr | 2281 hp | 0.17 g/hp-hr | 25A | VOC - Volatile Organic Compounds | PP | Y | NA
2016 | 1177 | 0607015001 | Tri-County Compressor Station (MarkWest / Ohio Oil Gath | N of intersection of Hwy 379 and Town | Barnesville | 43713 |  | Belmont | P003 | Compressor Engine #3 - 1980 HP (15.43 MMBtu/hr) Waukesha P9390 - natural gas-fired four-stroke rich burn internal combustion engine equipped with a three-way oxidation catalyst controlling CH2O, CO, NOx, & VOCs by 80, 97, 98.5 & 66 percent respectively | 2016-08-17 | CC002(Catalytic Converter): Compressor Engine #2 - 3-way Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - 3-way Catalyst; CC004(Catalytic Converter): Compressor Engine #4 - 3-way Catalyst; CC005(Catalytic Converter): Compressor Engine #5 - 3-w | Air Hygiene Internatinal, Inc | 1,980 hp | 0.7 g/hp-hr | 1,681 hp | 0.14 g/hp-hr | 25A | VOC - Volatile Organic Compounds | PP | Y | NA
2016 | 1178 | 0607015001 | Tri-County Compressor Station (MarkWest / Ohio Oil Gath | N of intersection of Hwy 379 and Town | Barnesville | 43713 |  | Belmont | P004 | Compressor Engine #4 - 1980 HP (15.43 MMBtu/hr) Waukesha P9390 - natural gas-fired four-stroke rich burn internal combustion engine equipped with a three-way oxidation catalyst controlling CH2O, CO, NOx, & VOCs by 80, 97, 98.5 & 66 percent respectively | 2016-08-17 | CC002(Catalytic Converter): Compressor Engine #2 - 3-way Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - 3-way Catalyst; CC004(Catalytic Converter): Compressor Engine #4 - 3-way Catalyst; CC005(Catalytic Converter): Compressor Engine #5 - 3-w | Air Hygiene Internatinal, Inc | 1,980 hp | 0.7 g/hp-hr | 1,668 hp | 0.17 g/hp-hr | 25A | VOC - Volatile Organic Compounds | PP | Y | NA
2016 | 1179 | 0607015001 | Tri-County Compressor Station (MarkWest / Ohio Oil Gath | N of intersection of Hwy 379 and Town | Barnesville | 43713 |  | Belmont | P005 | Compressor Engine #5 - 1980 HP (15.43 MMBtu/hr) Waukesha P9390 - natural gas-fired four-stroke rich burn internal combustion engine equipped with a three-way oxidation catalyst controlling CH2O, CO, NOx, & VOCs by 80, 97, 98.5 & 66 percent respectively | 2016-08-17 | CC002(Catalytic Converter): Compressor Engine #2 - 3-way Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - 3-way Catalyst; CC004(Catalytic Converter): Compressor Engine #4 - 3-way Catalyst; CC005(Catalytic Converter): Compressor Engine #5 - 3-w | Air Hygiene Internatinal, Inc | 1,980 hp | 0.7 g/hp-hr | 1,733 hp | 0.10 g/hp-hr | 25A | VOC - Volatile Organic Compounds | PP | Y | NA
2016 | 1180 | 0607015001 | Tri-County Compressor Station (MarkWest / Ohio Oil Gath | N of intersection of Hwy 379 and Town | Barnesville | 43713 |  | Belmont | P006 | Compressor Engine #6 - 1980 HP (15.43 MMBtu/hr) Waukesha P9390 - natural gas-fired four-stroke rich burn internal combustion engine equipped with a three-way oxidation catalyst controlling CH2O, CO, NOx, & VOCs by 80, 97, 98.5 & 66 percent respectively | 2016-08-17 | CC002(Catalytic Converter): Compressor Engine #2 - 3-way Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - 3-way Catalyst; CC004(Catalytic Converter): Compressor Engine #4 - 3-way Catalyst; CC005(Catalytic Converter): Compressor Engine #5 - 3-w | Air Hygiene Internatinal, Inc | 1,980 hp | 0.7 g/hp-hr | 1,709 hp | 0.07 g/hp-hr | 25A | VOC - Volatile Organic Compounds | PP | Y | NA
2016 | 1181 | 0607015001 | Tri-County Compressor Station (MarkWest / Ohio Oil Gath | N of intersection of Hwy 379 and Town | Barnesville | 43713 |  | Belmont | P007 | Compressor Engine #7 - 1980 HP (15.43 MMBtu/hr) Waukesha P9390 - natural gas-fired four-stroke rich burn internal combustion engine equipped with a three-way oxidation catalyst controlling CH2O, CO, NOx, & VOCs by 80, 97, 98.5 & 66 percent respectively | 2016-08-17 | CC002(Catalytic Converter): Compressor Engine #2 - 3-way Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - 3-way Catalyst; CC004(Catalytic Converter): Compressor Engine #4 - 3-way Catalyst; CC005(Catalytic Converter): Compressor Engine #5 - 3-w | Air Hygiene Internatinal, Inc | 1,980 hp | 0.7 g/hp-hr | 1,568 hp | 0.15 g/hp-hr | 25A | VOC - Volatile Organic Compounds | PP | Y | NA
2016 | 1182 | 0607015001 | Tri-County Compressor Station (MarkWest / Ohio Oil Gath | N of intersection of Hwy 379 and Town | Barnesville | 43713 |  | Belmont | P008 | Compressor Engine #8 - 1980 HP (15.43 MMBtu/hr) Waukesha P9390 - natural gas-fired four-stroke rich burn internal combustion engine equipped with a three-way oxidation catalyst controlling CH2O, CO, NOx, & VOCs by 80, 97, 98.5 & 66 percent respectively | 2016-08-17 | CC002(Catalytic Converter): Compressor Engine #2 - 3-way Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - 3-way Catalyst; CC004(Catalytic Converter): Compressor Engine #4 - 3-way Catalyst; CC005(Catalytic Converter): Compressor Engine #5 - 3-w | Air Hygiene Internatinal, Inc | 1,980 hp | 0.7 g/hp-hr | 1,757 hp | 0.04 g/hp-hr | 25A | VOC - Volatile Organic Compounds | PP | Y | NA
2016 | 1189 | 0607015007 | Humphreys Compressor Station | Johnson Ridge Rd | Barnesville | 43713 |  | Belmont | P001 | Compressor Engine #1 - Caterpillar G3612TA - natural gas fired four-stroke, lean burn internal combustion engine rated at an operating capacity of 3,550 horsepower equipped with a double oxidation catalyst. | 2016-04-12 | CC001(Catalytic Converter): Compressor Engine #1 - Oxidation Catalyst; CC002(Catalytic Converter): Compressor Engine #2 - Oxidation Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - Oxidation Catalyst | Air Hygiene, Inc | 3550 hp | 0.16 g/hp-hr | 3345 hp | 0.07 g/hp-hr | 25A | VOC - Volatile Organic Compounds | PP | Y | NA
2016 | 1190 | 0607015007 | Humphreys Compressor Station | Johnson Ridge Rd | Barnesville | 43713 |  | Belmont | P002 | Compressor Engine #1 - Caterpillar G3612TA - natural gas fired four-stroke, lean burn internal combustion engine rated at an operating capacity of 3,550 horsepower equipped with a double oxidation catalyst. | 2016-04-12 | CC001(Catalytic Converter): Compressor Engine #1 - Oxidation Catalyst; CC002(Catalytic Converter): Compressor Engine #2 - Oxidation Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - Oxidation Catalyst | Air Hygiene, Inc | 3550 hp | 0.16 g/hp-hr | 3318 hp | 0.09 g/hp-hr | 25A | VOC - Volatile Organic Compounds | PP | Y | NA
2016 | 1191 | 0607015007 | Humphreys Compressor Station | Johnson Ridge Rd | Barnesville | 43713 |  | Belmont | P003 | Compressor Engine #1 - Caterpillar G3612TA - natural gas fired four-stroke, lean burn internal combustion engine rated at an operating capacity of 3,550 horsepower equipped with a double oxidation catalyst. | 2016-04-12 | CC001(Catalytic Converter): Compressor Engine #1 - Oxidation Catalyst; CC002(Catalytic Converter): Compressor Engine #2 - Oxidation Catalyst; CC003(Catalytic Converter): Compressor Engine #3 - Oxidation Catalyst | Air Hygiene, Inc | 3550 hp | 0.16 g/hp-hr | 3402 hp | 0.08 g/hp-hr | 25A | VOC - Volatile Organic Compounds | PP | Y | NA
2016 | 1195 | 0607015007 | Humphreys Compressor Station | Johnson Ridge Rd | Barnesville | 43713 |  | Belmont | P004 | Compressor Engine #1 - Caterpillar G3612TA - natural gas fired four-stroke, lean burn internal combustion engine rated at an operating capacity of 3,550 horsepower equipped with a double oxidation catalyst. | 2016-04-13 | CC004(Catalytic Converter): Compressor Engine #4 - Oxidation Catalyst; CC005(Catalytic Converter): Compressor Engine #5 - Oxidation Catalyst; CC006(Catalytic Converter): Compressor Engine #6 - Oxidation Catalyst | Air Hygiene, Inc | 3550 hp | 0.16 g/hp-hr | 3345 hp | 0.11 g/hp-hr | 25A | VOC - Volatile Organic Compounds | PP | Y | NA
2016 | 1196 | 0607015007 | Humphreys Compressor Station | Johnson Ridge Rd | Barnesville | 43713 |  | Belmont | P005 | Compressor Engine #1 - Caterpillar G3612TA - natural gas fired four-stroke, lean burn internal combustion engine rated at an operating capacity of 3,550 horsepower equipped with a double oxidation catalyst. | 2016-04-13 | CC004(Catalytic Converter): Compressor Engine #4 - Oxidation Catalyst; CC005(Catalytic Converter): Compressor Engine #5 - Oxidation Catalyst; CC006(Catalytic Converter): Compressor Engine #6 - Oxidation Catalyst | Air Hygiene, Inc | 3550 hp | 0.16 g/hp-hr | 3341 hp | 0.10 g/hp-hr | 25A | VOC - Volatile Organic Compounds | PP | Y | NA
2016 | 1197 | 0607015007 | Humphreys Compressor Station | Johnson Ridge Rd | Barnesville | 43713 |  | Belmont | P006 | Compressor Engine #1 - Caterpillar G3612TA - natural gas fired four-stroke, lean burn internal combustion engine rated at an operating capacity of 3,550 horsepower equipped with a double oxidation catalyst. | 2016-04-13 | CC004(Catalytic Converter): Compressor Engine #4 - Oxidation Catalyst; CC005(Catalytic Converter): Compressor Engine #5 - Oxidation Catalyst; CC006(Catalytic Converter): Compressor Engine #6 - Oxidation Catalyst | Air Hygiene, Inc | 3550 hp | 0.16 g/hp-hr | 3297 hp | 0.08 g/hp-hr | 25A | VOC - Volatile Organic Compounds | PP | Y | NA
2016 | 1199 | 0607075002 | Ascent Resources - Utica, LLC - CHC Dutton (Wheeling) | 43125 Dutton Drive | Flushing | 43977 |  | Belmont | P007 | Natural Gas Compression engine | 2016-06-28 | Comp Engine(Catalytic Converter): Natural Gas Compressor Engine Catalytic Converter | EcoTest Energy Resources | 211 hp | 0.5 g/hp-hr | 139 hp | 0.01 g/hp-hr | 320 | VOC - Volatile Organic Compounds | PP | Y | NA
2016 | 1239 | 0630005035 | Ascent Resources - Utica LLC - Coad 12-9N-7W | 25595 Oxford Rd | Quaker City | 43773 |  | Guernsey | P002 | One or multiple stationary natural gas-fired spark ignition (SI) internal combustion engines (ICE) with a combined total horsepower (HP) of no more than 1,800 HP for the site. Includes 2007 and later model year engines manufactured after the applicable e | 2016-03-08 | catalyst | Great Plains Analytical Services | 221 hp | 0.70 g/hp-hr | 116 hp | 0.12 g/hp-hr | 6348 03 | VOC - Volatile Organic Compounds | PP | Y | NA
2016 | 1242 | 0630005037 | Blue Racer Midstream LLC - Guernsey Co Field Station #1 | East of I-70E and US 40E | Fairview | 43736 |  | Guernsey | P011 | Compressor engine 1875 HP Cat 3606 4 stroke lean burn oxidation catalyst | 2016-10-18 | CC-2(Catalytic Converter): Catalytic Converter 2; CC-3(Catalytic Converter): Catalytic Converter 3 | Great Plains Analytical Services | 1,875 hp | 0.7 g/hp-hr | 1,822 hp | 0.458 g/hp-hr | 6348 03 | VOC - Volatile Organic Compounds | PP | N | NA
2016 | 1245 | 0630005037 | Blue Racer Midstream LLC - Guernsey Co Field Station #1 | East of I-70E and US 40E | Fairview | 43736 |  | Guernsey | P012 | Compressor engine 1875 HP Cat 3606 4 stroke lean burn oxidation catalyst | 2016-10-18 | CC-2(Catalytic Converter): Catalytic Converter 2; CC-3(Catalytic Converter): Catalytic Converter 3 | Great Plains Analytical Services | 1,875 hp | 0.7 g/hp-hr | 1,800 hp | 0.473 g/hp-hr | 6348 03 | VOC - Volatile Organic Compounds | PP | N | NA
2016 | 1259 | 0630005039 | E2 Ohio Compression LLC - Hayes | 21260 Grape Hollow Rd | Salesville | 43778 |  | Guernsey | P032 | Cat G350B 690 HP NG engine | 2016-08-31 | Cat01(Catalytic Converter): Oxidation Catalyst for 4SLB RICE | E2Energy Services | 690 hp | 0.55 g/hp-hr | 345 hp | 0.25 g/hp-hr | 6348 03 | VOC - Volatile Organic Compounds | PP | Y | NA
2016 | 1264 | 0630005041 | E2 Energy Services - Borton | 65483 Lydick Rd | Quaker City | 43773 |  | Guernsey | P002 | 1,680 Hp. Waukesha (L7044GSI) natural gas-fired, rich burn, turbocharged, with oxidation catalyst, compressor engine (Model Year 2014) | 2016-03-02 | C-2701C(Catalytic Converter): Engine Catalyst | E2 Energy Services | 1680 hp | 0.03 g/hp-hr | 1519 hp | 0.01 g/hp-hr | 6348 03 | VOC - Volatile Organic Compounds | PP | N | NA
2016 | 1265 | 0630005041 | E2 Energy Services - Borton | 65483 Lydick Rd | Quaker City | 43773 |  | Guernsey | P004 | 1,680 Hp. Waukesha (L7044GSI) natural gas-fired, rich burn, turbocharged, with oxidation catalyst, compressor engine (Model Year 2014) | 2016-05-12 | C-2703C(Catalytic Converter): Engine Catalyst | E2 Energy Services | 1680 hp | 0.03 g/hp-hr | 1348 hp | 0.015 g/hp-hr | 6348 03 | VOC - Volatile Organic Compounds | PP | Y | NA
2016 | 1270 | 0630005050 | Carrizo Utica LLC- Wagler Production Facility | Deck Rd | Londonderry Twp. | 45647 |  | Guernsey | P002 | One or multiple stationary natural gas-fired spark ignition (SI) internal combustion engines (ICE) with a combined total horsepower of 1,800 HP for the site. Includes 2007 or later model year engines manufactured after the applicable effective date iden | 2016-04-11 | catalyst | Alliance Source Testing | 275 hp | 0.7 g/hp-hr | 263 hp | 0.03 g/hp-hr | 25A | VOC - Volatile Organic Compounds | PP | Y | NA
2016 | 1272 | 0630005054 | Ascent Resources - Utica LLC - J Bar J Wellpad | 25204 Oxford Rd | Quaker City | 43773 |  | Guernsey | P002 | One or multiple stationary natural gas-fired spark ignition (SI) internal combustion engines (ICE) with a combined total horsepower (HP) of no more than 1,800 HP for the site. Includes 2007 and later model year engines manufactured after the applicable e | 2016-03-08 | catalyst | Great Plains Analytical Services, Inc | 211 hp | 0.70 g/hp-hr | 117 hp | 0.06 g/hp-hr | 6348 03 | VOC - Volatile Organic Compounds | PP | Y | NA
2016 | 1274 | 0630005055 | Ascent Resources - Utica LLC - Eggleston Wellpad | 17146 Easton Rd | Salesville | 43778 |  | Guernsey | P002 | One or multiple stationary natural gas-fired spark ignition (SI) internal combustion engines (ICE) with a combined total horsepower (HP) of no more than 1,800 HP for the site. Includes 2007 and later model year engines manufactured after the applicable e | 2016-06-28 | catalyst | EcoTest Energy Resources | 211 hp | 0.7 g/hp-hr | 80 hp | 0.01 g/hp-hr | 320 | VOC - Volatile Organic Compounds | PP | Y | NA
2016 | 1283 | 0634005027 | Arrowhead Compressor Station | E of Clements Rd and S of Jockey Hollow | Athens Twp. | 43977 |  | Harrison | P008 | Compressor Engine #5 - Caterpillar G3608 - natural gas fired four-stroke, lean burn internal combustion engine rated at an operating capacity of 2,370 horsepower equipped with a catalytic convertor | 2016-10-31 | CC005(Catalytic Converter): Compressor Engine #5 Catalytic Convertor; CC006(Catalytic Converter): Compressor Engine #6 Catalytic Convertor | Air Hygiene International Inc. | 2,370 hp | 0.7 g/hp-hr | 2,264 hp | 0.20 g/hp-hr | 25A | VOC - Volatile Organic Compounds | PP | Y | NA
2016 | 1284 | 0634005027 | Arrowhead Compressor Station | E of Clements Rd and S of Jockey Hollow | Athens Twp. | 43977 |  | Harrison | P009 | Compressor Engine #6 - Caterpillar G3608 - natural gas fired four-stroke, lean burn internal combustion engine rated at an operating capacity of 2,370 horsepower equipped with a catalytic convertor | 2016-10-31 | CC005(Catalytic Converter): Compressor Engine #5 Catalytic Convertor; CC006(Catalytic Converter): Compressor Engine #6 Catalytic Convertor | Air Hygiene International Inc. | 2,370 hp | 0.7 g/hp-hr | 2,202 hp | 0.23 g/hp-hr | 25A | VOC - Volatile Organic Compounds | PP | Y | NA
2016 | 1289 | 0634005027 | Arrowhead Compressor Station | E of Clements Rd and S of Jockey Hollow | Athens Twp. | 43977 |  | Harrison | P010 | Compressor Engine #7 - Caterpillar G3608 - natural gas fired four-stroke, lean burn internal combustion engine rated at an operating capacity of 2,370 horsepower equipped with a catalytic convertor | 2016-11-01 | CC07(Catalytic Converter): Compressor Engine #7 Catalytic Convertor; CC008(Catalytic Converter): Compressor Engine #8 Catalytic Convertor | Air Hygiene International Inc. | 2,370 hp | 0.7 g/hp-hr | 2,210 hp | 0.20 g/hp-hr | 25A | VOC - Volatile Organic Compounds | PP | Y | NA
2016 | 1290 | 0634005027 | Arrowhead Compressor Station | E of Clements Rd and S of Jockey Hollow | Athens Twp. | 43977 |  | Harrison | P011 | Compressor Engine #8 - Caterpillar G3608 - natural gas fired four-stroke, lean burn internal combustion engine rated at an operating capacity of 2,370 horsepower equipped with a catalytic convertor | 2016-11-01 | CC07(Catalytic Converter): Compressor Engine #7 Catalytic Convertor; CC008(Catalytic Converter): Compressor Engine #8 Catalytic Convertor | Air Hygiene International Inc. | 2,370 hp | 0.7 g/hp-hr | 2,194 hp | 0.16 g/hp-hr | 25A | VOC - Volatile Organic Compounds | PP | Y | NA
2016 | 1297 | 0634005033 | Harrison West Compressor Station | Possum Hollow Road | Freeport | 43973 |  | Harrison | P005 | Compressor Engine #5 - 1980 HP (15.43 MMBtu/hr) Waukesha P9390 - natural gas-fired four-stroke rich burn internal combustion engine equipped with a three-way oxidation catalyst controlling CH2O, CO, NOx, & VOCs by 80, 97, 98.5 & 66 percent respectively | 2016-05-13 | CC005(Catalytic Converter): Compressor Engine #5 - 3-way Catalyst; CC006(Catalytic Converter): Compressor Engine #6 - 3-way Catalyst; CC007(Catalytic Converter): Compressor Engine #7 - 3-way Catalyst | Air Hygiene International | 1980 hp | 0.7 g/hp-hr | 1612 hp | 0.09 g/hp-hr | 25A | VOC - Volatile Organic Compounds | PP | Y | NA
2016 | 1298 | 0634005033 | Harrison West Compressor Station | Possum Hollow Road | Freeport | 43973 |  | Harrison | P006 | Compressor Engine #6 - 1980 HP (15.43 MMBtu/hr) Waukesha P9390 - natural gas-fired four-stroke rich burn internal combustion engine equipped with a three-way oxidation catalyst controlling CH2O, CO, NOx, & VOCs by 80, 97, 98.5 & 66 percent respectively | 2016-05-13 | CC005(Catalytic Converter): Compressor Engine #5 - 3-way Catalyst; CC006(Catalytic Converter): Compressor Engine #6 - 3-way Catalyst; CC007(Catalytic Converter): Compressor Engine #7 - 3-way Catalyst | Air Hygiene International | 1980 hp | 0.7 g/hp-hr | 1638 hp | 0.06 g/hp-hr | 25A | VOC - Volatile Organic Compounds | PP | Y | NA
2016 | 1299 | 0634005033 | Harrison West Compressor Station | Possum Hollow Road | Freeport | 43973 |  | Harrison | P007 | Compressor Engine #7 - 1980 HP (15.43 MMBtu/hr) Waukesha P9390 - natural gas-fired four-stroke rich burn internal combustion engine equipped with a three-way oxidation catalyst controlling CH2O, CO, NOx, & VOCs by 80, 97, 98.5 & 66 percent respectively | 2016-05-13 | CC005(Catalytic Converter): Compressor Engine #5 - 3-way Catalyst; CC006(Catalytic Converter): Compressor Engine #6 - 3-way Catalyst; CC007(Catalytic Converter): Compressor Engine #7 - 3-way Catalyst | Air Hygiene International | 1980 hp | 0.7 g/hp-hr | 1613 hp | 0.03 g/hp-hr | 25A | VOC - Volatile Organic Compounds | PP | Y | NA
2016 | 1306 | 0634005033 | Harrison West Compressor Station | Possum Hollow Road | Freeport | 43973 |  | Harrison | P001 | Compressor Engine #1 - 1480 HP (11.39 MMBtu/hr) Waukesha L7042 - natural gas-fired four-stroke rich burn internal combustion engine equipped with a three-way oxidation catalyst controlling CH2O, CO, NOx, & VOCs by 80, 97, 98.5 & 66 percent respectively | 2016-04-28 | CC001(Catalytic Converter): Compressor Engine #1 - 3-way Catalyst; CC002(Catalytic Converter): Compressor Engine #2 - 3-way Catalyst; CC004(Catalytic Converter): Compressor Engine #4 - 3-way Catalyst | Air Hygiene, Inc | 1480 hp | 0.7 g/hp-hr | 1181 hp | 0.08 g/hp-hr | 25A | VOC - Volatile Organic Compounds | PP | Y | NA
2016 | 1307 | 0634005033 | Harrison West Compressor Station | Possum Hollow Road | Freeport | 43973 |  | Harrison | P002 | Compressor Engine #2 - 1480 HP (11.39 MMBtu/hr) Waukesha L7042 - natural gas-fired four-stroke rich burn internal combustion engine equipped with a three-way oxidation catalyst controlling CH2O, CO, NOx, & VOCs by 80, 97, 98.5 & 66 percent respectively | 2016-04-28 | CC001(Catalytic Converter): Compressor Engine #1 - 3-way Catalyst; CC002(Catalytic Converter): Compressor Engine #2 - 3-way Catalyst; CC004(Catalytic Converter): Compressor Engine #4 - 3-way Catalyst | Air Hygiene, Inc | 1480 hp | 0.7 g/hp-hr | 1611 hp | 0.11 g/hp-hr | 25A | VOC - Volatile Organic Compounds | PP | Y | NA
2016 | 1308 | 0634005033 | Harrison West Compressor Station | Possum Hollow Road | Freeport | 43973 |  | Harrison | P004 | Compressor Engine #4 - 1980 HP (15.43 MMBtu/hr) Waukesha P9390 - natural gas-fired four-stroke rich burn internal combustion engine equipped with a three-way oxidation catalyst controlling CH2O, CO, NOx, & VOCs by 80, 97, 98.5 & 66 percent respectively | 2016-04-28 | CC001(Catalytic Converter): Compressor Engine #1 - 3-way Catalyst; CC002(Catalytic Converter): Compressor Engine #2 - 3-way Catalyst; CC004(Catalytic Converter): Compressor Engine #4 - 3-way Catalyst | Air Hygiene, Inc | 1980 hp | 0.7 g/hp-hr | 1589 hp | 0.07 g/hp-hr | 25A | VOC - Volatile Organic Compounds | PP | Y | NA
2016 | 1313 | 0634005034 | Lake Compressor Station | County Highway 21 | Freeport | 43973 |  | Harrison | P001 | Compressor Engine #1 - 1480 HP (11.39 MMBtu/hr) Waukesha L7042 - natural gas-fired four-stroke rich burn internal combustion engine equipped with a three-way oxidation catalyst controlling CH2O, CO, NOx, & VOCs by 80, 97, 98.5 & 66 percent respectively | 2016-03-28 | CC001(Catalytic Converter): Compressor Engine #1 - 3-way Catalyst; CC002(Catalytic Converter): Compressor Engine #2 - 3-way Catalyst | Air Hygiene, Inc. | 1480 hp | 0.28 g/hp-hr | 1233 hp | 0.09 g/hp-hr | 25A | VOC - Volatile Organic Compounds | PP | Y | NA
2016 | 1314 | 0634005034 | Lake Compressor Station | County Highway 21 | Freeport | 43973 |  | Harrison | P002 | Compressor Engine #2 - 1480 HP (11.39 MMBtu/hr) Waukesha L7042 - natural gas-fired four-stroke rich burn internal combustion engine equipped with a three-way oxidation catalyst controlling CH2O, CO, NOx, & VOCs by 80, 97, 98.5 & 66 percent respectively | 2016-03-28 | CC001(Catalytic Converter): Compressor Engine #1 - 3-way Catalyst; CC002(Catalytic Converter): Compressor Engine #2 - 3-way Catalyst | Air Hygiene, Inc. | 1480 hp | 0.38 g/hp-hr | 1374 hp | 0.08 g/hp-hr | 25A | VOC - Volatile Organic Compounds | PP | Y | NA
2016 | 1321 | 0634005034 | Lake Compressor Station | County Highway 21 | Freeport | 43973 |  | Harrison | P004 | Compressor Engine #4 - 1980 HP (15.43 MMBtu/hr) Waukesha P9390 - natural gas-fired four-stroke rich burn internal combustion engine equipped with a three-way oxidation catalyst controlling CH2O, CO, NOx, & VOCs by 80, 97, 98.5 & 66 percent respectively | 2016-04-14 | CC004(Catalytic Converter): Compressor Engine #4 - 3-way Catalyst; CC005(Catalytic Converter): Compressor Engine #5 - 3-way Catalyst; CC011(Catalytic Converter): Compressor Engine #9 - 3-way Catalyst | Air Hygiene, Inc | 1980 hp | 0.7 g/hp-hr | 1647 hp | 0.12 g/hp-hr | 25A | VOC - Volatile Organic Compounds | PP | N | NA | test did conform to test method-document locked
2016 | 1322 | 0634005034 | Lake Compressor Station | County Highway 21 | Freeport | 43973 |  | Harrison | P005 | Compressor Engine #5 - 1980 HP (15.43 MMBtu/hr) Waukesha P9390 - natural gas-fired four-stroke rich burn internal combustion engine equipped with a three-way oxidation catalyst controlling CH2O, CO, NOx, & VOCs by 80, 97, 98.5 & 66 percent respectively | 2016-04-14 | CC004(Catalytic Converter): Compressor Engine #4 - 3-way Catalyst; CC005(Catalytic Converter): Compressor Engine #5 - 3-way Catalyst; CC011(Catalytic Converter): Compressor Engine #9 - 3-way Catalyst | Air Hygiene, Inc | 1980 hp | 0.7 g/hp-hr | 1642 hp | 0.07 g/hp-hr | 25A | VOC - Volatile Organic Compounds | PP | N | NA | test did conform to test method-document locked
2016 | 1323 | 0634005034 | Lake Compressor Station | County Highway 21 | Freeport | 43973 |  | Harrison | P011 | Compressor Engine #9 - Waukesha L7042 - natural gas fired four-stroke, rich burn internal combustion engine rated at an operating capacity of 1,480 horsepower equipped with a three-way oxidation catalyst. | 2016-04-14 | CC004(Catalytic Converter): Compressor Engine #4 - 3-way Catalyst; CC005(Catalytic Converter): Compressor Engine #5 - 3-way Catalyst; CC011(Catalytic Converter): Compressor Engine #9 - 3-way Catalyst | Air Hygiene, Inc | 1980 hp | 0.7 g/hp-hr | 1079 hp | 0.02 g/hp-hr | 25A | VOC - Volatile Organic Compounds | PP | N | NA | test did conform to test method-document locked
2016 | 1326 | 0634005048 | Gulfport Energy - Boy Scout Well Pad | 79900 Adams Rd | Tippecanoe | 44699 |  | Harrison | P002 | One 630 hp Caterpillar 630 and one 118 hp Cummins G8.3C natural gas-fired engines for compressors. | 2016-08-24 | catalyst | Ecotest Inc. | 630 hp | 1.00 g/hp-hr | 455 hp | 0.58 g/hp-hr | 6348 03 | VOC - Volatile Organic Compounds | PP | Y | NA
2016 | 1328 | 0634005056 | Scio Compressor Station | 37650 Bower Rd | Scio | 43988 |  | Harrison | P001 | Compressor Engine #1 - 1,775 HP Caterpillar G3606 (4S-LB) - natural gas-fired four-cycle lean burn internal combustion engine equipped with an oxidation catalyst controlling CO & VOC emissions. | 2016-06-06 | CC001(Catalytic Converter): Compressor Engine #1 - Oxidation Catalyst | EcoTest Energy Services | 1775 hp | 0.7 g/hp-hr | 1700 hp | 0.06 g/hp-hr | 320 | VOC - Volatile Organic Compounds | PP | Y | NA
2016 | 1331 | 0634005056 | Scio Compressor Station | 37650 Bower Rd | Scio | 43988 |  | Harrison | P002 | Compressor Engine #2 - 1,775 HP Caterpillar G3606 (4S-LB) - natural gas-fired four-cycle lean burn internal combustion engine equipped with an oxidation catalyst controlling CO & VOC emissions | 2016-06-06 | CC002(Catalytic Converter): Compressor Engine #2 - Oxidation Catalyst | EcoTest Energy Services | 1775 hp | 0.7 g/hp-hr | 1695 hp | 0.04 g/hp-hr | 320 | VOC - Volatile Organic Compounds | PP | Y | NA
2016 | 1334 | 0634005056 | Scio Compressor Station | 37650 Bower Rd | Scio | 43988 |  | Harrison | P003 | Compressor Engine #3 - 1,775 HP Caterpillar G3606 (4S-LB) - natural gas-fired four-cycle lean burn internal combustion engine equipped with an oxidation catalyst controlling CO & VOC emissions | 2016-06-06 | CC003(Catalytic Converter): Compressor Engine #3 - Oxidation Catalyst | EcoTest Energy Services | 1775 hp | 0.7 g/hp-hr | 1680 hp | 0.04 g/hp-hr | 320 | VOC - Volatile Organic Compounds | PP | Y | NA
2016 | 1336 | 0634005056 | Scio Compressor Station | 37650 Bower Rd | Scio | 43988 |  | Harrison | P004 | Compressor Engine #4 - 1,775 HP Caterpillar G3606 (4S-LB) - natural gas-fired four-cycle lean burn internal combustion engine equipped with an oxidation catalyst controlling CO & VOC emissions | 2016-06-06 | CC004(Catalytic Converter): Compressor Engine #4 - Oxidation Catalyst | EcoTest Energy Services | 1775 hp | 0.7 g/hp-hr | 1750 hp | 0.05 g/hp-hr | 320 | VOC - Volatile Organic Compounds | PP | Y | NA
2016 | 1339 | 0634005056 | Scio Compressor Station | 37650 Bower Rd | Scio | 43988 |  | Harrison | P005 | Compressor Engine #5 - 1,775 HP Caterpillar G3606 (4S-LB) - natural gas-fired four-cycle lean burn internal combustion engine equipped with an oxidation catalyst controlling CO & VOC emissions | 2016-06-06 | CC005(Catalytic Converter): Compressor Engine #5 - Oxidation Catalyst | EcoTest Energy Services | 1775 hp | 0.7 g/hp-hr | 1720 hp | 0.05 g/hp-hr | 320 | VOC - Volatile Organic Compounds | PP | Y | NA
2016 | 1344 | 0634005056 | Scio Compressor Station | 37650 Bower Rd | Scio | 43988 |  | Harrison | P006 | Compressor Engine #6 - 1,775 HP Caterpillar G3606 (4S-LB) - natural gas-fired four-cycle lean burn internal combustion engine equipped with an oxidation catalyst controlling CO & VOC emissions | 2016-06-06 | CC006(Catalytic Converter): Compressor Engine #6 - Oxidation Catalyst | EcoTest Energy Services | 1775 hp | 0.7 g/hp-hr | 1720 hp | 0.06 g/hp-hr | 320 | VOC - Volatile Organic Compounds | PP | Y | NA
2016 | 1346 | 0634005056 | Scio Compressor Station | 37650 Bower Rd | Scio | 43988 |  | Harrison | P007 | Compressor Engine #7 - 1,775 HP Caterpillar G3606 (4S-LB) - natural gas-fired four-cycle lean burn internal combustion engine equipped with an oxidation catalyst controlling CO & VOC emissions | 2016-06-07 | CC007(Catalytic Converter): Compressor Engine #7 - Oxidation Catalyst | EcoTest Energy Services | 1775 hp | 0.7 g/hp-hr | 1700 hp | 0.05 g/hp-hr | 320 | VOC - Volatile Organic Compounds | PP | Y | NA
2016 | 1349 | 0634005056 | Scio Compressor Station | 37650 Bower Rd | Scio | 43988 |  | Harrison | P008 | Compressor Engine #8 - 1,775 HP Caterpillar G3606 (4S-LB) - natural gas-fired four-cycle lean burn internal combustion engine equipped with an oxidation catalyst controlling CO & VOC emissions | 2016-06-07 | CC008(Catalytic Converter): Compressor Engine #8 - Oxidation Catalyst | EcoTest Energy Services | 1775 hp | 0.7 g/hp-hr | 1707 hp | 0.07 g/hp-hr | 320 | VOC - Volatile Organic Compounds | PP | Y | NA
2016 | 1351 | 0634005056 | Scio Compressor Station | 37650 Bower Rd | Scio | 43988 |  | Harrison | P009 | Compressor Engine #9 - 1,775 HP Caterpillar G3606 (4S-LB) - natural gas-fired four-cycle lean burn internal combustion engine equipped with an oxidation catalyst controlling CO & VOC emissions | 2016-06-07 | CC009(Catalytic Converter): Compressor Engine #9 - Oxidation Catalyst | EcoTest Energy Services | 1775 hp | 0.7 g/hp-hr | 1760 hp | 0.06 g/hp-hr | 320 | VOC - Volatile Organic Compounds | PP | Y | NA
2016 | 1354 | 0634005056 | Scio Compressor Station | 37650 Bower Rd | Scio | 43988 |  | Harrison | P010 | Compressor Engine #10 - 1,775 HP Caterpillar G3606 (4S-LB) - natural gas-fired four-cycle lean burn internal combustion engine equipped with an oxidation catalyst controlling CO & VOC emissions | 2016-06-07 | CC010(Catalytic Converter): Compressor Engine #10 - Oxidation Catalyst | EcoTest Energy Services | 1775 hp | 0.7 g/hp-hr | 1725 hp | 0.06 g/hp-hr | 320 | VOC - Volatile Organic Compounds | PP | Y | NA
2016 | 1358 | 0634005070 | Gulfport Energy - County Line II - Gustina-Bear | 34011 Cadiz-Piedmont Rd | Flushing | 43977 |  | Harrison | P002 | One or multiple stationary natural gas-fired spark ignition (SI) internal combustion engines (ICE) wiht a combined total horsepower (HP) of no more than 1,800 HP for the site. | 2016-02-17 | cagalyst | Ecotest Energy Services | 118 hp | 1.0 g/hp-hr | 90 hp | 0.03 g/hp-hr | 6348 03 | VOC - Volatile Organic Compounds | PP | Y | NA
2016 | 1362 | 0634005086 | Ascent Resources - Utica LLC - Hamilton 19-11N-6W | 34385 Kennedy Ridge Rd | Flushing | 43977 |  | Harrison | P002 | One or multiple stationary natural gas-fired spark ignition (SI) internal combustion engines (ICE) with a combined total horsepower (HP) of no more than 1,800 HP for the site. Includes 2007 and later model year engines manufactured after the applicable e | 2016-05-23 | catalyst | Great Plaines Analytical Services | 400 hp 203 hp | 1.0 g/hp-hr | 338 hp 188 hp | 0.39 g/hp-hr | 6348 03 | VOC - Volatile Organic Compounds | PP | Y | NA | P002 two engines on allowable rate
2016 | 1363 | 0634005086 | Ascent Resources - Utica LLC - Hamilton 19-11N-6W | 34385 Kennedy Ridge Rd | Flushing | 43977 |  | Harrison | P002 | One or multiple stationary natural gas-fired spark ignition (SI) internal combustion engines (ICE) with a combined total horsepower (HP) of no more than 1,800 HP for the site. Includes 2007 and later model year engines manufactured after the applicable e | 2016-05-26 | catalyst | Great Plaines Analytical Services | 400 hp 203 hp | 1.0 g/hp-hr | 338 hp 188 hp | 0.39 g/hp-hr | 6348 03 | VOC - Volatile Organic Compounds | PP | Y | NA | P002 two engines on allowable rate
2016 | 1368 | 0634005090 | E2 Ohio Compression LLC - Mizer | 84500 Addy Rd | Cadiz | 43907 |  | Harrison | P010 | One stationary natural gas-fired spark ignition (SI) internal combustion engine (ICE) with a total horsepower (HP) of 1680 HP. Includes a 2007 and later model year engine manufactured after the applicable effective date identified in 40 CFR 60.4230(a)(3) | 2016-02-25 | Cat03(Catalytic Converter): 3-Way NSCR for 4SRB RICE | E2 Energy Services | 1680 hp | 0.04 g/hp-hr | 1534 hp | 0.04 g/hp-hr | 6348 03 | VOC - Volatile Organic Compounds | PP | Y | NA
2016 | 1371 | 0634005090 | E2 Ohio Compression LLC - Mizer | 84500 Addy Rd | Cadiz | 43907 |  | Harrison | P009 | One stationary natural gas-fired spark ignition (SI) internal combustion engine (ICE) with a total horsepower (HP) of 1680 HP. Includes a 2007 and later model year engine manufactured after the applicable effective date identified in 40 CFR 60.4230(a)(3) | 2016-02-24 | Cat02(Catalytic Converter): 3-Way NSCR for 4SRB RICE | E2 Energy Services | 1680 hp | 0.04 g/hp-hr | 1563 hp | 0.02 g/hp-hr | 6348 03 | VOC - Volatile Organic Compounds | PP | Y | NA
2016 | 1374 | 0634005090 | E2 Ohio Compression LLC - Mizer | 84500 Addy Rd | Cadiz | 43907 |  | Harrison | P011 | One stationary natural gas-fired spark ignition (SI) internal combustion engine (ICE) with a total horsepower (HP) of 1680 HP. Includes a 2007 and later model year engine manufactured after the applicable effective date identified in 40 CFR 60.4230(a)(3) | 2016-02-26 | Cat04(Catalytic Converter): 3-Way NSCR for 4SLB Rice | E2 Energy Services | 1680 hp | 0.04 g/hp-hr | 1431 hp | 0.03 g/hp-hr | 6348 03 | VOC - Volatile Organic Compounds | PP | Y | NA
2016 | 1376 | 0634005121 | Ascent Resources - Utica LLC - Pettay Well Pad | 3440 Huff Run Rd | Cadiz | 43907 |  | Harrison | P002 | One or multiple stationary natural gas-fired spark ignition (SI) internal combustion engines (ICE) with a combined total horsepower (HP) of no more than 1,800 HP for the site. Includes 2007 and later model year engines manufactured after the applicable e | 2016-05-25 | catalyst | Great Plains Analytical Services | 276 hp 225 hp | 1.0 g/hp-hr | 216 hp 154 hp | 0.217 g/hp-hr | 6348 03 | VOC - Volatile Organic Compounds | PP | N | NA | two engines 276 hp and 225 hp. emissions rates and allowable combined
2016 | 1384 | 0634005123 | Yoder Compressor Station | 79300 Cassville Rd | Cadiz | 43907 |  | Harrison | P001 | Natural gas-fired four-stroke lean burn (4SLB) internal combustion engine rated at an operating capacity of 2,370 horsepower (hp) and equipped with an oxidation catalyst. | 2016-05-19 | CC001(Catalytic Converter): Compressor Engine #1 Catalytic Converter; CC002(Catalytic Converter): Compressor Engine #2 Catalytic Converter; CC003(Catalytic Converter): Compressor Engine #3 Catalytic Converter | Air Hygiene International | 2370 hp | 1.46 lb/hr | 2889 hp | 0.22 lb/hr | 25A | VOC - Volatile Organic Compounds | PP | Y | NA
2016 | 1385 | 0634005123 | Yoder Compressor Station | 79300 Cassville Rd | Cadiz | 43907 |  | Harrison | P002 | Natural gas-fired four-stroke lean burn (4SLB) internal combustion engine rated at an operating capacity of 2,370 horsepower (hp) and equipped with an oxidation catalyst. | 2016-05-19 | CC001(Catalytic Converter): Compressor Engine #1 Catalytic Converter; CC002(Catalytic Converter): Compressor Engine #2 Catalytic Converter; CC003(Catalytic Converter): Compressor Engine #3 Catalytic Converter | Air Hygiene International | 2370 hp | 1.46 lb/hr | 2202 hp | 0.12 lb/hr | 25A | VOC - Volatile Organic Compounds | PP | Y | NA
2016 | 1386 | 0634005123 | Yoder Compressor Station | 79300 Cassville Rd | Cadiz | 43907 |  | Harrison | P003 | Natural gas-fired four-stroke lean burn (4SLB) internal combustion engine rated at an operating capacity of 2,370 horsepower (hp) and equipped with an oxidation catalyst. | 2016-05-19 | CC001(Catalytic Converter): Compressor Engine #1 Catalytic Converter; CC002(Catalytic Converter): Compressor Engine #2 Catalytic Converter; CC003(Catalytic Converter): Compressor Engine #3 Catalytic Converter | Air Hygiene International | 2370 hp | 1.46 lb/hr | 2185 hp | 0.30 lb/hr | 25A | VOC - Volatile Organic Compounds | PP | Y | NA
2016 | 1389 | 0634005127 | Chesapeake Exploration LLC - Wright 35-11-5 Pad | Lightner House Rd | Scio | 43988 |  | Harrison | P002 | One or multiple stationary natural gas-fired spark ignition (SI) internal combustion engines (ICE) with a combined total horsepower (HP) of no more than 1,800 HP for the site.* Includes 2007 and later model year engines manufactured after the applicable | 2016-02-12 | catalyst | Alliance Source Testing | 211 hp | 1.0 g/hp-hr | 190 hp | 0.03 g/hp-hr | 25A | VOC - Volatile Organic Compounds | PP | Y | NA
2016 | 1446 | 0656005010 | Dominion East Ohio - Switzerland Compressor Station | German Ridge Road | Switzerland Twp. | 43942 |  | Monroe | P001 | 3550 Hp Natural gas-fired (4SLB) Caterpillar model 3612 LE DM5309-06 compressor engines equipped with catalytic reduction (three-way). | 2016-09-22 | catalyst | Environmental Quality management | 3,550 hp | 0.7 g/hp-hr | 3,307 hp | 0.12 g/hp-hr | 25A | VOC - Volatile Organic Compounds | PP | Y | NA
2016 | 1447 | 0656005010 | Dominion East Ohio - Switzerland Compressor Station | German Ridge Road | Switzerland Twp. | 43942 |  | Monroe | P002 | 3550 Hp Natural gas-fired (4SLB) Caterpillar model 3612 LE DM5309-06 compressor engines equipped with catalytic reduction (three-way). | 2016-09-22 | catalyst | Environmental Quality management | 3,550 hp | 0.7 g/hp-hr | 3,343 hp | 0.14 g/hp-hr | 25A | VOC - Volatile Organic Compounds | PP | Y | NA
2016 | 1448 | 0656005010 | Dominion East Ohio - Switzerland Compressor Station | German Ridge Road | Switzerland Twp. | 43942 |  | Monroe | P003 | 3550 Hp Natural gas-fired (4SLB) Caterpillar model 3612 LE DM5309-06 compressor engines equipped with catalytic reduction (three-way). | 2016-09-22 | catalyst | Environmental Quality management | 3,550 hp | 0.7 g/hp-hr | 3,361 hp | 0.20 g/hp-hr | 25A | VOC - Volatile Organic Compounds | PP | Y | NA
2016 | 1449 | 0656005011 | Ormet Production Facility | 43879 St Rte 7 | Hannibal | 43931 |  | Monroe | P006 | CAT 3508BLE SI combustion engine 690 bhp | 2016-07-28 | catalyst | EcoTest Energy Services | 690 hp | 0.38 g/hp-hr | 670 hp | 0.15 g/hp-hr | 320 | VOC - Volatile Organic Compounds | PP | Y | NA
2016 | 1452 | 0656005011 | Ormet Production Facility | 43879 St Rte 7 | Hannibal | 43931 |  | Monroe | P001 | CAT 3516BLE SI combustion engine 1380 bhp | 2016-06-02 | CD-1(Catalytic Converter): Control Device for Compressor Engine-1 | EcoTest Energy Services | 1380 hp | 0.18 g/hp-hr | 850 hp | 0.18 g/hp-hr | 320 | VOC - Volatile Organic Compounds | PP | Y | NA
2016 | 1457 | 0656005014 | StatOil USA Onshore Properties Inc - Dangle PAD | 49675 Dangel Lane | Sardis | 43946 |  | Monroe | P002 | One or multiple stationary natural gas-fired spark ignition (SI) internal combustion engines (ICE) with a combined total horsepower (HP) of no more than 1,800 HP for the site.* Includes 2007 and later model year engines manufactured after the applicable | 2016-02-23 | catalyst | Ecotest Energy Services | 1775 hp | 0.70 g/hp-hr | 1600 hp | 0.65 g/hp-hr | 320 | VOC - Volatile Organic Compounds | PP | Y | NA
2016 | 1458 | 0656005017 | Triad Hunter, LLC, Stalder Pad | 49947 Twp 724 | Sardis | 43946 |  | Monroe | P002 | Natural Gas Engines | 2016-03-04 | C003(Catalytic Converter): Oxidation Catalyst | EcoTest Energy Services | 630 hp | 1.00 g/hp-hr | 590 hp | 0.02 g/hp-hr | 320 | VOC - Volatile Organic Compounds | PP | Y | NA
2016 | 1469 | 0656005025 | REX Booster Station | Twp Rd 964 | Switzerland Twp. | 43915 |  | Monroe | P001 | Caterpillar 3616 Compressor Engine. This is a natural gas fired engine associated with the Compressor Unit | 2016-05-04 | C001(Catalytic Converter): Oxidation Catalysts; C002(Catalytic Converter): Oxidation Catalysts; C003(Catalytic Converter): Oxidation Catalysts | Alliance Source Testing | 4725 hp | 2.61 lbs/hr | 4451 hp | 0.40 lb/hr | 25A | VOC - Volatile Organic Compounds | PP | Y | NA
2016 | 1470 | 0656005025 | REX Booster Station | Twp Rd 964 | Switzerland Twp. | 43915 |  | Monroe | P002 | Caterpillar 3616 Compressor Engine. This is a natural gas fired engine associated with the Compressor Unit | 2016-05-04 | C001(Catalytic Converter): Oxidation Catalysts; C002(Catalytic Converter): Oxidation Catalysts; C003(Catalytic Converter): Oxidation Catalysts | Alliance Source Testing | 4725 hp | 2.61 lbs/hr | 4451 hp | 0.86 lb/hr | 25A | VOC - Volatile Organic Compounds | PP | Y | NA
2016 | 1471 | 0656005025 | REX Booster Station | Twp Rd 964 | Switzerland Twp. | 43915 |  | Monroe | P003 | Caterpillar 3616 Compressor Engine. This is a natural gas fired engine associated with the Compressor Unit | 2016-05-04 | C001(Catalytic Converter): Oxidation Catalysts; C002(Catalytic Converter): Oxidation Catalysts; C003(Catalytic Converter): Oxidation Catalysts | Alliance Source Testing | 4725 hp | 2.61 lbs/hr | 4514 hp | 0.43 lb/hr | 25A | VOC - Volatile Organic Compounds | PP | Y | NA
2016 | 1478 | 0656005028 | Miller Compressor Station | 51103 Twp Rd 847 | Seneca Twp. | 43788 |  | Monroe | P005 | Waukesha 1680 bhp Model L7044GSI 4-stroke Natural Gas Rich Burn Gas Compressor Engine Model Year 2014 controlled by a catalyst | 2016-02-05 | C-2705C(Catalytic Converter): Engine Catalyst | E2 Energy Services | 1680 hp | 0.16 g/hp-hr | 1542 hp | 0.02 g/hp-hr | 6348 03 | VOC - Volatile Organic Compounds | PP | Y | NA
2016 | 1482 | 0656005028 | Miller Compressor Station | 51103 Twp Rd 847 | Seneca Twp. | 43788 |  | Monroe | P006 | Waukesha 1680 bhp Model L7044GSI 4-stroke Natural Gas Rich Burn Gas Compressor Engine Model Year 2014 controlled by a catalyst | 2016-01-29 | C-2706C(Catalytic Converter): Engine Catalyst | E2 Energy Services | 1680 hp | 0.16 g/hp-hr | 1545 hp | 0.03 g/hp-hr | 6348 03 | VOC - Volatile Organic Compounds | PP | Y | NA
2016 | 1484 | 0656005028 | Miller Compressor Station | 51103 Twp Rd 847 | Seneca Twp. | 43788 |  | Monroe | P007 | Waukesha 1680 bhp Model L7044GSI 4-stroke Natural Gas Rich Burn Gas Compressor Engine Model Year 2014 controlled by a catalyst | 2016-01-27 | C-2707C(Catalytic Converter): Engine Catalyst | E2 Energy Services | 1680 hp | 0.16 g/hp-hr | 1542 hp | 0.04 g/hp-hr | 6348 03 | VOC - Volatile Organic Compounds | PP | Y | NA
2016 | 1488 | 0656005028 | Miller Compressor Station | 51103 Twp Rd 847 | Seneca Twp. | 43788 |  | Monroe | P008 | Waukesha 1680 bhp Model L7044GSI 4-stroke Natural Gas Rich Burn Gas Compressor Engine Model Year 2014 controlled by a catalyst | 2016-01-21 | C-2708C(Catalytic Converter): Engine Catalyst | E2 Energy Services | 1680 hp | 0.16 g/hp-hr | 1510 hp | 0.06 g/hp-hr | 6348 03 | VOC - Volatile Organic Compounds | PP | Y | NA
2016 | 1489 | 0656005028 | Miller Compressor Station | 51103 Twp Rd 847 | Seneca Twp. | 43788 |  | Monroe | P009 | Waukesha 1680 bhp Model L7044GSI 4-stroke Natural Gas Rich Burn Gas Compressor Engine Model Year 2014 controlled by a catalyst | 2016-01-22 | C-2709C(Catalytic Converter): Engine Catalyst | E2 Energy Services | 1680 hp | 0.16 g/hp-hr | 1477 hp | 0.07 g/hp-hr | 6348 03 | VOC - Volatile Organic Compounds | PP | Y | NA
2016 | 1510 | 0656005028 | Miller Compressor Station | 51103 Twp Rd 847 | Seneca Twp. | 43788 |  | Monroe | P001 | Waukesha 1680 bhp Model L7044GSI 4-stroke Natural Gas Rich Burn Gas Compressor Engine Model Year 2014 controlled by a catalyst | 2016-06-22 | C-2701C(Catalytic Converter): Engine Catalyst; C-2702C(Catalytic Converter): Engine Catalyst; C-2703C(Catalytic Converter): Engine Catalyst; C-2704C(Catalytic Converter): Engine Catalyst; C-2705C(Catalytic Converter): Engine Catalyst; C-2706C(Catalytic Co | Alliance Source Testing | 1680 hp | 0.16 g/hp-hr | 1680 hp | 0.02 g/hp-hr | 25A | VOC - Volatile Organic Compounds | PP | N | NA
2016 | 1511 | 0656005028 | Miller Compressor Station | 51103 Twp Rd 847 | Seneca Twp. | 43788 |  | Monroe | P002 | Waukesha 1680 bhp Model L7044GSI 4-stroke Natural Gas Rich Burn Gas Compressor Engine Model Year 2014 controlled by a catalyst | 2016-06-22 | C-2701C(Catalytic Converter): Engine Catalyst; C-2702C(Catalytic Converter): Engine Catalyst; C-2703C(Catalytic Converter): Engine Catalyst; C-2704C(Catalytic Converter): Engine Catalyst; C-2705C(Catalytic Converter): Engine Catalyst; C-2706C(Catalytic Co | Alliance Source Testing | 1680 hp | 0.16 g/hp-hr | 1680 hp | 0.02 g/hp-hr | 25A | VOC - Volatile Organic Compounds | PP | N | NA
2016 | 1512 | 0656005028 | Miller Compressor Station | 51103 Twp Rd 847 | Seneca Twp. | 43788 |  | Monroe | P003 | Waukesha 1680 bhp Model L7044GSI 4-stroke Natural Gas Rich Burn Gas Compressor Engine Model Year 2014 controlled by a catalyst | 2016-06-22 | C-2701C(Catalytic Converter): Engine Catalyst; C-2702C(Catalytic Converter): Engine Catalyst; C-2703C(Catalytic Converter): Engine Catalyst; C-2704C(Catalytic Converter): Engine Catalyst; C-2705C(Catalytic Converter): Engine Catalyst; C-2706C(Catalytic Co | Alliance Source Testing | 1680 hp | 0.16 g/hp-hr | 1680 hp | 0.02 g/hp-hr | 25A | VOC - Volatile Organic Compounds | PP | N | NA
2016 | 1513 | 0656005028 | Miller Compressor Station | 51103 Twp Rd 847 | Seneca Twp. | 43788 |  | Monroe | P004 | Waukesha 1680 bhp Model L7044GSI 4-stroke Natural Gas Rich Burn Gas Compressor Engine Model Year 2014 controlled by a catalyst | 2016-06-22 | C-2701C(Catalytic Converter): Engine Catalyst; C-2702C(Catalytic Converter): Engine Catalyst; C-2703C(Catalytic Converter): Engine Catalyst; C-2704C(Catalytic Converter): Engine Catalyst; C-2705C(Catalytic Converter): Engine Catalyst; C-2706C(Catalytic Co | Alliance Source Testing | 1680 hp | 0.16 g/hp-hr | 1680 hp | 0.01 g/hp-hr | 25A | VOC - Volatile Organic Compounds | PP | N | NA
2016 | 1514 | 0656005028 | Miller Compressor Station | 51103 Twp Rd 847 | Seneca Twp. | 43788 |  | Monroe | P005 | Waukesha 1680 bhp Model L7044GSI 4-stroke Natural Gas Rich Burn Gas Compressor Engine Model Year 2014 controlled by a catalyst | 2016-06-22 | C-2701C(Catalytic Converter): Engine Catalyst; C-2702C(Catalytic Converter): Engine Catalyst; C-2703C(Catalytic Converter): Engine Catalyst; C-2704C(Catalytic Converter): Engine Catalyst; C-2705C(Catalytic Converter): Engine Catalyst; C-2706C(Catalytic Co | Alliance Source Testing | 1680 hp | 0.16 g/hp-hr | 1680 hp | 0.01 g/hp-hr | 25A | VOC - Volatile Organic Compounds | PP | N | NA
2016 | 1515 | 0656005028 | Miller Compressor Station | 51103 Twp Rd 847 | Seneca Twp. | 43788 |  | Monroe | P006 | Waukesha 1680 bhp Model L7044GSI 4-stroke Natural Gas Rich Burn Gas Compressor Engine Model Year 2014 controlled by a catalyst | 2016-06-22 | C-2701C(Catalytic Converter): Engine Catalyst; C-2702C(Catalytic Converter): Engine Catalyst; C-2703C(Catalytic Converter): Engine Catalyst; C-2704C(Catalytic Converter): Engine Catalyst; C-2705C(Catalytic Converter): Engine Catalyst; C-2706C(Catalytic Co | Alliance Source Testing | 1680 hp | 0.16 g/hp-hr | 1680 hp | 0.01 g/hp-hr | 25A | VOC - Volatile Organic Compounds | PP | N | NA
2016 | 1516 | 0656005028 | Miller Compressor Station | 51103 Twp Rd 847 | Seneca Twp. | 43788 |  | Monroe | P007 | Waukesha 1680 bhp Model L7044GSI 4-stroke Natural Gas Rich Burn Gas Compressor Engine Model Year 2014 controlled by a catalyst | 2016-06-22 | C-2701C(Catalytic Converter): Engine Catalyst; C-2702C(Catalytic Converter): Engine Catalyst; C-2703C(Catalytic Converter): Engine Catalyst; C-2704C(Catalytic Converter): Engine Catalyst; C-2705C(Catalytic Converter): Engine Catalyst; C-2706C(Catalytic Co | Alliance Source Testing | 1680 hp | 0.16 g/hp-hr | 1680 hp | 0.01 g/hp-hr | 25A | VOC - Volatile Organic Compounds | PP | N | NA
2016 | 1517 | 0656005028 | Miller Compressor Station | 51103 Twp Rd 847 | Seneca Twp. | 43788 |  | Monroe | P008 | Waukesha 1680 bhp Model L7044GSI 4-stroke Natural Gas Rich Burn Gas Compressor Engine Model Year 2014 controlled by a catalyst | 2016-06-22 | C-2701C(Catalytic Converter): Engine Catalyst; C-2702C(Catalytic Converter): Engine Catalyst; C-2703C(Catalytic Converter): Engine Catalyst; C-2704C(Catalytic Converter): Engine Catalyst; C-2705C(Catalytic Converter): Engine Catalyst; C-2706C(Catalytic Co | Alliance Source Testing | 1680 hp | 0.16 g/hp-hr | 1680 hp | 0.01 g/hp-hr | 25A | VOC - Volatile Organic Compounds | PP | N | NA
2016 | 1518 | 0656005028 | Miller Compressor Station | 51103 Twp Rd 847 | Seneca Twp. | 43788 |  | Monroe | P009 | Waukesha 1680 bhp Model L7044GSI 4-stroke Natural Gas Rich Burn Gas Compressor Engine Model Year 2014 controlled by a catalyst | 2016-06-22 | C-2701C(Catalytic Converter): Engine Catalyst; C-2702C(Catalytic Converter): Engine Catalyst; C-2703C(Catalytic Converter): Engine Catalyst; C-2704C(Catalytic Converter): Engine Catalyst; C-2705C(Catalytic Converter): Engine Catalyst; C-2706C(Catalytic Co | Alliance Source Testing | 1680 hp | 0.16 g/hp-hr | 1680 hp | 0.01 g/hp-hr | 25A | VOC - Volatile Organic Compounds | PP | N | NA
2016 | 1521 | 0656025005 | Gulfport Energy - Campbell | Seal Road | Beallsville | 43716 |  | Monroe | P002 | One or multiple stationary natural gas-fired spark ignition (SI) internal combustion engines (ICE) with a combined total horsepower (HP) of no more than 1,800 HP for the site.* Includes 2007 and later model year engines manufactured after the applicable | 2016-09-27 | catalyst | Ecotest | 1,775 hp | 1.0 g/hp-hr | 1,500 hp | 0.04 g/hp-hr | 6348 03 | VOC - Volatile Organic Compounds | PP | Y | NA
2016 | 1524 | 0656025008 | Gulfport Energy - Howell | Twp Hwy 145 | Beallsville | 43716 |  | Monroe | P002 | One or multiple stationary natural gas-fired spark ignition (SI) internal combustion engines (ICE) with a combined total horsepower (HP) of no more than 1,800 HP for the site.* Includes 2007 and later model year engines manufactured after the applicable | 2016-09-27 | catalyst | Ecotest | 1,775 hp | 1.0 g/hp-hr | 1,500 hp | 0.04 g/hp-hr | 6348 03 | VOC - Volatile Organic Compounds | PP | Y | NA
2016 | 1526 | 0656025012 | Goliath Compressor Station | 48208 St Rte 556 | Beallsville | 43716 |  | Monroe | P001 | Compressor #1 - driven by Caterpillar G3608 engine | 2016-01-13 | C301Catalyst(Other): null | Technical Compliance Solutions | 2370 hp | 0.66 lb/hr | 1497 hp | 0.32 lb/hr | 320 | VOC - Volatile Organic Compounds | PP | Y | NA
2016 | 1529 | 0656025012 | Goliath Compressor Station | 48208 St Rte 556 | Beallsville | 43716 |  | Monroe | P002 | Compressor #2 - driven by Caterpillar G3608 engine | 2016-01-13 | C302Catalyst(Other): null | Technical Compliance Solutions | 2370 hp | 0.66 lb/hr | 1501 hp | 0.24 lb/hr | 320 | VOC - Volatile Organic Compounds | PP | Y | NA
2016 | 1535 | 0656025012 | Goliath Compressor Station | 48208 St Rte 556 | Beallsville | 43716 |  | Monroe | P003 | Compressor #3 - driven by Caterpillar G3608 engine | 2016-01-14 | C303Catalyst(Other): | Technical Compliance Solutions | 2370 hp | 0.66 lb/hr | 1523 hp | 0.24 lb/hr | 320 | VOC - Volatile Organic Compounds | PP | Y | NA
2016 | 1540 | 0656025012 | Goliath Compressor Station | 48208 St Rte 556 | Beallsville | 43716 |  | Monroe | P004 | Compressor #4 - driven by Caterpillar G3608 engine | 2016-01-13 | C304Catalyst(Other): null | Technical Compliance Solutions | 2370 hp | 0.66 lb/hr | 1501 hp | 0.27 lb/hr | 320 | VOC - Volatile Organic Compounds | PP | Y | NA
2016 | 1541 | 0656025012 | Goliath Compressor Station | 48208 St Rte 556 | Beallsville | 43716 |  | Monroe | P005 | Compressor #5 - driven by Caterpillar G3608 engine | 2016-01-13 | C305Catalyst(Other): null | Technical Compliance Solutions | 2370 hp | 0.66 lb/hr | 1497 hp | 0.36 lb/hr | 320 | VOC - Volatile Organic Compounds | PP | Y | NA
2016 | 1547 | 0656035009 | Eureka Midstream-Zink Compressor Station | 51213 Krebs Hill Rd | Clarington | 43915 |  | Monroe | P006 | Natural Gas Fueled Lean Burn 4-Stroke Caterpillar G3608TALE Compressor Engine | 2016-04-12 | catalyst | EcoTest Energy Services | 2370 hp | 0.823 lb/hr | 2150 hp | 0.09 lb/hr | 320 | VOC - Volatile Organic Compounds | PP | Y | NA | P006 serial number BEN00694 P007 serial number BEN00693
2016 | 1549 | 0656035009 | Eureka Midstream-Zink Compressor Station | 51213 Krebs Hill Rd | Clarington | 43915 |  | Monroe | P007 | Natural Gas Fueled Lean Burn 4-Stroke Caterpillar G3608TALE Compressor Engine | 2016-04-12 | catalyst | EcoTest Energy Services | 2370 hp | 0.823 lb/hr | 2150 hp | 0.36 lb/hr | 320 | VOC - Volatile Organic Compounds | PP | Y | NA | P006 serial number BEN00694 P007 serial number BEN00693
2016 | 1551 | 0656035012 | CNX Gas LLC - Switz 6 Production Facility | 49498 SR 556 | Clarington | 43915 |  | Monroe | P002 | NOT INSTALLED AT PERMIT ISSUANCE TIME NG engine | 2016-05-16 | catalyst | Ecotest Energy Services | 68 hp, 276 hp 425 hp | 3.0 g/hp-hr | 35 hp, 102 hp, 188 hp | 0.17 g/hp-hr | 320 | VOC - Volatile Organic Compounds | PP | Y | NA | 425 hp engine, 276 hp and 68 hp engine combined allowable for P002
2016 | 1555 | 0656035012 | CNX Gas LLC - Switz 6 Production Facility | 49498 SR 556 | Clarington | 43915 |  | Monroe | P002 | NOT INSTALLED AT PERMIT ISSUANCE TIME NG engine | 2016-06-01 | catalyst | Ecotest Energy Services | 68 hp, 276 hp 425 hp | 3.0 g/hp-hr | 35 hp, 102 hp, 188 hp | 0.17 g/hp-hr | 320 | VOC - Volatile Organic Compounds | PP | Y | NA | 425 hp engine, 276 hp and 68 hp engine combined allowable for P002
2016 | 1558 | 0656065002 | Antero Resources- Webb Pad | 42006 Sandbar Rd | Lewisville | 43754 |  | Monroe | P002 | One or multiple stationary natural gas-fired spark ignition (SI) internal combustion engines (ICE) with a combined total horsepower (HP) of no more than 1,800 HP for the site.* Includes 2007 and later model year engines manufactured after the applicable | 2016-02-05 | catalyst | Techhical Compliance Solutions | 400 hp | 1.0 g/hp-hr | 379 hp | 0.04 g/hp-hr | 320 | VOC - Volatile Organic Compounds | PP | N | NA
2016 | 1561 | 0656065006 | Antero Resources - Hercher Pad | 39886 Township Rd | Lewisville | 43754 |  | Monroe | P002 | One or multiple stationary natural gas-fired spark ignition (SI) internal combustion engines (ICE) with a combined total horsepower (HP) of no more than 1,800 HP for the site.* Includes 2007 and later model year engines manufactured after the applicable | 2016-02-05 | catalyst | Technical Compliance Solutions | 1,775 hp | 1.00 g/hp-hr | 1,605 hp | 0.19 g/hp-hr | 320 | VOC - Volatile Organic Compounds | PP | Y | NA
2016 | 1563 | 0656105005 | E2 Appalachian Compression LLC - Reusser | Twp Hwy 68 and Twp Hwy 66 | Woodsfield | 43793 |  | Monroe | P001 | 1680 Hp. natural gas rich burn compressor engine - Waukesha L7044GSI | 2016-03-18 | C-1(Catalytic Converter): Engine Catalyst | E2 Energy Services | 1680 hp | 0.22 lb/hr | 1538 hp | 0.9 lb/hr | 6348 03 | VOC - Volatile Organic Compounds | PP | Y | NA
2016 | 1566 | 0656105005 | E2 Appalachian Compression LLC - Reusser | Twp Hwy 68 and Twp Hwy 66 | Woodsfield | 43793 |  | Monroe | P004 | 1680 Hp. natural gas rich burn compressor engine - Waukesha L7044GSI | 2016-03-09 | C-4(Catalytic Converter): Engine #4 Catalyst | E2 Energy Services | 1680 hp | 0.22 lb/hr | 1481 hp | 0.07 lb/hr | 6348 03 | VOC - Volatile Organic Compounds | PP | Y | NA
2016 | 1569 | 0656105005 | E2 Appalachian Compression LLC - Reusser | Twp Hwy 68 and Twp Hwy 66 | Woodsfield | 43793 |  | Monroe | P005 | 1680 Hp. natural gas rich burn compressor engine - Waukesha L7044GSI | 2016-03-10 | C-5(Catalytic Converter): Engine #5 Catalyst | E2 Energy Services | 1680 hp | 0.22 lb/hr | 1479 hp | 0.05 lb/hr | 6348 03 | VOC - Volatile Organic Compounds | PP | Y | NA
2016 | 1572 | 0656105005 | E2 Appalachian Compression LLC - Reusser | Twp Hwy 68 and Twp Hwy 66 | Woodsfield | 43793 |  | Monroe | P006 | 1680 Hp. natural gas rich burn compressor engine - Waukesha L7044GSI | 2016-03-10 | C-6(Catalytic Converter): Engine #6Catalyst | E2 Energy Services | 1680 hp | 0.22 lb/hr | 1592 hp | 0.06 lb/hr | 6348 03 | VOC - Volatile Organic Compounds | PP | Y | NA
2016 | 1575 | 0656105005 | E2 Appalachian Compression LLC - Reusser | Twp Hwy 68 and Twp Hwy 66 | Woodsfield | 43793 |  | Monroe | P007 | 1680 Hp. natural gas rich burn compressor engine - Waukesha L7044GSI | 2016-03-18 | C-7(Catalytic Converter): Engine #7Catalyst | E2 Energy Services | 1680 hp | 0.22 lb/hr | 1535 hp | 0.07 lb/hr | 6348 03 | VOC - Volatile Organic Compounds | PP | Y | NA
2016 | 1578 | 0656105005 | E2 Appalachian Compression LLC - Reusser | Twp Hwy 68 and Twp Hwy 66 | Woodsfield | 43793 |  | Monroe | P008 | 1680 Hp. natural gas rich burn compressor engine - Waukesha L7044GSI | 2016-03-11 | C-7(Catalytic Converter): Engine #7Catalyst | E2 Energy Services | 1680 hp | 0.22 lb/hr | 1548 hp | 0.06 lb/hr | 6348 03 | VOC - Volatile Organic Compounds | PP | Y | NA
2016 | 1599 | 0656105005 | E2 Appalachian Compression LLC - Reusser | Twp Hwy 68 and Twp Hwy 66 | Woodsfield | 43793 |  | Monroe | P001 | 1680 Hp. natural gas rich burn compressor engine - Waukesha L7044GSI | 2016-07-14 | C-1(Catalytic Converter): Engine Catalyst; C-2(Catalytic Converter): Engine Catalyst; C-3(Catalytic Converter): Engine #3 Catalyst; C-4(Catalytic Converter): Engine #4 Catalyst; C-5(Catalytic Converter): Engine #5 Catalyst; C-6(Catalytic Converter): Engin | Alliance Source Testing | 1680 hp | 0.22 lb/hr | 1646 hp | 0.05 lb/hr | 25A | VOC - Volatile Organic Compounds | PP | Y | NA
2016 | 1600 | 0656105005 | E2 Appalachian Compression LLC - Reusser | Twp Hwy 68 and Twp Hwy 66 | Woodsfield | 43793 |  | Monroe | P002 | 1680 Hp. natural gas rich burn compressor engine - Waukesha L7044GSI | 2016-07-14 | C-1(Catalytic Converter): Engine Catalyst; C-2(Catalytic Converter): Engine Catalyst; C-3(Catalytic Converter): Engine #3 Catalyst; C-4(Catalytic Converter): Engine #4 Catalyst; C-5(Catalytic Converter): Engine #5 Catalyst; C-6(Catalytic Converter): Engin | Alliance Source Testing | 1680 hp | 0.22 lb/hr | 1457 hp | 0.01 lb/hr | 25A | VOC - Volatile Organic Compounds | PP | Y | NA
2016 | 1601 | 0661005008 | Seneca Gas Plant | Zep Road | Summerfield | 43788 |  | Noble | P001 | Compressor Engine #1 - Natural gas-fired four-stroke lean burn (4SLB) internal combustion engine rated at an operating capacity of 4,735 horsepower (hp) and equipped with an oxidation catalyst. | 2016-03-17 | CC001(Catalytic Converter): Compressor Engine #1 - Catalyic Convertor; CC002(Catalytic Converter): Compressor Engine #2 - Catalytic Convertor | Air Hygiene International, Inc | 4735 hp | 0.16 g/hp-hr | 4182 hp | 0.04 g/hp-hr | 25A | VOC - Volatile Organic Compounds | PP | Y | NA
2016 | 1602 | 0661005008 | Seneca Gas Plant | Zep Road | Summerfield | 43788 |  | Noble | P002 | Compressor Engine #2 - Natural gas-fired four-stroke lean burn (4SLB) internal combustion engine rated at an operating capacity of 4,735 horsepower (hp) and equipped with an oxidation catalyst. | 2016-03-17 | CC001(Catalytic Converter): Compressor Engine #1 - Catalyic Convertor; CC002(Catalytic Converter): Compressor Engine #2 - Catalytic Convertor | Air Hygiene International, Inc | 4735 hp | 0.16 g/hp-hr | 4187 hp | 0.04 g/hp-hr | 25A | VOC - Volatile Organic Compounds | PP | Y | NA
2016 | 1607 | 0661005010 | E2 Appalachian Compression LLC - Upper Hill | Opossum Run Rd and Town Hwy 120 | Sarahsville | 43779 |  | Noble | P003 | 1,680 Hp. Waukesha (L7044GSI) natural gas-fired, rich burn, turbocharged, with oxidation catalyst, compressor engine. | 2016-04-29 | C-3(Catalytic Converter): Engine Catalyst; C-9(Catalytic Converter): Engine Catalyst | Alliance Source Testing | 1680 hp | 1.0 g/hp-hr | 1658 hp | 0.01 g/hp-hr | 25A | VOC - Volatile Organic Compounds | PP | Y | NA
2016 | 1608 | 0661005010 | E2 Appalachian Compression LLC - Upper Hill | Opossum Run Rd and Town Hwy 120 | Sarahsville | 43779 |  | Noble | P009 | 1,680 Hp. Waukesha (L7044GSI) natural gas-fired, rich burn, turbocharged, with oxidation catalyst, compressor engine. | 2016-04-29 | C-3(Catalytic Converter): Engine Catalyst; C-9(Catalytic Converter): Engine Catalyst | Alliance Source Testing | 1680 hp | 1.0 g/hp-hr | 1646 hp | 0.02 g/hp-hr | 25A | VOC - Volatile Organic Compounds | PP | Y | NA
2016 | 1613 | 0661005010 | E2 Appalachian Compression LLC - Upper Hill | Opossum Run Rd and Town Hwy 120 | Sarahsville | 43779 |  | Noble | P007 | 1,680 Hp. Waukesha (L7044GSI) natural gas-fired, rich burn, turbocharged, with oxidation catalyst, compressor engine. | 2016-03-17 | C-7(Catalytic Converter): Engine Catalyst; C-8(Catalytic Converter): Engine Catalyst | Alliance Source Testing | 1680 hp | 1.0 g/hp-hr | 1464 hp | 0.02 g/hp-hr | 25A | VOC - Volatile Organic Compounds | PP | Y | NA
2016 | 1614 | 0661005010 | E2 Appalachian Compression LLC - Upper Hill | Opossum Run Rd and Town Hwy 120 | Sarahsville | 43779 |  | Noble | P008 | 1,680 Hp. Waukesha (L7044GSI) natural gas-fired, rich burn, turbocharged, with oxidation catalyst, compressor engine. | 2016-03-17 | C-7(Catalytic Converter): Engine Catalyst; C-8(Catalytic Converter): Engine Catalyst | Alliance Source Testing | 1680 hp | 1.0 g/hp-hr | 1406 hp | 0.02 g/hp-hr | 25A | VOC - Volatile Organic Compounds | PP | Y | NA
2016 | 1617 | 0661005010 | E2 Appalachian Compression LLC - Upper Hill | Opossum Run Rd and Town Hwy 120 | Sarahsville | 43779 |  | Noble | P003 | 1,680 Hp. Waukesha (L7044GSI) natural gas-fired, rich burn, turbocharged, with oxidation catalyst, compressor engine. | 2016-04-29 | C-3(Catalytic Converter): Engine Catalyst; C-9(Catalytic Converter): Engine Catalyst | Ecotest Energy Services | 1680 hp | 1.0 g/hp-hr | 1658 hp | 0.01 g/hp-hr | 6348 03 | VOC - Volatile Organic Compounds | PP | Y | NA
2016 | 1618 | 0661005010 | E2 Appalachian Compression LLC - Upper Hill | Opossum Run Rd and Town Hwy 120 | Sarahsville | 43779 |  | Noble | P009 | 1,680 Hp. Waukesha (L7044GSI) natural gas-fired, rich burn, turbocharged, with oxidation catalyst, compressor engine. | 2016-04-29 | C-3(Catalytic Converter): Engine Catalyst; C-9(Catalytic Converter): Engine Catalyst | Ecotest Energy Services | 1680 hp | 1.0 g/hp-hr | 1646 hp | 0.02 g/hp-hr | 6348 03 | VOC - Volatile Organic Compounds | PP | Y | NA
2016 | 1625 | 0661005010 | E2 Appalachian Compression LLC - Upper Hill | Opossum Run Rd and Town Hwy 120 | Sarahsville | 43779 |  | Noble | P002 | 1,680 Hp. Waukesha (L7044GSI) natural gas-fired, rich burn, turbocharged, with oxidation catalyst, compressor engine. | 2016-07-13 | C-2(Catalytic Converter): Engine Catalyst; C-8(Catalytic Converter): Engine Catalyst | Alliance Source Testing | 1,680 hp | 86 ppm | 1,529 hp | 1.1 ppm | 25A | VOC - Volatile Organic Compounds | PP | Y | NA
2016 | 1626 | 0661005010 | E2 Appalachian Compression LLC - Upper Hill | Opossum Run Rd and Town Hwy 120 | Sarahsville | 43779 |  | Noble | P008 | 1,680 Hp. Waukesha (L7044GSI) natural gas-fired, rich burn, turbocharged, with oxidation catalyst, compressor engine. | 2016-07-13 | C-2(Catalytic Converter): Engine Catalyst; C-8(Catalytic Converter): Engine Catalyst | Alliance Source Testing | 1,680 hp | 86 ppm | 1,518 hp | 1.1 ppm | 25A | VOC - Volatile Organic Compounds | PP | Y | NA
2016 | 1628 | 0661005027 | E2 Appalachian LLC - Batesville | 58380 St John Rd | Quaker City | 43773 |  | Noble | P001 | 1,680 Hp. Waukesha (L7044GSI) natural gas-fired, rich burn, turbocharged, with oxidation catalyst, compressor engine | 2016-04-13 | C2701C(Catalytic Converter): Engine Catalyst | E2 Appalachian | 1680 hp | 0.7 g/hp-hr | 1539 hp | 0.023 g/hp-hr | 6348 03 | VOC - Volatile Organic Compounds | PP | Y | NA
2016 | 1632 | 0661005027 | E2 Appalachian LLC - Batesville | 58380 St John Rd | Quaker City | 43773 |  | Noble | P002 | 1,680 Hp. Waukesha (L7044GSI) natural gas-fired, rich burn, turbocharged, with oxidation catalyst, compressor engine | 2016-03-24 | C2702C(Catalytic Converter): Engine Catalyst | E2 Appalachian | 1680 hp | 0.7 g/hp-hr | 1473 hp | 0.0225 g/hp-hr | 6348 03 | VOC - Volatile Organic Compounds | PP | Y | NA
2016 | 1633 | 0661005027 | E2 Appalachian LLC - Batesville | 58380 St John Rd | Quaker City | 43773 |  | Noble | P003 | 1,680 Hp. Waukesha (L7044GSI) natural gas-fired, rich burn, turbocharged, with oxidation catalyst, compressor engine | 2016-03-23 | C2703C(Catalytic Converter): Engine Catalyst | E2 Appalachian | 1680 hp | 0.7 g/hp-hr | 1348 hp | 0.0174 g/hp-hr | 6348 03 | VOC - Volatile Organic Compounds | PP | Y | NA
2016 | 1637 | 0661005027 | E2 Appalachian LLC - Batesville | 58380 St John Rd | Quaker City | 43773 |  | Noble | P004 | 1,680 Hp. Waukesha (L7044GSI) natural gas-fired, rich burn, turbocharged, with oxidation catalyst, compressor engine | 2016-03-30 | C2704C(Catalytic Converter): Engine Catalyst | E2 Appalachian | 1680 hp | 0.7 g/hp-hr | 1470 hp | 0.0180 g/hp-hr | 6348 03 | VOC - Volatile Organic Compounds | PP | Y | NA
2016 | 1641 | 0661005027 | E2 Appalachian LLC - Batesville | 58380 St John Rd | Quaker City | 43773 |  | Noble | P005 | 1,680 Hp. Waukesha (L7044GSI) natural gas-fired, rich burn, turbocharged, with oxidation catalyst, compressor engine | 2016-03-31 | C2705C(Catalytic Converter): Engine Catalyst | E2 Appalachian | 1680 hp | 0.7 g/hp-hr | 1425 hp | 0.0189 g/hp-hr | 6348 03 | VOC - Volatile Organic Compounds | PP | Y | NA
2016 | 1642 | 0661005027 | E2 Appalachian LLC - Batesville | 58380 St John Rd | Quaker City | 43773 |  | Noble | P006 | 1,680 Hp. Waukesha (L7044GSI) natural gas-fired, rich burn, turbocharged, with oxidation catalyst, compressor engine | 2016-04-01 | C2705C(Catalytic Converter): Engine Catalyst | E2 Appalachian | 1680 hp | 0.06 g/hp-hr | 1551 hp | 0.0077 g/hp-hr | 6348 03 | VOC - Volatile Organic Compounds | PP | Y | NA
2016 | 1647 | 0661005027 | E2 Appalachian LLC - Batesville | 58380 St John Rd | Quaker City | 43773 |  | Noble | P008 | 1,680 Hp. Waukesha (L7044GSI) natural gas-fired, rich burn, turbocharged, with oxidation catalyst, compressor engine | 2016-04-14 | C2708C(Catalytic Converter): Engine Catalyst | E2 Appalachian | 1680 hp | 0.7 g/hp-hr | 1475 hp | 0.0222 g/hp-hr | 6348 03 | VOC - Volatile Organic Compounds | PP | Y | NA
2016 | 1648 | 0661005027 | E2 Appalachian LLC - Batesville | 58380 St John Rd | Quaker City | 43773 |  | Noble | P002 | 1,680 Hp. Waukesha (L7044GSI) natural gas-fired, rich burn, turbocharged, with oxidation catalyst, compressor engine | 2016-04-14 | C2702C(Catalytic Converter): Engine Catalyst | E2 Energy Services | 1680 hp | 0.7 g/hp-hr | 1473 hp | 0.02 g/hp-hr | 6348 03 | VOC - Volatile Organic Compounds | PP | N | NA
2016 | 1653 | 0661005027 | E2 Appalachian LLC - Batesville | 58380 St John Rd | Quaker City | 43773 |  | Noble | P002 | 1,680 Hp. Waukesha (L7044GSI) natural gas-fired, rich burn, turbocharged, with oxidation catalyst, compressor engine | 2016-04-28 | C2702C(Catalytic Converter): Engine Catalyst | Alliance Source Testing | 1680 hp | 0.7 g/hp-hr | 1529 hp | 0.01 g/hp-hr | 25A | VOC - Volatile Organic Compounds | PP | N | NA
2016 | 1660 | 0661005027 | E2 Appalachian LLC - Batesville | 58380 St John Rd | Quaker City | 43773 |  | Noble | P001 | 1,680 Hp. Waukesha (L7044GSI) natural gas-fired, rich burn, turbocharged, with oxidation catalyst, compressor engine | 2016-07-11 | C2701C(Catalytic Converter): Engine Catalyst; C2707C(Catalytic Converter): Engine Catalyst; C2708C(Catalytic Converter): Engine Catalyst | Alliance Source Testing | 1,680 hp | 0.7 g/hp-hr | 1,529 hp | 0.01 g/hp-hr | 25A | VOC - Volatile Organic Compounds | PP | Y | NA
2016 | 1661 | 0661005027 | E2 Appalachian LLC - Batesville | 58380 St John Rd | Quaker City | 43773 |  | Noble | P007 | 1,680 Hp. Waukesha (L7044GSI) natural gas-fired, rich burn, turbocharged, with oxidation catalyst, compressor engine | 2016-07-11 | C2701C(Catalytic Converter): Engine Catalyst; C2707C(Catalytic Converter): Engine Catalyst; C2708C(Catalytic Converter): Engine Catalyst | Alliance Source Testing | 1,680 hp | 0.7 g/hp-hr | 1,607 hp | 0.03 g/hp-hr | 25A | VOC - Volatile Organic Compounds | PP | Y | NA
2016 | 1662 | 0661005027 | E2 Appalachian LLC - Batesville | 58380 St John Rd | Quaker City | 43773 |  | Noble | P008 | 1,680 Hp. Waukesha (L7044GSI) natural gas-fired, rich burn, turbocharged, with oxidation catalyst, compressor engine | 2016-07-11 | C2701C(Catalytic Converter): Engine Catalyst; C2707C(Catalytic Converter): Engine Catalyst; C2708C(Catalytic Converter): Engine Catalyst | Alliance Source Testing | 1,680 hp | 0.7 g/hp-hr | 1,568 hp | 0.01 g/hp-hr | 25A | VOC - Volatile Organic Compounds | PP | Y | NA
2016 | 1665 | 0661005027 | E2 Appalachian LLC - Batesville | 58380 St John Rd | Quaker City | 43773 |  | Noble | P006 | 1,680 Hp. Waukesha (L7044GSI) natural gas-fired, rich burn, turbocharged, with oxidation catalyst, compressor engine | 2016-07-12 | C2706C(Catalytic Converter): Engine Catalyst | Alliance Source Testing | 1,680 hp | 0.06 g/hp-hr | 1,490 hp | 0.01 g/hp-hr | 25A | VOC - Volatile Organic Compounds | PP | Y | NA
2016 | 1684 | 0661005040 | Crum Compressor Station | 52934 Town Highway 192 | Seneca Twp. | 43780 |  | Noble | P001 | One (1) Waukesha 7044GSI 1,680 hp compressor engine fitted with a 5-element non-selective catalytic reduction catalyst. | 2016-08-31 | C-1(Catalytic Converter): 5-element NSCR for compressor engine C-100; C-2(Catalytic Converter): 5-element NSCR for compressor engine C-200; C-3(Catalytic Converter): 5-element NSCR for compressor engine C-300; C-4(Catalytic Converter): 5-element NSCR for | Alliance Source Testing | 1680 hp | 0.7 g/hp-hr | 1568 hp | 0.02 g/hp-hr | 25A | VOC - Volatile Organic Compounds | PP | Y | NA
2016 | 1685 | 0661005040 | Crum Compressor Station | 52934 Town Highway 192 | Seneca Twp. | 43780 |  | Noble | P002 | One (1) Waukesha 7044GSI 1,680 hp compressor engine fitted with a 5-element non-selective catalytic reduction catalyst. | 2016-08-31 | C-1(Catalytic Converter): 5-element NSCR for compressor engine C-100; C-2(Catalytic Converter): 5-element NSCR for compressor engine C-200; C-3(Catalytic Converter): 5-element NSCR for compressor engine C-300; C-4(Catalytic Converter): 5-element NSCR for | Alliance Source Testing | 1680 hp | 0.7 g/hp-hr | 1584 hp | 0.01 g/hp-hr | 25A | VOC - Volatile Organic Compounds | PP | Y | NA
2016 | 1686 | 0661005040 | Crum Compressor Station | 52934 Town Highway 192 | Seneca Twp. | 43780 |  | Noble | P003 | One (1) Waukesha 7044GSI 1,680 hp compressor engine fitted with a 5-element non-selective catalytic reduction catalyst. | 2016-08-31 | C-1(Catalytic Converter): 5-element NSCR for compressor engine C-100; C-2(Catalytic Converter): 5-element NSCR for compressor engine C-200; C-3(Catalytic Converter): 5-element NSCR for compressor engine C-300; C-4(Catalytic Converter): 5-element NSCR for | Alliance Source Testing | 1680 hp | 0.7 g/hp-hr | 1558 hp | 0.007 g/hp-hr | 25A | VOC - Volatile Organic Compounds | PP | Y | NA
2016 | 1687 | 0661005040 | Crum Compressor Station | 52934 Town Highway 192 | Seneca Twp. | 43780 |  | Noble | P004 | One (1) Waukesha 7044GSI 1,680 hp compressor engine fitted with a 5-element non-selective catalytic reduction catalyst. | 2016-08-31 | C-1(Catalytic Converter): 5-element NSCR for compressor engine C-100; C-2(Catalytic Converter): 5-element NSCR for compressor engine C-200; C-3(Catalytic Converter): 5-element NSCR for compressor engine C-300; C-4(Catalytic Converter): 5-element NSCR for | Alliance Source Testing | 1680 hp | 0.7 g/hp-hr | 1563 hp | 0.007 g/hp-hr | 25A | VOC - Volatile Organic Compounds | PP | Y | NA
2016 | 1688 | 0661005040 | Crum Compressor Station | 52934 Town Highway 192 | Seneca Twp. | 43780 |  | Noble | P005 | One (1) Waukesha 7044GSI 1,680 hp compressor engine fitted with a 5-element non-selective catalytic reduction catalyst. | 2016-08-31 | C-1(Catalytic Converter): 5-element NSCR for compressor engine C-100; C-2(Catalytic Converter): 5-element NSCR for compressor engine C-200; C-3(Catalytic Converter): 5-element NSCR for compressor engine C-300; C-4(Catalytic Converter): 5-element NSCR for | Alliance Source Testing | 1680 hp | 0.7 g/hp-hr | 1503 hp | 0.005 g/hp-hr | 25A | VOC - Volatile Organic Compounds | PP | Y | NA
2016 | 1689 | 0661005040 | Crum Compressor Station | 52934 Town Highway 192 | Seneca Twp. | 43780 |  | Noble | P006 | One (1) Waukesha 7044GSI 1,680 hp compressor engine fitted with a 5-element non-selective catalytic reduction catalyst. | 2016-08-31 | C-1(Catalytic Converter): 5-element NSCR for compressor engine C-100; C-2(Catalytic Converter): 5-element NSCR for compressor engine C-200; C-3(Catalytic Converter): 5-element NSCR for compressor engine C-300; C-4(Catalytic Converter): 5-element NSCR for | Alliance Source Testing | 1680 hp | 0.7 g/hp-hr | 1533 hp | 0.01 g/hp-hr | 25A | VOC - Volatile Organic Compounds | PP | Y | NA
2016 | 1690 | 0661005040 | Crum Compressor Station | 52934 Town Highway 192 | Seneca Twp. | 43780 |  | Noble | P007 | One (1) Waukesha 7044GSI 1,680 hp compressor engine fitted with a 5-element non-selective catalytic reduction catalyst. | 2016-08-31 | C-1(Catalytic Converter): 5-element NSCR for compressor engine C-100; C-2(Catalytic Converter): 5-element NSCR for compressor engine C-200; C-3(Catalytic Converter): 5-element NSCR for compressor engine C-300; C-4(Catalytic Converter): 5-element NSCR for | Alliance Source Testing | 1680 hp | 0.7 g/hp-hr | 1330 hp | 0.004 g/hp-hr | 25A | VOC - Volatile Organic Compounds | PP | Y | NA
2016 | 1691 | 0661005040 | Crum Compressor Station | 52934 Town Highway 192 | Seneca Twp. | 43780 |  | Noble | P008 | One (1) Waukesha 7044GSI 1,680 hp compressor engine fitted with a 5-element non-selective catalytic reduction catalyst. | 2016-08-31 | C-1(Catalytic Converter): 5-element NSCR for compressor engine C-100; C-2(Catalytic Converter): 5-element NSCR for compressor engine C-200; C-3(Catalytic Converter): 5-element NSCR for compressor engine C-300; C-4(Catalytic Converter): 5-element NSCR for | Alliance Source Testing | 1680 hp | 0.7 g/hp-hr | 1451 hp | 0.004 g/hp-hr | 25A | VOC - Volatile Organic Compounds | PP | Y | NA
2016 | 1692 | 0661005040 | Crum Compressor Station | 52934 Town Highway 192 | Seneca Twp. | 43780 |  | Noble | P009 | One (1) Waukesha 7044GSI 1,680 hp compressor engine fitted with a 5-element non-selective catalytic reduction catalyst. | 2016-08-31 | C-1(Catalytic Converter): 5-element NSCR for compressor engine C-100; C-2(Catalytic Converter): 5-element NSCR for compressor engine C-200; C-3(Catalytic Converter): 5-element NSCR for compressor engine C-300; C-4(Catalytic Converter): 5-element NSCR for | Alliance Source Testing | 1680 hp | 0.7 g/hp-hr | 1430 hp | 0.01 g/hp-hr | 25A | VOC - Volatile Organic Compounds | PP | Y | NA
2016 | 1693 | 0661005042 | CNX Gas LLC., Noble 19 | 51109 Lew Martin Rd | Summerfield | 43778 |  | Noble | P002 | One or multiple stationary natural gas-fired spark ignition (SI) internal combustion engines (ICE) with a combined total horsepower of 1,800 HP for the site. Includes 2007 or later model year engines manufactured after the applicable effective date iden | 2016-05-17 | catalyst | Ecotest Energy Services | 380 hp 84 hp | 1.0 g/hp-hr | 165 hp 55 hp | 0.57 g/hp-hr | 6348 03 | VOC - Volatile Organic Compounds | PP | Y | NA | 380 hp flash gas unit and 84 hp VRU compressor engine-P002 allowable combined and results combined
2016 | 1696 | 0661005052 | Long Compressor Station | 55135 Batesville Rd | Quaker City | 43773 |  | Noble | P001 | 1,680 hp Waukesha 7044GSI NG Fired-rich burn-4stroke compressor engine | 2016-01-28 | C-01(Catalytic Converter): Non-selective catalyst reduction device for C-2000; C-02(Catalytic Converter): Non-selective catalyst reduction device for C-2100; C-03(Catalytic Converter): Non-selective catalyst reduction device for C-2200; C-04(Catalytic Con | Technical Compliance Solutions | 1680 hp | 0.07 g/hp-hr | 1628 hp | 0.004 g/hp-hr | 320 | VOC - Volatile Organic Compounds | PP | Y | NA
2016 | 1700 | 0661005052 | Long Compressor Station | 55135 Batesville Rd | Quaker City | 43773 |  | Noble | P002 | 1,680 hp Waukesha 7044GSI NG Fired-rich burn-4stroke compressor engine | 2016-01-28 | C-01(Catalytic Converter): Non-selective catalyst reduction device for C-2000; C-02(Catalytic Converter): Non-selective catalyst reduction device for C-2100; C-03(Catalytic Converter): Non-selective catalyst reduction device for C-2200; C-04(Catalytic Con | Technical Compliance Solutions | 1680 hp | 0.07 g/hp-hr | 1610 hp | 0.02 g/hp-hr | 320 | VOC - Volatile Organic Compounds | PP | Y | NA
2016 | 1704 | 0661005052 | Long Compressor Station | 55135 Batesville Rd | Quaker City | 43773 |  | Noble | P003 | 1,680 hp Waukesha 7044GSI NG Fired-rich burn-4stroke compressor engine | 2016-01-28 | C-01(Catalytic Converter): Non-selective catalyst reduction device for C-2000; C-02(Catalytic Converter): Non-selective catalyst reduction device for C-2100; C-03(Catalytic Converter): Non-selective catalyst reduction device for C-2200; C-04(Catalytic Con | Technical Compliance Solutions | 1680 hp | 0.07 g/hp-hr | 1606 hp | 0.002 g/hp-hr | 320 | VOC - Volatile Organic Compounds | PP | Y | NA
2016 | 1707 | 0661005052 | Long Compressor Station | 55135 Batesville Rd | Quaker City | 43773 |  | Noble | P004 | 1,680 hp Waukesha 7044GSI NG Fired-rich burn-4stroke compressor engine | 2016-01-28 | C-01(Catalytic Converter): Non-selective catalyst reduction device for C-2000; C-02(Catalytic Converter): Non-selective catalyst reduction device for C-2100; C-03(Catalytic Converter): Non-selective catalyst reduction device for C-2200; C-04(Catalytic Con | Technical Compliance Solutions | 1680 hp | 0.07 g/hp-hr | 1627 hp | 0.03 g/hp-hr | 320 | VOC - Volatile Organic Compounds | PP | Y | NA
2016 | 1709 | 0661005052 | Long Compressor Station | 55135 Batesville Rd | Quaker City | 43773 |  | Noble | P005 | 1,680 hp Waukesha 7044GSI NG Fired-rich burn-4stroke compressor engine | 2016-01-28 | C-01(Catalytic Converter): Non-selective catalyst reduction device for C-2000; C-02(Catalytic Converter): Non-selective catalyst reduction device for C-2100; C-03(Catalytic Converter): Non-selective catalyst reduction device for C-2200; C-04(Catalytic Con | Technical Compliance Solutions | 1680 hp | 0.07 g/hp-hr | 1628 hp | 0.002 g/hp-hr | 320 | VOC - Volatile Organic Compounds | PP | Y | NA
2016 | 1711 | 0661005052 | Long Compressor Station | 55135 Batesville Rd | Quaker City | 43773 |  | Noble | P006 | 1,680 hp Waukesha 7044GSI NG Fired-rich burn-4stroke compressor engine | 2016-01-28 | C-01(Catalytic Converter): Non-selective catalyst reduction device for C-2000; C-02(Catalytic Converter): Non-selective catalyst reduction device for C-2100; C-03(Catalytic Converter): Non-selective catalyst reduction device for C-2200; C-04(Catalytic Con | Technical Compliance Solutions | 1680 hp | 0.07 g/hp-hr | 1623 hp | 0.02 g/hp-hr | 320 | VOC - Volatile Organic Compounds | PP | Y | NA
2016 | 1716 | 0661005052 | Long Compressor Station | 55135 Batesville Rd | Quaker City | 43773 |  | Noble | P007 | 1,680 hp Waukesha 7044GSI NG Fired-rich burn-4stroke compressor engine | 2016-01-28 | C-01(Catalytic Converter): Non-selective catalyst reduction device for C-2000; C-02(Catalytic Converter): Non-selective catalyst reduction device for C-2100; C-03(Catalytic Converter): Non-selective catalyst reduction device for C-2200; C-04(Catalytic Con | Technical Compliance Solutions | 1680 hp | 0.07 g/hp-hr | 1616 hp | 0.003 g/hp-hr | 320 | VOC - Volatile Organic Compounds | PP | Y | NA
2016 | 1717 | 0661005052 | Long Compressor Station | 55135 Batesville Rd | Quaker City | 43773 |  | Noble | P008 | 1,680 hp Waukesha 7044GSI NG Fired-rich burn-4stroke compressor engine | 2016-01-28 | C-01(Catalytic Converter): Non-selective catalyst reduction device for C-2000; C-02(Catalytic Converter): Non-selective catalyst reduction device for C-2100; C-03(Catalytic Converter): Non-selective catalyst reduction device for C-2200; C-04(Catalytic Con | Technical Compliance Solutions | 1680 hp | 0.07 g/hp-hr | 1544 hp | 0.01 g/hp-hr | 320 | VOC - Volatile Organic Compounds | PP | Y | NA
2016 | 1963 | 0857103154 | PINNACLE GAS PRODUCERS LLC | 4220 PINNACLE RD | MORAINE | 45439 |  | Montgomery | B003 | Natural Gas Fired Compressor Engine, 12 MMBtu/hour nominal heat input | 2016-02-24 | N/A | DTE Energy | 12MMBtu/hr heat input | 86ppmvd@15%O2 | 867 RPM | 18ppmvd@15%O2 | 25A | Total Hydrocarbons | PP | Y | NA | RAPCA calculation of NMOC differed from report but still below permit allowable. Fuel content averaged 984 BTU/scf. Combustion temperature averaged 1503 degrees Fahrenheit.
2015 | 338 | 0238000187 | Trailway Wood II | 2261 County Rd 168 | Dundee | 44624 |  | Holmes | B004 | 4SLB Stationary RICE Natural Gas Engine #1 | 2015-04-16 | Engineered to meet the standard | Custom Stack Analysis | 452.8 Kw | 60 ppm @ 15% O2 | 188.6 Kw | 60.51 ppm @ 15% O2 | 25A | VOC - Volatile Organic Compounds | FF | NA | Y | Operated at only 41.78 % of load. . A retest has been requested and is in the works as of 6/5/15 | Yes
2016 | 536 | 0238000191 | H W CHAIR, LTD | 6291 COUNTY ROAD 77 | MILLERSBURG | 44654 |  | Holmes | B002 | 738 hp (550 kW) 4SRB natural gas engine controlled by a NSCR and AFR to power facility: Waukesha F3521GSI | 2016-06-01 | CCWEG2(Catalytic Converter): catalyst | Custom Stack Analysis | 550 Kw | 60 ppm @ 15% O2 or 0.7 g/hp-hr | 354.83 KW | 2.68 ppm @ 15% O2 or 0.03 g/hp-hr | 25A | VOC - Volatile Organic Compounds | PP | Y | NA |  | Yes
2013 | 154 | 0210012004 | Augusta Compressor Facility- Utica Gas Services, L.L.C. | 8034 Bane Rd NE | East Twp. | 44427 |  | Carroll | P014 | 605-hp Baldor IGLC420-2N Engine Driven Emergency Generator | 2013-10-08 | Oxid. Cat. 3(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 4(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 5(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 6(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 7(Catalytic Converter): | Alliance Source Testing | 605 Hp | 0.93 lbs/hr, 1.0 g/hp/hr, 86ppmvd@15%O2 | 551 Hp or 91% of Max | 0.1 lbs/hr, 0.02 g/hp/hr, 1.4ppmvd@15%O2 | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y
2013 | 156 | 0210012004 | Augusta Compressor Facility- Utica Gas Services, L.L.C. | 8034 Bane Rd NE | East Twp. | 44427 |  | Carroll | P015 | 605-hp Baldor IGLC420-2N Engine Driven Emergency Generator | 2013-10-08 | Oxid. Cat. 3(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 4(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 5(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 6(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 7(Catalytic Converter): | Alliance Source Testing | 605 Hp | 0.93 lbs/hr, 1.0 g/hp/hr, 86ppmvd@15%O2 | 551 Hp or 91% of Max | 0.02 lbs/hr, 0.01 g/hp/hr, 1.1ppmvd@15%O2 | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y
2014 | 1930 | 0634005058 | Atlas Noble, LLC - Cramblett Well Pad | Bowers Road | North Twp. | 43988 |  | Harrison | P003 | NA - One or multiple stationary diesel-fired compression ignition (CI) (diesel) internal combustion engines (ICE), certified to meet the Tier 3 emission standards for diesel engines, with a combined total horsepower (HP) of no more than 250 HP for the site . | 2014-03-04 | none | Air Compliance Consultants | 68 hp | 86 ppm | 33 hp | 2.9 ppm | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y | VRU engine 2- 68 hp caterpillar engine
2013 | 291 | 0210012004 | Augusta Compressor Facility- Utica Gas Services, L.L.C. | 8034 Bane Rd NE | East Twp. | 44427 |  | Carroll | P014 | 605-hp Baldor IGLC420-2N Engine Driven Emergency Generator | 2013-10-09 | Oxid. Cat. 3(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 4(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 5(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 6(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 7(Catalytic Converter): | Alliance Source Testing | 605 Hp | 0.93 lbs/hr, 1.0 g/hp/hr, 86ppmvd@15%O2 | 551 Hp or 91% of Max | 0.1 lbs/hr, 0.02 g/hp/hr, 1.4ppmvd@15%O2 | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y
2013 | 292 | 0210012004 | Augusta Compressor Facility- Utica Gas Services, L.L.C. | 8034 Bane Rd NE | East Twp. | 44427 |  | Carroll | P015 | 605-hp Baldor IGLC420-2N Engine Driven Emergency Generator | 2013-10-09 | Oxid. Cat. 3(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 4(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 5(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 6(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 7(Catalytic Converter): | Alliance Source Testing | 605 Hp | 0.93 lbs/hr, 1.0 g/hp/hr, 86ppmvd@15%O2 | 551 Hp or 91% of Max | 0.02 lbs/hr, 0.01 g/hp/hr, 1.1ppmvd@15%O2 | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y
2013 | 321 | 0210012004 | Augusta Compressor Facility- Utica Gas Services, L.L.C. | 8034 Bane Rd NE | East Twp. | 44427 |  | Carroll | P014 | 605-hp Baldor IGLC420-2N Engine Driven Emergency Generator | 2013-10-10 | Oxid. Cat. 3(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 4(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 5(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 6(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 7(Catalytic Converter): | Alliance Source Testing | 605 Hp | 0.93 lbs/hr, 1.0 g/hp/hr, 86ppmvd@15%O2 | 551 Hp or 91% of Max | 0.1 lbs/hr, 0.02 g/hp/hr, 1.4ppmvd@15%O2 | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y
2013 | 322 | 0210012004 | Augusta Compressor Facility- Utica Gas Services, L.L.C. | 8034 Bane Rd NE | East Twp. | 44427 |  | Carroll | P015 | 605-hp Baldor IGLC420-2N Engine Driven Emergency Generator | 2013-10-10 | Oxid. Cat. 3(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 4(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 5(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 6(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 7(Catalytic Converter): | Alliance Source Testing | 605 Hp | 0.93 lbs/hr, 1.0 g/hp/hr, 86ppmvd@15%O2 | 551 Hp or 91% of Max | 0.02 lbs/hr, 0.01 g/hp/hr, 1.1ppmvd@15%O2 | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y
2011 | 778 | 0664000056 | Waste Management of Ohio (Suburban South Recycling) | 3415 Township Road 447 | Glenford | 43739 |  | Perry | P004 | 1148 HP CAT 3516 Reciprocating LFG Engine | 2011-05-24 | NA | Custom Statck Analysis , LLC | 1148 Hp/ 800 Kw | 1.0 grams/hp-hr | 1148 grams/hr-hr/812 Kw | 0.22 grams/hp-hr | 25A | Total Hydrocarbons | PASS | NA | Y |  | Yes
2011 | 781 | 0664000056 | Waste Management of Ohio (Suburban South Recycling) | 3415 Township Road 447 | Glenford | 43739 |  | Perry | P006 | 1148 HP CAT 3516 Reciprocating LFG Engine | 2011-05-25 | NA | Custom Statck Analysis , LLC | 1148 Hp/ 800 Kw | 1.0 grams/hp-hr | 1148 grams/hr-hr/815 Kw | 0.18 grams/hp-hr | 25A | Total Hydrocarbons | PASS | NA | Y |  | Yes
2011 | 787 | 0664000056 | Waste Management of Ohio (Suburban South Recycling) | 3415 Township Road 447 | Glenford | 43739 |  | Perry | P003 | 1148 HP CAT 3516 Reciprocating LFG Engine | 2011-05-26 | NA | Custom Statck Analysis , LLC | 1148 Hp/ 800 Kw | 1.0 grams/hp-hr | 1148 grams/hr-hr | 0.20 grams/hp-hr | 25A | Total Hydrocarbons | PASS | NA | Y |  | Yes
2011 | 790 | 0664000056 | Waste Management of Ohio (Suburban South Recycling) | 3415 Township Road 447 | Glenford | 43739 |  | Perry | P007 | 1148 HP CAT 3516 Reciprocating LFG Engine | 2011-05-26 | NA | Custom Statck Analysis , LLC | 1148 Hp/ 800 Kw | 1.0 grams/hp-hr | 1148 grams/hr-hr/811 Kw | 0.22 grams/hp-hr | 25A | Total Hydrocarbons | PASS | NA | Y |  | Yes
2011 | 793 | 0664000056 | Waste Management of Ohio (Suburban South Recycling) | 3415 Township Road 447 | Glenford | 43739 |  | Perry | P008 | 1148 HP CAT 3516 Reciprocating LFG Engine | 2011-05-26 | NA | Custom Statck Analysis , LLC | 1148 Hp/ 800 Kw | 1.0 grams/hp-hr | 1148 grams/hr-hr/810 Kw | 0.24 grams/hp-hr | 25A | Total Hydrocarbons | PASS | NA | Y |  | Yes
2011 | 796 | 0664000056 | Waste Management of Ohio (Suburban South Recycling) | 3415 Township Road 447 | Glenford | 43739 |  | Perry | P002 | 1148 HP CAT 3516 Reciprocating LFG Engine | 2011-06-01 | NA | Custom Statck Analysis , LLC | 1148 Hp/ 800 Kw | 1.0 grams/hp-hr | 1148 grams/hr-hr | 0.24 grams/hp-hr | 25A | Total Hydrocarbons | PASS | NA | Y |  | Yes
2011 | 800 | 0664000056 | Waste Management of Ohio (Suburban South Recycling) | 3415 Township Road 447 | Glenford | 43739 |  | Perry | P005 | 1148 HP CAT 3516 Reciprocating LFG Engine | 2011-06-01 | NA | Custom Statck Analysis , LLC | 1148 Hp/ 800 Kw | 1.0 grams/hp-hr | 1148 grams/hr-hr/812 Kw | 0.26 grams/hp-hr | 25A | Total Hydrocarbons | PASS | NA | Y |  | Yes
2012 | 738 | 0664000056 | Waste Management of Ohio (Suburban South Recycling) | 3415 Township Road 447 | Glenford | 43739 |  | Perry | P008 | 1148 HP CAT 3516 Reciprocating LFG Engine | 2012-04-02 | NA | RMC Environmental, Inc. | 1148 Hp/ 800 Kw | 1.0 grams/hp-hr | 1148 grams/hr-hr/810 Kw | 0.07 grams/hp-hr | 25A | Total Hydrocarbons | PASS | NA | Y |  | Yes
2012 | 743 | 0664000056 | Waste Management of Ohio (Suburban South Recycling) | 3415 Township Road 447 | Glenford | 43739 |  | Perry | P005 | 1148 HP CAT 3516 Reciprocating LFG Engine | 2012-04-03 | NA | RMC Environmental, Inc. | 1148 Hp/ 800 Kw | 1.0 grams/hp-hr | 1148 grams/hr-hr/810 Kw | 0.12 grams/hp-hr | 25A | Total Hydrocarbons | PASS | NA | Y | emissions limit: 0.55 lbs/hr test results: 0.29 lbs/hr | Yes
2012 | 745 | 0664000056 | Waste Management of Ohio (Suburban South Recycling) | 3415 Township Road 447 | Glenford | 43739 |  | Perry | P006 | 1148 HP CAT 3516 Reciprocating LFG Engine | 2012-04-03 | NA | RMC Environmental, Inc. | 1148 Hp/ 800 Kw | 1.0 grams/hp-hr | 1148 grams/hr-hr/810 Kw | 0.02 grams/hp-hr | 25A | Total Hydrocarbons | PASS | NA | Y | emissions limit: 0.55 lbs/hr test results: 0.06 lbs/hr | Yes
2012 | 748 | 0664000056 | Waste Management of Ohio (Suburban South Recycling) | 3415 Township Road 447 | Glenford | 43739 |  | Perry | P007 | 1148 HP CAT 3516 Reciprocating LFG Engine | 2012-04-03 | NA | RMC Environmental, Inc. | 1148 Hp/ 800 Kw | 1.0 grams/hp-hr | 1148 grams/hr-hr/810 Kw | 0.01 grams/hp-hr | 25A | Total Hydrocarbons | PASS | NA | Y | emissions limit: 0.55 lbs/hr test results: 0.02 lbs/hr | Yes
2012 | 753 | 0664000056 | Waste Management of Ohio (Suburban South Recycling) | 3415 Township Road 447 | Glenford | 43739 |  | Perry | P003 | 1148 HP CAT 3516 Reciprocating LFG Engine | 2012-04-04 | NA | RMC Environmental, Inc. | 1148 Hp/ 800 Kw | 1.0 grams/hp-hr | 1148 grams/hr-hr/810 Kw | 0.08 grams/hp-hr | 25A | Total Hydrocarbons | PASS | NA | Y | emissions limit: 0.55 lbs/hr test results: 0.20 lbs/hr | Yes
2012 | 757 | 0664000056 | Waste Management of Ohio (Suburban South Recycling) | 3415 Township Road 447 | Glenford | 43739 |  | Perry | P004 | 1148 HP CAT 3516 Reciprocating LFG Engine | 2012-04-04 | NA | RMC Environmental, Inc. | 1148 Hp/ 800 Kw | 1.0 grams/hp-hr | 1148 grams/hr-hr/810 Kw | 0.04 grams/hp-hr | 25A | Total Hydrocarbons | PASS | NA | Y | emissions limit: 0.55 lbs/hr test results: 0.09 lbs/hr | Yes
2012 | 760 | 0664000056 | Waste Management of Ohio (Suburban South Recycling) | 3415 Township Road 447 | Glenford | 43739 |  | Perry | P002 | 1148 HP CAT 3516 Reciprocating LFG Engine | 2012-04-05 | NA | RMC Environmental, Inc. | 1148 Hp/ 800 Kw | 1.0 grams/hp-hr | 1148 grams/hr-hr/810 Kw | 0.0 grams/hp-hr | 25A | Total Hydrocarbons | PASS | NA | Y | emissions limit: 0.55 lbs/hr test results: 0.01 lbs/hr | Yes
2013 | 1256 | 0664000056 | Waste Management of Ohio (Suburban South Recycling) | 3415 Township Road 447 | Glenford | 43739 |  | Perry | P002 | 1148 HP CAT 3516 Reciprocating LFG Engine | 2013-03-26 | oxidative catalyst reduction | RMC Environmental, Inc. | 1148 Hp | 1.0 grams/Hp-hr 0.55 lb/hr | 1148 Hp | 0.11 grams/Hp-hr 0.28 lb/hr | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y | Testing occurred March 26 - 28, 2013. Lisa witnessed three different tests.
2013 | 1259 | 0664000056 | Waste Management of Ohio (Suburban South Recycling) | 3415 Township Road 447 | Glenford | 43739 |  | Perry | P003 | 1148 HP CAT 3516 Reciprocating LFG Engine | 2013-03-26 | oxidative catalyst reduction | RMC Environmental, Inc. | 1148 Hp | 1.0 grams/Hp-hr 0.55 lb/hr | 1148 Hp | 0.06 grams/Hp-hr 0.16 lb/hr | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y | Testing occurred March 26 - 28, 2013. Lisa witnessed three different tests.
2013 | 1262 | 0664000056 | Waste Management of Ohio (Suburban South Recycling) | 3415 Township Road 447 | Glenford | 43739 |  | Perry | P004 | 1148 HP CAT 3516 Reciprocating LFG Engine | 2013-03-26 | oxidative catalyst reduction | RMC Environmental, Inc. | 1148 Hp | 1.0 grams/Hp-hr 0.55 lb/hr | 1148 Hp | 0.07 grams/Hp-hr 0.18 lb/hr | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y | Testing occurred March 26 - 28, 2013. Lisa witnessed three different tests.
2013 | 1264 | 0664000056 | Waste Management of Ohio (Suburban South Recycling) | 3415 Township Road 447 | Glenford | 43739 |  | Perry | P005 | 1148 HP CAT 3516 Reciprocating LFG Engine | 2013-03-26 | oxidative catalyst reduction | RMC Environmental, Inc. | 1148 Hp | 1.0 grams/Hp-hr 0.55 lb/hr | 1148 Hp | 0.09 grams/Hp-hr 0.24 lb/hr | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y | Testing occurred March 26 - 28, 2013. Lisa witnessed three different tests.
2013 | 1267 | 0664000056 | Waste Management of Ohio (Suburban South Recycling) | 3415 Township Road 447 | Glenford | 43739 |  | Perry | P006 | 1148 HP CAT 3516 Reciprocating LFG Engine | 2013-03-26 | oxidative catalyst reduction | RMC Environmental, Inc. | 1148 Hp | 1.0 grams/Hp-hr 0.55 lb/hr | 1148 Hp | 0.08 grams/Hp-hr 0.20 lb/hr | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y | Testing occurred March 26 - 28, 2013. Lisa witnessed three different tests.
2013 | 1271 | 0664000056 | Waste Management of Ohio (Suburban South Recycling) | 3415 Township Road 447 | Glenford | 43739 |  | Perry | P007 | 1148 HP CAT 3516 Reciprocating LFG Engine | 2013-03-26 | oxidative catalyst reduction | RMC Environmental, Inc. | 1148 Hp | 1.0 grams/Hp-hr 0.55 lb/hr | 1148 Hp | 0.13 grams/Hp-hr 0.34 lb/hr | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y | Testing occurred March 26 - 28, 2013. Lisa witnessed three different tests.
2013 | 1274 | 0664000056 | Waste Management of Ohio (Suburban South Recycling) | 3415 Township Road 447 | Glenford | 43739 |  | Perry | P008 | 1148 HP CAT 3516 Reciprocating LFG Engine | 2013-03-26 | oxidative catalyst reduction | RMC Environmental, Inc. | 1148 Hp | 1.0 grams/Hp-hr 0.55 lb/hr | 1148 Hp | 0.05 grams/Hp-hr 0.12 lb/hr | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y | Testing occurred March 26 - 28, 2013. Lisa witnessed three different tests.
2014 | 2110 | 0664000056 | Waste Management of Ohio (Suburban South Recycling) | 3415 Township Road 447 | Glenford | 43739 |  | Perry | P002 | 1148 HP CAT 3516 Reciprocating LFG Engine | 2014-04-28 | none | RMC Environmental | 800 MW | 1.0 g/hp-hr | 824 MW | 0.03 g/hp-hr | 24A | VOC - Volatile Organic Compounds | PASS | NA | Y |  | Yes
2014 | 2113 | 0664000056 | Waste Management of Ohio (Suburban South Recycling) | 3415 Township Road 447 | Glenford | 43739 |  | Perry | P004 | 1148 HP CAT 3516 Reciprocating LFG Engine | 2014-04-28 | none | RMC Environmental | 800 MW | 1.0 g/hp-hr | 828 MW | 0.04 g/hp-hr | 24A | VOC - Volatile Organic Compounds | PASS | NA | Y |  | Yes
2014 | 2117 | 0664000056 | Waste Management of Ohio (Suburban South Recycling) | 3415 Township Road 447 | Glenford | 43739 |  | Perry | P005 | 1148 HP CAT 3516 Reciprocating LFG Engine | 2014-04-28 | none | RMC Environmental | 800 MW | 1.0 g/hp-hr | 818 MW | 0.1 g/hp-hr | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y |  | Yes
2014 | 2118 | 0664000056 | Waste Management of Ohio (Suburban South Recycling) | 3415 Township Road 447 | Glenford | 43739 |  | Perry | P003 | 1148 HP CAT 3516 Reciprocating LFG Engine | 2014-04-29 | none | RMC Environmental | 800 MW | 1.0 g/hp-hr | 818 | 0.03 g/hp-hr | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y |  | Yes
2014 | 2123 | 0664000056 | Waste Management of Ohio (Suburban South Recycling) | 3415 Township Road 447 | Glenford | 43739 |  | Perry | P007 | 1148 HP CAT 3516 Reciprocating LFG Engine | 2014-04-29 | none | RMC Environmental | 800 MW | 1.0 g/hp-hr | 823 MW | 0.1 g/hp-hr | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y |  | Yes
2014 | 2124 | 0664000056 | Waste Management of Ohio (Suburban South Recycling) | 3415 Township Road 447 | Glenford | 43739 |  | Perry | P008 | 1148 HP CAT 3516 Reciprocating LFG Engine | 2014-04-29 | none | RMC Environmental | 800 MW | 1.0 g/hp-hr | 824 MW | 0.1 g/hp-hr | 24A | VOC - Volatile Organic Compounds | PASS | NA | Y |  | Yes
2014 | 2127 | 0664000056 | Waste Management of Ohio (Suburban South Recycling) | 3415 Township Road 447 | Glenford | 43739 |  | Perry | P006 | 1148 HP CAT 3516 Reciprocating LFG Engine | 2014-04-30 | none | RMC Environmenatl | 800 MW | 1.0 g/hp-hr | 825 MW | 0.1 g/hp-hr | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y |  | Yes
2015 | 912 | 0664000056 | Waste Management of Ohio (Suburban South Recycling) | 3415 Township Road 447 | Glenford | 43739 |  | Perry | P003 | 1148 HP CAT 3516 Reciprocating LFG Engine | 2015-03-24 | none | RMC Envirnmental, Inc. | 1,148 hp | 1.0 g/hp-hr | 1,260 hp | 0.14 g/hp-hr | 25A | VOC - Volatile Organic Compounds | PP | NA | Y
2015 | 913 | 0664000056 | Waste Management of Ohio (Suburban South Recycling) | 3415 Township Road 447 | Glenford | 43739 |  | Perry | P005 | 1148 HP CAT 3516 Reciprocating LFG Engine | 2015-03-24 | none | RMC Environmental, Inc | 1,148 hp | 1.0 g/hp-hr | 1,252 hp | 0.1 g/hp-hr | 25A | VOC - Volatile Organic Compounds | PP | NA | Y
2015 | 918 | 0664000056 | Waste Management of Ohio (Suburban South Recycling) | 3415 Township Road 447 | Glenford | 43739 |  | Perry | P002 | 1148 HP CAT 3516 Reciprocating LFG Engine | 2015-03-25 | none | RMC Envirnmental, Inc. | 1,148hp | 1.0 g/hp-hr | 1,228hp | 0.12 g/hp-hr | 25A | VOC - Volatile Organic Compounds | PP | NA | Y
2015 | 919 | 0664000056 | Waste Management of Ohio (Suburban South Recycling) | 3415 Township Road 447 | Glenford | 43739 |  | Perry | P004 | 1148 HP CAT 3516 Reciprocating LFG Engine | 2015-03-25 | none | RMC Environmental, Inc | 1,148 hp | 1.0 g/hp-hr | 1,231 hp | 0.07 g/hp-hr | 25A | VOC - Volatile Organic Compounds | PP | NA | Y
2015 | 924 | 0664000056 | Waste Management of Ohio (Suburban South Recycling) | 3415 Township Road 447 | Glenford | 43739 |  | Perry | P006 | 1148 HP CAT 3516 Reciprocating LFG Engine | 2015-03-25 | none | RMC Environmental, Inc | 1,148 hp | 1.0 g/hp-hr | 1,251 hp | 0.1 g/hp-hr | 25A | VOC - Volatile Organic Compounds | PP | NA | Y
2015 | 925 | 0664000056 | Waste Management of Ohio (Suburban South Recycling) | 3415 Township Road 447 | Glenford | 43739 |  | Perry | P007 | 1148 HP CAT 3516 Reciprocating LFG Engine | 2015-03-26 | none | RMC Environmental, Inc | 1,148 hp | 1.0 g/hp-hr | 1,241 hp | 0.1 g/hr-hr | 25A | VOC - Volatile Organic Compounds | PP | NA | Y
2015 | 930 | 0664000056 | Waste Management of Ohio (Suburban South Recycling) | 3415 Township Road 447 | Glenford | 43739 |  | Perry | P008 | 1148 HP CAT 3516 Reciprocating LFG Engine | 2015-03-26 | none | RMC Environmental, Inc | 1,148 hp | 1.0 g/hp-hr | 1,268 hp | 0.1 g/hp-hr | 25A | VOC - Volatile Organic Compounds | PP | NA | Y
2016 | 1725 | 0664000056 | Waste Management of Ohio (Suburban South Recycling) | 3415 Township Road 447 | Glenford | 43739 |  | Perry | P002 | 1148 HP CAT 3516 Reciprocating LFG Engine | 2016-03-31 | none | RMC Environmental, Inc. | 1148 hp | 1.0 g/hp-hr | 1251 hp | 0.2 g/hp-hr | 25A | VOC - Volatile Organic Compounds | PP | Y | NA
2016 | 1726 | 0664000056 | Waste Management of Ohio (Suburban South Recycling) | 3415 Township Road 447 | Glenford | 43739 |  | Perry | P003 | 1148 HP CAT 3516 Reciprocating LFG Engine | 2016-03-31 | none | RMC Environmental, Inc. | 1148 hp | 1.0 g/hp-hr | 1239 hp | 0.2 g/hp-hr | 25A | VOC - Volatile Organic Compounds | PP | Y | NA
2016 | 1727 | 0664000056 | Waste Management of Ohio (Suburban South Recycling) | 3415 Township Road 447 | Glenford | 43739 |  | Perry | P004 | 1148 HP CAT 3516 Reciprocating LFG Engine | 2016-03-31 | none | RMC Environmental, Inc. | 1148 hp | 1.0 g/hp-hr | 1240 hp | 0.2 g/hp-hr | 25A | VOC - Volatile Organic Compounds | PP | Y | NA
2016 | 1728 | 0664000056 | Waste Management of Ohio (Suburban South Recycling) | 3415 Township Road 447 | Glenford | 43739 |  | Perry | P005 | 1148 HP CAT 3516 Reciprocating LFG Engine | 2016-03-31 | none | RMC Environmental, Inc. | 1148 hp | 1.0 g/hp-hr | 1244 hp | 0.1 g/hp-hr | 25A | VOC - Volatile Organic Compounds | PP | Y | NA
2016 | 1729 | 0664000056 | Waste Management of Ohio (Suburban South Recycling) | 3415 Township Road 447 | Glenford | 43739 |  | Perry | P006 | 1148 HP CAT 3516 Reciprocating LFG Engine | 2016-03-31 | none | RMC Environmental, Inc. | 1148 hp | 1.0 g/hp-hr | 1334 hp | 0.1 g/hp-hr | 25A | VOC - Volatile Organic Compounds | PP | Y | NA
2016 | 1730 | 0664000056 | Waste Management of Ohio (Suburban South Recycling) | 3415 Township Road 447 | Glenford | 43739 |  | Perry | P007 | 1148 HP CAT 3516 Reciprocating LFG Engine | 2016-03-31 | none | RMC Environmental, Inc. | 1148 hp | 1.0 g/hp-hr | 1288 hp | 0.04 g/hp-hr | 25A | VOC - Volatile Organic Compounds | PP | Y | NA
2016 | 1731 | 0664000056 | Waste Management of Ohio (Suburban South Recycling) | 3415 Township Road 447 | Glenford | 43739 |  | Perry | P008 | 1148 HP CAT 3516 Reciprocating LFG Engine | 2016-03-31 | none | RMC Environmental, Inc. | 1148 hp | 1.0 g/hp-hr | 1258 hp | 0.1 g/hp-hr | 25A | VOC - Volatile Organic Compounds | PP | Y | NA
2015 | 552 | 0285032008 | Wooster Renewable Energy, LLC | 1123 Old Columbus Road | Wooster | 44619 |  | Wayne | B001 | Combined Heat and Process Unit consisting of a 1,475 hp/1,800 rpm/1,100 kw, 4SLB, digester gas engine powering a 1.3 MW generator | 2015-04-21 | Oxygen Sensor that will adjust fuel to air ratios. | Custom Stack Analysis | 1475 Hp | 86 ppm @ 15% O2 1.0 g/hp-hr | 1341 Hp | 24.24 ppm @ 15% O2 0.29 g/hp-hr | 25A | Total Hydrocarbons | PP | NA | Y |  | Yes
2006 | 1400 | 1431070849 | University of Cincinnati | Clifton Campus | Cincinnati | 45221 |  | Hamilton | P007 | 2 MW Diesel fuel-fired internal combustion engine | 2006-07-16 | CATALYTIC OXIDIZER | EQM | 2 MW | 0.29 LB/HR | 1.8 MW | 0.11 LB/HR | 25A | Total Hydrocarbons | PASS | NA | Y |  | Yes
2006 | 1402 | 1431070849 | University of Cincinnati | Clifton Campus | Cincinnati | 45221 |  | Hamilton | P008 | 1.5 MW Diesel fuel-fired internal combustion engine | 2006-08-15 | CATALYTIC OXIDIZER | EQM | 1.5 MW | 0.75 LB/HR | 1.35 MW | 0.05 LB/HR | 25A | Total Hydrocarbons | PASS | NA | Y |  | Yes
2012 | 1546 | 1677011251 | Urban Renewables III, LLC | 2460 Akron Peninsula Rd | Akron | 44313 |  | Summit | B001 | Reciprocating internal combustion engine burning landfill gas to drive an electrical generator. | 2012-11-16 | None | Air Compliance Testing, Inc | 1000 kW | 80 ppmvd @ 15% O2 | 997.96 kW | 25.3 ppmvd @ 15% O2 | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y | Testing to comply with 40 CFR part 60 subpart JJJJ. Emission Standards for Stationary Non-Emergency SI. Stationary SI Landfill/Digester Gas Engines. Table 1 (HP > 500). | Yes
2016 | 2421 | 1677011251 | Urban Renewables III, LLC | 2460 Akron Peninsula Rd | Akron | 44313 |  | Summit | B001 | Reciprocating internal combustion engine burning landfill gas to drive an electrical generator. | 2016-06-01 | n/a | Air Compliance Testing, Inc. | 1137 | 80 ppmvd @15%O2 | 900 | 38.8 ppmvd @ 15% O2 | 25A | VOC - Volatile Organic Compounds | PP | Y | Y | Testing to comply with 40 CFR part 60 subpart JJJJ. Emission Standards for Stationary Non-Emergency SI. Stationary SI Landfill/Digester Gas Engines. Table 1 (HP > 500).
2016 | 1472 | 0656005025 | REX Booster Station | Twp Rd 964 | Switzerland Twp. | 43915 |  | Monroe | P004 | Caterpillar 3516C. This is a natural gas fired engine associated with the Generator Unit | 2016-05-04 | C001(Catalytic Converter): Oxidation Catalysts; C002(Catalytic Converter): Oxidation Catalysts; C003(Catalytic Converter): Oxidation Catalysts | Alliance Source Testing | 2175 hp | 0.51 g/hp-hr | 1958 hp | 0.34 g/hp-hr | 25A | VOC - Volatile Organic Compounds | PP | Y | NA
2012 | 374 | 0285000421 | PIONEER EQUIPMENT, INC. | 16875 JERICHO RD. | DALTON | 44618 |  | Wayne | P004 | Stationary natural gas, spark ignition (SI) internal combustion engine (ICE); 440 horsepower (hp), used as primary power source | 2012-10-05 | None | Custom Stack Analysis | 440 Hp | 86 ppm @15%O2 or 1.0 g/hp-hr | 340 HP | 72.25 and .44 | 25A | Total Hydrocarbons | PASS | NA | Y | The Tested average emission rate comes from only runs two and three. Run one was omittted from the average because of an adjustment made after the test run was completed.
2005 | 1143 | 1409090081 | Miami University | Cole Service Building | Oxford | 45056 |  | Butler | P002 | 5732 KW Lean Burn Natural Gas Fired 4-stroke Reciprocating Engine | 2005-08-17 | CO CATALYST | ENVIRONMENTAL QUALITY MANAGEMENT | 5.7 MW | 3.2 LB/HR | 5.7 MW | <0.2 LB/HR | 18 | VOC - Volatile Organic Compounds | PASS | NA | Y | THE TEMPERATURE OF THE GAS AT THE CATALYST INLET WAS 667 DEGREES F AND THE PRESSURE DROP WAS 8.0". THE VOC CONTENT OF THE SAMPLES, EXCLUDING METHANE AND ETHANE, WERE BELOW THE 5 PPM DETECTION LIMIT OF THE METHOD. | Yes
2005 | 1148 | 1409090081 | Miami University | Cole Service Building | Oxford | 45056 |  | Butler | P001 | 5732 KW Lean Burn Natural Gas Fired 4-stroke Reciprocating Engine | 2005-08-18 | CO CATALYST | ENVIRONMENTAL QUALITY MANAGEMENT | 5.7 MW | 3.2 LB/HR | 5.7 MW | <0.2 LB/HR | 18 | VOC - Volatile Organic Compounds | PASS | NA | Y | THE TEMPERATURE OF THE GAS AT THE CATALYST INLET WAS 669 DEGREES F AND THE PRESSURE DROP WAS 8.0". THE BAG SAMPLE FOR RUN 1 WAS LEAKING SO THE DATA WAS NOT USED TO AVERAGE THE RESULTS. THE VOC CONTENT OF THE SAMPLES, EXCLUDING METHANE AND ETHANE, WERE BELOW THE 5 PPM DETECTION LIMIT OF THE METHOD. | Yes
2007 | 1493 | 1318538151 | MM Cuyahoga Energy LLC | Cochran and Solon Roads | Solon | 44139 |  | Cuyahoga | P003 | 9.06 MMBtu per hour Caterpillar internal combustion engine for the burning of landfill gas | 2007-09-06 | N/A | CK Environmental | 950 KW | 20 ppm | 850 KW | 12.5 ppm | 25A | Total Hydrocarbons | PASS | NA | Y |  | Yes
2007 | 1501 | 1318538151 | MM Cuyahoga Energy LLC | Cochran and Solon Roads | Solon | 44139 |  | Cuyahoga | P004 | 9.06 MMBtu per hour Caterpillar internal combustion engine for the burning of landfill gas | 2007-09-06 | N/A | CK Environmental | 950 KW | 20 ppm | 850 KW | 10.1 ppm | 25A | Total Hydrocarbons | PASS | NA | Y |  | Yes
2016 | 402 | 0210002039 | Kilgore Compressor Station-Utica Gas Services, LLC | Pontiff Rd | Kilgore | 43988 |  | Carroll | P013 | 605 hp NG-fired generator equipped w/3-way catalyst Baldor IGLC420-2N: engine reconstructed and given new manufacture date 2016-02-23 (see compliance reports) | 2016-04-18 | CC013(Catalytic Converter): Generator #3 - Three-way Catalyst | Alliance Source Testing, Inc. | 605 | 1.0g/Hp-hr & 86ppm @ 15% O2, & 0.93lb/hr | 555 | 0.006g/Hp-hr & 0.44ppm @ 15% O2, & 0.007lb/hr | 25A | VOC - Volatile Organic Compounds | PP | Y | NA
2013 | 143 | 0204010112 | Iten Industries, Inc. - Plant 1 | 4001 Benefit Ave | Ashtabula | 44005 |  | Ashtabula | P017 | Gen Set SITA (CoGen), 4 stroke rich burn (4SRB), reciprocating internal combustion engine (RICE) for driving and electrical generator. equipped with a catalytic converter | 2013-10-01 | Catalyst | Air Compliance Testing, Inc. | 370 kw | 30% reduction in total VOC through Catalyst | 333 kw or 95.8% of Max | 64.05ppmvd@15%O2 or 33.03% Reduction | 25A | Total Hydrocarbons | PASS | NA | Y | $ test runs were conducted, However two of which failed on the Testing method applicability. The two middle runs with correct data were used and testing was accepted. | Yes
2014 | 1406 | 0370010128 | Jay Plastics-Broscho Fab. Prod. Div. | 1595 W. LONGVIEW AVENUE | Mansfield | 44906 |  | Richland | P006 | 9.361 mmBtu/hr (1531 HP) NG, 4-stroke, LB, SI ICE - Generator #4 | 2014-02-26 | GEN1 cat(Catalytic Converter): 3-way catalytic converter for Generator #1 | Air Compliance Testing, Inc. | 1142 kW | 1.0 gram/bhp-hr | 1089.05 kW | <0.033 gram/bhp-hr | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y |  | Yes
2014 | 1410 | 0370010128 | Jay Plastics-Broscho Fab. Prod. Div. | 1595 W. LONGVIEW AVENUE | Mansfield | 44906 |  | Richland | P002 | 11.581 mmBtu/hour (1475 HP), Natural Gas-Fired, 4-Stroke, Rich-Burn, Spark Ignition, Reciprocating Internal Combustion Engine, w/NSCR | 2014-02-28 | GEN1 cat(Catalytic Converter): 3-way catalytic converter for Generator #1 | Air Compliance Testing, Inc. | 1368 kW | 0.15 gram/bhp-hr | 1042.5 kW | 0.032 g/bhp-hr | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y | Low process weight rate determination made by Chad Winebrenner. VOC emission rate of 0.032 g/bhp-hr is the average of runs 1 and 3 only. | Yes
2004 | 137 | 0180000156 | Honda R & D North America Inc. | 21001 St. Rt. 739 | Raymond | 43067 |  | Union | B027 | Engine testing dynamometer, Bldg 5 Room 100B | 2004-05-11 | thermal incinerator | ALMEGA ENVIRONMENTAL, INC. | 22 gallons/hr | 96% reduction (dre x capture) | 21+ gallons/hr | 99.3% reduction | 204 | Total Hydrocarbons | PASS | NA | Y | Capture efficiency test for MACT initial compliance test
2014 | 2581 | 1431052206 | H.B. Fuller Co. | 4440/4450 MALSBARY RD | BLUE ASH | 45242 |  | Hamilton | P007 | R-5 emulsion polymerization process with thermal oxidizer emissions control device. | 2014-09-30 | oxidizer | Bureau Veritas North America, Inc. | 3 of 6 polymerization kettles in use | 95% DE | 3 kettles were in use | 96.6% | 25A | Total Hydrocarbons | PASS | NA | Y | Report located in Stars2 ID number 89508
2014 | 2582 | 1431052206 | H.B. Fuller Co. | 4440/4450 MALSBARY RD | BLUE ASH | 45242 |  | Hamilton | P008 | R-6 emulsion polymerization process with thermal oxidizer emissions control device. | 2014-09-30 | oxidizer | Bureau Veritas North America, Inc. | 3 of 6 polymerization kettles in use | 95% DE | 3 kettles were in use | 96.6% | 25A | Total Hydrocarbons | PASS | NA | Y | Report located in Stars2 ID number 89508
2014 | 1118 | 0278002033 | Halcon Operating Co Inc - Avalon Farms Production Facility | 3393 Warren Sharon Rd | Vienna Twp.. | 44473 |  | Trumbull | P002 | Natural Gas Engines | 2014-04-08 | CTRL-3(Other): NSCR | Air Compliance/Consultants | 400 HP | .7 g/bhp-hr and 60 ppmvd@15%O2 | 260 Hp | 0.012 g and 0.76 ppmvd | 25A | VOC - Volatile Organic Compounds | PASS | Y | Y
2006 | 1217 | 1318120179 | Ford Motor Company, Cleveland Engine Plants | 17601 Brookpark Rd | Brook Park | 44142 | 1518 | Cuyahoga | P245 | This PTI application is for the modification of emissions unit P245 to allow the capacity of testing larger (3.5 liter) engines and to provide a larger thermal (recuperative) oxidizer to control the resulting engine exhaust emissions. | 2006-12-08 | Thermal Oxidizer | Conestoga-Rovers & Associates | Three 3.5L D35 Engines | OC: 0.4 lb/hr & 95% Destruction Effcy. | Three 3.5L D35 Engines | OC: 0.02 lb/hr & 99.6% Destruction Effcy. | 25A | Total Hydrocarbons | PASS | NA | Y
2011 | 1184 | 1576002033 | East Ohio Gas - Pike Compressor Station | 6024 Kieffer Ave., SW | Canton | 44706 |  | Stark | P003 | One mmBtu/hr. natural gas dehydration system with thermal oxidizer that serves as a control device for VOC's. | 2011-07-08 | Thermal oxidizer | Environmental Quality Management Inc. | 1 MM BTU/hr | 0.5 lb total HAPs/hr | 1 MM BTU/hr | 0.00778 lb total HAPs/hr | 18 | VOC - Volatile Organic Compounds | PASS | NA | Y | Addendum to TR requested. Rec. ok 07/29/11.
2011 | 1185 | 1576002033 | East Ohio Gas - Pike Compressor Station | 6024 Kieffer Ave., SW | Canton | 44706 |  | Stark | P003 | One mmBtu/hr. natural gas dehydration system with thermal oxidizer that serves as a control device for VOC's. | 2011-07-08 | Thermal oxidizer | Environmental Quality Management Inc. | 1 MM BTU/hr | 0.5 lb TOGC/hr | 1 MM BTU/hr | 0.00335 lb propane/hr | 25A | Total Hydrocarbons | PASS | NA | Y | Contacted EQM to update report with sample set of calculations and fill in some missing data. Received ok on 07/29/11.
2016 | 291 | 0125064019 | Dublin Advanced Energy Partners - Dublin Rec Center | 5600 Post Road | Dublin | 43017 |  | Franklin | B001 | 349 bhp natural gas-fired stationary combustion engine | 2016-03-22 | None | Air Compliance Testing | 349 hp-hr | 0.7 g/hp-hr or 60 ppmvd at 15% O2 | 332.6 hp-hr | 6.1 ppmvd, as propane, at 15% O2 | 25A | Total Hydrocarbons | PP | Y | NA | This testing was performed to satisfy the initial testing requirements of 40 CFR Part 60 Subpart JJJJ - Standards of Performance for Stationary Spark Ignition Internal Combustion Engines.
2012 | 1522 | 1667080028 | Cleveland Steel Container Corp - Streetsboro | 10048 Aurora Hudson Rd | Streetsboro | 44241 |  | Portage | K008 | Spray painting line used to coat the interior and exterior of covers for 5-gallon steel pails. Includes 5 MMBtu/hr dry-off oven. Emissions are vented to a regenerative thermal oxidizer control device shared with K001. | 2012-07-13 | Regenerative Thermal Oxidizer | Air Compliance Testing, Inc | 80 covers/minute | 100% Capture Efficiency | 54 covers/minute | 100% Capture Efficiency | 204 | VOC - Volatile Organic Compounds | PASS | NA | Y
2015 | 587 | 0322000295 | Bio-Gas Technologies, LTD | 10215 Hoover Road | Milan | 44846 |  | Erie | P001 | 13.9 mmBtu/hr LFG fired IC engine/generator #1 | 2015-01-22 | None | Air Compliance Testing, Inc. | 800 kW | 1.04 lbs/hr | 779 kW | 1.14 lbs/hr as propane | 25A | VOC - Volatile Organic Compounds | FF | NA | Y |  | Yes
2016 | 416 | 0210012004 | Augusta Compressor Facility- Utica Gas Services, L.L.C. | 8034 Bane Rd NE | East Twp. | 44427 |  | Carroll | P014 | 605-hp Baldor IGLC420-2N Engine Driven Emergency Generator | 2016-09-08 | Oxid. Cat. 3(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 4(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 5(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 6(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 7(Catalytic Converter): | EcoTest Energy Services | 605 Hp | 0.93 lbs/hr, 1.0 g/hp/hr, 86ppmvd@15%O2 | 560 Hp or 92.6% of Max | 0.01 lbs/hr, 0.0 g/hp/hr, 0.01 ppmvd@15%O2 | 25A | VOC - Volatile Organic Compounds | PP | Y | NA
2016 | 417 | 0210012004 | Augusta Compressor Facility- Utica Gas Services, L.L.C. | 8034 Bane Rd NE | East Twp. | 44427 |  | Carroll | P015 | 605-hp Baldor IGLC420-2N Engine Driven Emergency Generator | 2016-09-08 | Oxid. Cat. 3(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 4(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 5(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 6(Catalytic Converter): Oxidative Catalyst; Oxid. Cat. 7(Catalytic Converter): | EcoTest Energy Services | 605 Hp | 0.93 lbs/hr, 1.0 g/hp/hr, 86ppmvd@15%O2 | 560 Hp or 92.6% of Max | 0.01 lbs/hr, 0.0 g/hp/hr, 0.01 ppmvd@15%O2 | 25A | VOC - Volatile Organic Compounds | PP | Y | NA

## Turbine NOx
REPORTING YEAR | RECORD_NUMBER | FACILITY ID | FACILITY NAME | ADDRESS | CITY | ZIP5 | ZIP4 | COUNTY | EUID | EUID DESCRIPTION | EVALUATION DATE | CONTROL EQUPMENT | COMPANY PERFORMING TEST | MAX RATE | ALLOWABLE RATE | TESTED OPERATING RATE | TESTED EMISSION RATE | METHOD NUMBER | POLLUTANTS | RESULTS | CONFORM | AUDIT | NOTES | COULD_BE_GENERATOR
2003 | 3 | 0124010117 | Dominion Transmission - Washington Compressor Station | 708 Parrott Road, N.W. | Washington Court House | 43160 |  | Fayette | B001 | Solar Centaur Combustion Turbine No. 1, 5500 HP | 2003-04-30 | low nox burners | DOMINION TRANSMISSION | 5500 hp | 8.2 lbs/hr | 4477hp | 2.04 lbs/hr | 20 | Nitrogen Dioxide | PASS | NA | Y | emissions unit was at max during test. max pwr is more than just HP and is dependent on NGP. This emissions unit was at 97% NGP. Aslso, this report was reviewed prior to the necessary corrections being made to CETA and therefore this test couldn''t be entered into CETA until august.
2003 | 4 | 0124010117 | Dominion Transmission - Washington Compressor Station | 708 Parrott Road, N.W. | Washington Court House | 43160 |  | Fayette | B002 | Solar Centaur Combustion Turbine No. 2, 5500 HP | 2003-05-01 | none | DOMINION TRANSMISSION | 5500 hp | 8.2 lbs/hr | see comments | 3.59 lbs/hr | 20 | Nitrogen Dioxide | PASS | Y | Y | emissions unit was at max during test. max pwr is more than just HP and is dependent on NGP. This emissions unit was at 96.6% NGP. Aslso, this report was reviewed prior to the necessary corrections being made to CETA and therefore this test couldn''t be entered into CETA until august.
2003 | 5 | 0145000307 | Dominion - Newark Compressor Station | 19042 Nashport Road | Nashport | 43830 |  | Licking | B002 | Solar Centaur Combustion Turbine No. 2, 5500 HP | 2003-05-14 | none | DOMINION TRANSMISSION | 5500 hp | 8.2 lbs/hr | 99%ngp | 3.76 lbs/hr | 20 | Nitrogen Dioxide | PASS | NA | Y | stack test reviewed well prior to ceta form k function becoming operational in our office. Therefore, form k data was entered into ceta august 2003. This emissions unit also demonstrated compliance w/ subpart GGG of the NSPS. Note that max PWR depends on more than just HP and that NGP is a real indicator of the emissions unit being at max during the test TSmore than just HP and that NGP is a real indicator of the emissions unit being at max during the test TS
2003 | 6 | 0124010117 | Dominion Transmission - Washington Compressor Station | 708 Parrott Road, N.W. | Washington Court House | 43160 |  | Fayette | B003 | Solar Centaur Combustion Turbine No. 3, 5500 HP | 2003-04-29 | none | DOMINION TRANSMISSION | 5500 hp | 8.2 lbs/hr | see comments | 5.3 lbs/hr | 20 | Nitrogen Dioxide | PASS | NA | Y | emissions unit was at max during test. max pwr is more than just HP and is dependent on NGP. This emissions unit was at 95.9% NGP. Aslso, this report was reviewed prior to the necessary corrections being made to CETA and therefore this test couldn''t be entered into CETA until august.
2003 | 7 | 0142010079 | Siemens Energy Inc. | 105 N. SANDUSKY STREET | Mount Vernon | 43050 |  | Knox | P019 | Turbine/Compressor Test Stand firing natural gas or petroleum distillate (stack 87-S-06) | 2003-05-29 | control equipment? | AIR COMPLIANCE TESTING, INC. | n/a | 568.8 lbs nox/hr | n/a | 294.84 lbs nox/hr | 7 | Nitrogen Dioxide | PASS | Y | Y
2003 | 8 | 0145000307 | Dominion - Newark Compressor Station | 19042 Nashport Road | Nashport | 43830 |  | Licking | B001 | Solar Centaur Combustion Turbine No. 1, 5500 HP | 2003-05-13 | none | DOMINION TRANSMISSION | 5500 hp | 8.2 lbs/hr | 99% ngp | 7.1 lbs/hr | 20 | Nitrogen Dioxide | PASS | NA | Y | stack test reviewed well prior to ceta form k function becoming operational in our office. Therefore, form k data was entered into ceta august 2003. This emissions unit also demonstrated compliance w/ subpart GGG of the NSPS. Note that max PWR depends on more than just HP and that NGP is a real indicator of the emissions unit being at max during the test TSmore than just HP and that NGP is a real indicator of the emissions unit being at max during the test TS
2003 | 9 | 0145000307 | Dominion - Newark Compressor Station | 19042 Nashport Road | Nashport | 43830 |  | Licking | B003 | Solar Centaur Combustion Turbine No. 3, 5500 HP | 2003-05-16 | none | DOMINION TRANSMISSION | 5500 hp | 8.2 lbs/hr | 99%ngp | 5.52 lbs/hr | 20 | Nitrogen Dioxide | PASS | NA | Y | stack test reviewed well prior to ceta form k function becoming operational in our office. Therefore, form k data was entered into ceta august 2003. This emissions unit also demonstrated compliance w/ subpart GGG of the NSPS. Note that max PWR depends on more than just HP and that NGP is a real indicator of the emissions unit being at max during the test TSmore than just HP and that NGP is a real indicator of the emissions unit being at max during the test TS
2003 | 16 | 0656000032 | Texas Eastern Transmission LP - Berne | 46552 Swazey Road | Lewisville | 43754 | 0000 | Monroe | B002 | Dresser Rand DC 990; 51.62 MMBtu/hr natural gas-fired turbine used for natural gas compression | 2003-03-10 | none | CUBIX CORP. | 51.6 mmbh | 32.8 lb/hr | 35 mmbh - low load | 8.48 lb/hr | 20 | Nitrogen Dioxide | PASS | NA | Y
2003 | 43 | 1409000896 | Duke Energy Indiana, Madison Generating Station | 5657 Kennel Road | Trenton | 45067 |  | Butler | P001 | 84.65 Megawatt (Nominal) Simple-Cycle Combustion Turbine No.1 | 2003-06-17 | control equipment? | GRACE |  |  |  |  | 7 | Nitrogen Oxide | PASS | Y | Y
2003 | 44 | 1409000896 | Duke Energy Indiana, Madison Generating Station | 5657 Kennel Road | Trenton | 45067 |  | Butler | P001 | 84.65 Megawatt (Nominal) Simple-Cycle Combustion Turbine No.1 | 2003-06-17 | control equipment? | GRACE |  |  |  |  | 7 | Nitrogen Dioxide | PASS | Y | Y
2003 | 45 | 1409000896 | Duke Energy Indiana, Madison Generating Station | 5657 Kennel Road | Trenton | 45067 |  | Butler | P002 | 84.65 Megawatt (Nominal) Simple-Cycle Combustion Turbine No 2 | 2003-06-17 | control equipment? | COMPANY DID THE TEST? |  |  |  |  | 7 | Nitrogen Oxide | PASS | NA | Y
2003 | 46 | 1409000896 | Duke Energy Indiana, Madison Generating Station | 5657 Kennel Road | Trenton | 45067 |  | Butler | P002 | 84.65 Megawatt (Nominal) Simple-Cycle Combustion Turbine No 2 | 2003-06-17 | control equipment? | COMPANY DID THE TEST? |  |  |  |  | 7 | Nitrogen Dioxide | PASS | NA | Y
2003 | 47 | 1409000896 | Duke Energy Indiana, Madison Generating Station | 5657 Kennel Road | Trenton | 45067 |  | Butler | P003 | 84.65 Megawatt (Nominal) simple-cycle combustion turbine No. 3 | 2003-06-17 | control equipment? | GRACE |  |  |  |  | 7 | Nitrogen Oxide | PASS | NA | Y
2003 | 48 | 1409000896 | Duke Energy Indiana, Madison Generating Station | 5657 Kennel Road | Trenton | 45067 |  | Butler | P003 | 84.65 Megawatt (Nominal) simple-cycle combustion turbine No. 3 | 2003-06-17 | control equipment? | GRACE |  |  |  |  | 7 | Nitrogen Dioxide | PASS | NA | Y
2003 | 49 | 1409000896 | Duke Energy Indiana, Madison Generating Station | 5657 Kennel Road | Trenton | 45067 |  | Butler | P004 | 84.65 Megawatt (Nominal) simple-cycle combustion turbine No. 4 | 2003-06-17 | control equipment? | GRACE |  |  |  |  | 7 | Nitrogen Oxide | PASS | NA | Y
2003 | 50 | 1409000896 | Duke Energy Indiana, Madison Generating Station | 5657 Kennel Road | Trenton | 45067 |  | Butler | P004 | 84.65 Megawatt (Nominal) simple-cycle combustion turbine No. 4 | 2003-06-17 | control equipment? | GRACE |  |  |  |  | 7 | Nitrogen Dioxide | PASS | NA | Y
2003 | 51 | 1409000896 | Duke Energy Indiana, Madison Generating Station | 5657 Kennel Road | Trenton | 45067 |  | Butler | P005 | 84.65 Megawatt (Nominal) simple-cycle combustion turbine No. 5 | 2003-06-17 | control equipment? | GRACE |  |  |  |  | 7 | Nitrogen Dioxide | PASS | NA | Y
2003 | 52 | 1409000896 | Duke Energy Indiana, Madison Generating Station | 5657 Kennel Road | Trenton | 45067 |  | Butler | P005 | 84.65 Megawatt (Nominal) simple-cycle combustion turbine No. 5 | 2003-06-17 | control equipment? | GRACE |  |  |  |  | 7 | Nitrogen Oxide | PASS | NA | Y
2003 | 53 | 1409000896 | Duke Energy Indiana, Madison Generating Station | 5657 Kennel Road | Trenton | 45067 |  | Butler | P006 | 84.65 Megawatt (Nominal) simple-cycle combustion turbine No. 6 | 2003-06-17 | control equipment? | GRACE |  |  |  |  | 7 | Nitrogen Dioxide | PASS | NA | Y
2003 | 54 | 1409000896 | Duke Energy Indiana, Madison Generating Station | 5657 Kennel Road | Trenton | 45067 |  | Butler | P006 | 84.65 Megawatt (Nominal) simple-cycle combustion turbine No. 6 | 2003-06-17 | control equipment? | GRACE |  |  |  |  | 7 | Nitrogen Oxide | PASS | NA | Y
2003 | 55 | 1409000896 | Duke Energy Indiana, Madison Generating Station | 5657 Kennel Road | Trenton | 45067 |  | Butler | P007 | 84.65 Megawatt (Nominal) simple-cycle combustion turbine No. 7 | 2003-06-17 | control equipment? | GRACE |  |  |  |  | 7 | Nitrogen Oxide | PASS | NA | Y
2003 | 56 | 1409000896 | Duke Energy Indiana, Madison Generating Station | 5657 Kennel Road | Trenton | 45067 |  | Butler | P007 | 84.65 Megawatt (Nominal) simple-cycle combustion turbine No. 7 | 2003-06-17 | control equipment? | GRACE |  |  |  |  | 7 | Nitrogen Dioxide | PASS | NA | Y
2003 | 57 | 1409000896 | Duke Energy Indiana, Madison Generating Station | 5657 Kennel Road | Trenton | 45067 |  | Butler | P008 | 84.65 Megawatt (Nominal) simple-cycle combustion turbine No. 8 | 2003-06-17 | control equipment? | GRACE |  |  |  |  | 7 | Nitrogen Dioxide | PASS | NA | Y
2003 | 58 | 1409000896 | Duke Energy Indiana, Madison Generating Station | 5657 Kennel Road | Trenton | 45067 |  | Butler | P008 | 84.65 Megawatt (Nominal) simple-cycle combustion turbine No. 8 | 2003-06-17 | control equipment? | GRACE |  |  |  |  | 7 | Nitrogen Oxide | PASS | NA | Y
2003 | 63 | 1483060328 | Texas Eastern Transmission - Lebanon | 1157 State Road 122 West | Lebanon | 45036 |  | Warren | P001 | 67.98 MMBtu natural gas fired turbine used for natural gas compression | 2003-09-09 | control equipment? | CUBIX |  |  |  |  | 7 | Nitrogen Dioxide | PASS | NA | Y
2004 | 798 | 0664000100 | Texas Eastern Transmission LP - Somerset | 1895 Big Inch Road | Somerset | 43783 | 0000 | Perry | B009 | Mars Solar Turbine, 10,600 HP, Natural gas-fired turbine used for natural gas compression. ser# 0260M | 2004-03-09 | none | CUBIX CORP. | 85.6 mmbh | 18 lb/hr | 106 mmbh | 9.6 lb/hr | 7 | Nitrogen Dioxide | PASS | NA | Y
2004 | 1179 | 1483060328 | Texas Eastern Transmission - Lebanon | 1157 State Road 122 West | Lebanon | 45036 |  | Warren | P001 | 67.98 MMBtu natural gas fired turbine used for natural gas compression | 2004-07-09 | control equipment? | CUBIX |  |  |  |  | 7 | Nitrogen Dioxide | PASS | NA | Y
2005 | 548 | 0387000377 | Troy Energy, LLC | 22379 Pemberville Road | Luckey | 43443 |  | Wood | P001 | 1,570 mmBTU/hr combustion turbine | 2005-07-13 | none | TRC ENVIRONMENTAL CORPORATION |  |  |  |  | 7 | Nitrogen Oxide | PASS | NA | Y
2005 | 549 | 0387000377 | Troy Energy, LLC | 22379 Pemberville Road | Luckey | 43443 |  | Wood | P001 | 1,570 mmBTU/hr combustion turbine | 2005-07-13 | none | TRC ENVIRONMENTAL CORPORATION |  |  |  |  | 7 | Nitrogen Dioxide | PASS | NA | Y
2005 | 552 | 0387000377 | Troy Energy, LLC | 22379 Pemberville Road | Luckey | 43443 |  | Wood | P001 | 1,570 mmBTU/hr combustion turbine | 2005-07-14 | none | TRC ENVIRONMENTAL CORPORATION |  |  |  |  | 7 | Nitrogen Oxide | PASS | NA | Y
2005 | 555 | 0387000377 | Troy Energy, LLC | 22379 Pemberville Road | Luckey | 43443 |  | Wood | P001 | 1,570 mmBTU/hr combustion turbine | 2005-07-14 | none | TRC ENVIRONMENTAL CORPORATION |  |  |  |  | 7 | Nitrogen Dioxide | PASS | NA | Y
2005 | 557 | 0387000377 | Troy Energy, LLC | 22379 Pemberville Road | Luckey | 43443 |  | Wood | P002 | 1,570 mmBTU/hr combustion turbine | 2005-07-15 | none | TRC ENVIRONMENTAL CORPORATION |  |  |  |  | 7 | Nitrogen Dioxide | PASS | NA | Y
2005 | 558 | 0387000377 | Troy Energy, LLC | 22379 Pemberville Road | Luckey | 43443 |  | Wood | P002 | 1,570 mmBTU/hr combustion turbine | 2005-07-15 | none | TRC ENVIRONMENTAL CORPORATION |  |  |  |  | 7 | Nitrogen Oxide | PASS | NA | Y
2005 | 561 | 0387000377 | Troy Energy, LLC | 22379 Pemberville Road | Luckey | 43443 |  | Wood | P002 | 1,570 mmBTU/hr combustion turbine | 2005-07-18 | none | TRC ENVIRONMENTAL CORPORATION |  |  |  |  | 7 | Nitrogen Dioxide | PASS | NA | Y
2005 | 562 | 0387000377 | Troy Energy, LLC | 22379 Pemberville Road | Luckey | 43443 |  | Wood | P002 | 1,570 mmBTU/hr combustion turbine | 2005-07-18 | none | TRC ENVIRONMENTAL CORPORATION |  |  |  |  | 7 | Nitrogen Oxide | PASS | NA | Y
2005 | 565 | 0387000377 | Troy Energy, LLC | 22379 Pemberville Road | Luckey | 43443 |  | Wood | P003 | 1,570 mmBTU/hr combustion turbine | 2005-07-19 | none | TRC ENVIRONMENTAL CORPORATION |  |  |  |  | 7 | Nitrogen Dioxide | PASS | NA | Y
2005 | 566 | 0387000377 | Troy Energy, LLC | 22379 Pemberville Road | Luckey | 43443 |  | Wood | P003 | 1,570 mmBTU/hr combustion turbine | 2005-07-19 | none | TRC ENVIRONMENTAL CORPORATION |  |  |  |  | 7 | Nitrogen Oxide | PASS | NA | Y
2005 | 570 | 0387000377 | Troy Energy, LLC | 22379 Pemberville Road | Luckey | 43443 |  | Wood | P003 | 1,570 mmBTU/hr combustion turbine | 2005-07-20 | none | TRC ENVIRONMENTAL CORPORATION |  |  |  |  | 7 | Nitrogen Oxide | PASS | NA | Y
2005 | 571 | 0387000377 | Troy Energy, LLC | 22379 Pemberville Road | Luckey | 43443 |  | Wood | P003 | 1,570 mmBTU/hr combustion turbine | 2005-07-20 | none | TRC ENVIRONMENTAL CORPORATION |  |  |  |  | 7 | Nitrogen Dioxide | PASS | NA | Y
2005 | 573 | 0387000377 | Troy Energy, LLC | 22379 Pemberville Road | Luckey | 43443 |  | Wood | P004 | 1,570 mmBTU/hr combustion turbine | 2005-07-21 | none | TRC ENVIRONMENTAL CORPORATION |  |  |  |  | 7 | Nitrogen Oxide | PASS | NA | Y
2005 | 574 | 0387000377 | Troy Energy, LLC | 22379 Pemberville Road | Luckey | 43443 |  | Wood | P004 | 1,570 mmBTU/hr combustion turbine | 2005-07-21 | none | TRC ENVIRONMENTAL CORPORATION |  |  |  |  | 7 | Nitrogen Dioxide | PASS | NA | Y
2005 | 1097 | 1409000896 | Duke Energy Indiana, Madison Generating Station | 5657 Kennel Road | Trenton | 45067 |  | Butler | P007 | 84.65 Megawatt (Nominal) simple-cycle combustion turbine No. 7 | 2005-06-17 | control equipment? | GRACE CONSULTING |  |  |  |  | 7 | Nitrogen Dioxide | PASS | NA | Y
2005 | 1099 | 1409000896 | Duke Energy Indiana, Madison Generating Station | 5657 Kennel Road | Trenton | 45067 |  | Butler | P007 | 84.65 Megawatt (Nominal) simple-cycle combustion turbine No. 7 | 2005-06-17 | control equipment? | GRACE CONSULTING |  |  |  |  | 7 | Nitrogen Oxide | PASS | NA | Y
2006 | 829 | 0656000032 | Texas Eastern Transmission LP - Berne | 46552 Swazey Road | Lewisville | 43754 | 0000 | Monroe | B002 | Dresser Rand DC 990; 51.62 MMBtu/hr natural gas-fired turbine used for natural gas compression | 2006-12-12 | N/A | TRC |  |  |  |  | 7 | Nitrogen Dioxide | PASS | NA | Y
2006 | 830 | 0656000032 | Texas Eastern Transmission LP - Berne | 46552 Swazey Road | Lewisville | 43754 | 0000 | Monroe | B002 | Dresser Rand DC 990; 51.62 MMBtu/hr natural gas-fired turbine used for natural gas compression | 2006-12-12 | N/A | TRC |  |  |  |  | 7 | Nitrogen Oxide | PASS | NA | Y
2007 | 1300 | 1483060328 | Texas Eastern Transmission - Lebanon | 1157 State Road 122 West | Lebanon | 45036 |  | Warren | P001 | 67.98 MMBtu natural gas fired turbine used for natural gas compression | 2007-03-21 | LOW NOX LEAN AIR COMBUSTOR | CUBIX CORPORATION (GE) |  |  |  |  | 20 | Nitrogen Oxide | PASS | NA | Y
2007 | 1326 | 0819780231 | TEXAS EASTERN TRANS, LP - GLEN KARN | 180 MIKESELL RD | Hollansburg | 45332 |  | Darke | B001 | 79.1 mmBtu/hr Natural Gas Turbine | 2007-07-11 | DRY LOW NOX BURNER | GE ENERGY MANAGEMENT SERVICES, INC. |  |  |  |  | 7E | Nitrogen Dioxide | PASS | NA | Y
2007 | 1327 | 0819780231 | TEXAS EASTERN TRANS, LP - GLEN KARN | 180 MIKESELL RD | Hollansburg | 45332 |  | Darke | B001 | 79.1 mmBtu/hr Natural Gas Turbine | 2007-07-11 | DRY LOW NOX BURNER | GE ENERGY MANAGEMENT SERVICES, INC. |  |  |  |  | 7E | Nitrogen Oxide | PASS | NA | Y
2007 | 1329 | 0819780231 | TEXAS EASTERN TRANS, LP - GLEN KARN | 180 MIKESELL RD | Hollansburg | 45332 |  | Darke | B001 | 79.1 mmBtu/hr Natural Gas Turbine | 2007-07-12 | DRY LOW NOX BURNER | GE ENERGY MANAGEMENT SERVICES, INC. |  |  |  |  | 7E | Nitrogen Oxide | PASS | NA | Y
2007 | 1331 | 0819780231 | TEXAS EASTERN TRANS, LP - GLEN KARN | 180 MIKESELL RD | Hollansburg | 45332 |  | Darke | B001 | 79.1 mmBtu/hr Natural Gas Turbine | 2007-07-12 | DRY LOW NOX BURNER | GE ENERGY MANAGEMENT SERVICES, INC. |  |  |  |  | 7E | Nitrogen Dioxide | PASS | NA | Y
2007 | 1332 | 0819780231 | TEXAS EASTERN TRANS, LP - GLEN KARN | 180 MIKESELL RD | Hollansburg | 45332 |  | Darke | B001 | 79.1 mmBtu/hr Natural Gas Turbine | 2007-07-13 | DRY LOW NOX BURNER | GE ENERGY MANAGEMENT SERVICES, INC. |  |  |  |  | 7E | Nitrogen Dioxide | PASS | NA | Y
2007 | 1333 | 0819780231 | TEXAS EASTERN TRANS, LP - GLEN KARN | 180 MIKESELL RD | Hollansburg | 45332 |  | Darke | B001 | 79.1 mmBtu/hr Natural Gas Turbine | 2007-07-13 | DRY LOW NOX BURNER | GE ENERGY MANAGEMENT SERVICES, INC. |  |  |  |  | 7E | Nitrogen Oxide | PASS | NA | Y
2007 | 1335 | 0819780231 | TEXAS EASTERN TRANS, LP - GLEN KARN | 180 MIKESELL RD | Hollansburg | 45332 |  | Darke | B001 | 79.1 mmBtu/hr Natural Gas Turbine | 2007-07-14 | DRY LOW NOX BURNER | GE ENERGY MANAGEMENT SERVICES, INC. |  |  |  |  | 7E | Nitrogen Oxide | PASS | NA | Y | (Stars2 Migration Problems: Tested pollutants: NO2, NO; Permitted Allowable Emission Rate = 25 PPMVD NOX @ 15% O2; Permitted Maximum Operating Rate = 71.19 MMBTU/HR HEAT INPUT; Average Tested Emission Rate = 8.6 PPM NOX @ 15% 02; Average Tested Operating Rate = 71 MMBTU/HR HEAT INPUT;100% OF TURBINE CAPACITY; Results = Passed; AFS Date = 2009-01-05 00:00:00.0; AFS ID = legacy) HIGH CAPACITY DEMONSTRATION. NUMEROUS TEST DELAYS PUSHED THE DATE REPEATEDLY. THE UNIT WAS DELAYED FOR LACK OF DEMAND FOR NATURAL GAS BUT MORE IMPORTANTLY MAINTENANCE PROBLEMS RELATING TO FRACTURES IN THE BODY OF THE HOUSING. UPON REPAIR - THE TEST WAS COMPLETED. THE TEST WAS COMPOSED OF 12 RUNS TOTAL = 3 TEST RUNS PER OPERATING CAPACITY. FOUR OPERATING CAPACITIES SPANNING 92%, 95%, 98%, AND 100% OF THE NORMAL OPERATING RANGE AS ALLOWED BY SUBPART GG. NOX AND CO WERE TESTED IN EACH RANGE AND THE VALUES ARE GIVEN IN SEPARATE APPENDIX K FILES. TESTS AT THE DIFFERENT CAPACITIES CONDUCTED ON SAME DATE BUT ENTERED AS SUCCESSIVE DATES FOR CETA ENTRY PURPOSES. NOX = 2.18 LB/HR.
2007 | 1337 | 0819780231 | TEXAS EASTERN TRANS, LP - GLEN KARN | 180 MIKESELL RD | Hollansburg | 45332 |  | Darke | B001 | 79.1 mmBtu/hr Natural Gas Turbine | 2007-07-14 | DRY LOW NOX BURNER | GE ENERGY MANAGEMENT SERVICES, INC. |  |  |  |  | 7E | Nitrogen Dioxide | PASS | NA | Y
2007 | 1674 | 1483060328 | Texas Eastern Transmission - Lebanon | 1157 State Road 122 West | Lebanon | 45036 |  | Warren | P001 | 67.98 MMBtu natural gas fired turbine used for natural gas compression | 2007-03-21 | LOW NOX LEAN AIR COMBUSTOR | CUBIX CORPORATION (GE) |  |  |  |  | 20 | Nitrogen Dioxide | PASS | NA | Y
2009 | 103 | 1483060328 | Texas Eastern Transmission - Lebanon | 1157 State Road 122 West | Lebanon | 45036 |  | Warren | P001 | 67.98 MMBtu natural gas fired turbine used for natural gas compression | 2009-05-19 | LOW NOX LEAN AIR COMBUSTOR | CUBIX CORPORATION (GE) |  |  |  |  | 20 | Nitrogen Oxide | PASS | NA | Y | Tested pollutants: NO2, NO; Permitted Allowable Emission Rate = 9.0 LB/HR and 40 PPMV; Permitted Maximum Operating Rate = 45.69 MMBTU/HR; Average Tested Emission Rate = 2.36 LB/HR and 11.81 PPMV; Average Tested Operating Rate = 44.7 MMBTU/HR (LOAD 98%); Results = Passed; AFS Date = 2009-07-30 00:00:00.0; AFS ID = legacy) TESTED AT THREE ADDITIONAL LOAD CONDITIONS: NOX EMISSIONS LB/HR PPMV LOAD 92% 1.42 8.2 LOAD 94% 1.54 8.4 LOAD 96% 1.65 8.6
2009 | 104 | 1483060328 | Texas Eastern Transmission - Lebanon | 1157 State Road 122 West | Lebanon | 45036 |  | Warren | P001 | 67.98 MMBtu natural gas fired turbine used for natural gas compression | 2009-05-19 | LOW NOX LEAN AIR COMBUSTOR | CUBIX CORPORATION (GE) |  |  |  |  | 20 | Nitrogen Dioxide | PASS | NA | Y | Tested pollutants: NO2, NO; Permitted Allowable Emission Rate = 9.0 LB/HR and 40 PPMV; Permitted Maximum Operating Rate = 45.69 MMBTU/HR; Average Tested Emission Rate = 2.36 LB/HR and 11.81 PPMV; Average Tested Operating Rate = 44.7 MMBTU/HR (LOAD 98%); Results = Passed; AFS Date = 2009-07-30 00:00:00.0; AFS ID = legacy) TESTED AT THREE ADDITIONAL LOAD CONDITIONS: NOX EMISSIONS LB/HR PPMV LOAD 92% 1.42 8.2 LOAD 94% 1.54 8.4 LOAD 96% 1.65 8.6
2010 | 28 | 0656000032 | Texas Eastern Transmission LP - Berne | 46552 Swazey Road | Lewisville | 43754 | 0000 | Monroe | B002 | Dresser Rand DC 990; 51.62 MMBtu/hr natural gas-fired turbine used for natural gas compression | 2010-02-09 | N/A | Nordon Corporation |  |  |  |  | 7 | Nitrogen Dioxide | PASS | NA | Y | Tested pollutants:NO2, NO; Permitted Allowable Emission Rate = 32.8 lbs/hr; Permitted Maximum Operating Rate = 5100 Hp; Average Tested Emission Rate = 9.5, 10.7, 15.4, & 18.8 lbs/hr; Average Tested Operating Rate = 50%,60%,75%, and >90% of max load; Results = Passed; AFS Date = 2010-07-28 00:00:00.0; AFS ID = legacy; Witnessed=No, but it says Witnessed By Lisa Duvall)
2010 | 31 | 1576001799 | East Ohio Gas - Robinson Station | 5433 West Blvd | Canton | 44718 |  | Stark | P005 | Solar Centaur Model 40-4700S, natural gas-fired lean-burn regenerative cycle gas turbine #1, unit #4805.2, with 4700 HP rated power output, and 41.62 MMBtu/hr rated heat input. This turbine drives a NG compressor unit 4805 for underground NG storage during non-winter months. Upgraded in year 2009 by adding SoLoNOx burners which increased the horsepower from 3730 to 4700, increased heat input from 29 mmBTU/hr to 41.62 mmBUT/hr and decreased the NOx emissions from 66.2 TPY to 30.5 TPY. | 2010-05-20 | SoLo NOx Control System | Environmental Quality Management, Inc. |  |  |  |  | 7E | Nitrogen Oxide | PASS | NA | Y | Tested pollutants:NO2, NO; Permitted Allowable Emission Rate = 7.0 lbs NOx/hr; Permitted Maximum Operating Rate = 4700 HP rated power output, 41.62 MMBtu/hr; Average Tested Emission Rate = 2.1 lbs NOx/hr; Average Tested Operating Rate = 3473 HP; Results = Passed; AFS Date = 2010-07-28 00:00:00.0; AFS ID = legacy) Three test runs were conducted, Run #1 at 100% load (4730 HP), Run #2 at 95% load (3473 HP), and Run #3 at 90% load (2220 HP). See full report for additional results.
2011 | 1167 | 1483060328 | Texas Eastern Transmission - Lebanon | 1157 State Road 122 West | Lebanon | 45036 |  | Warren | P001 | 67.98 MMBtu natural gas fired turbine used for natural gas compression | 2011-11-04 | LOW NOX LEAN AIR COMBUSTOR | Nordon Corporation |  |  |  |  | 20 | Nitrogen Oxide | PASS | NA | Y | Tested pollutants: NO2, NO; Permitted Allowable Emission Rate = 9.0 LB/HR and 40 PPMV@15%O2; Permitted Maximum Operating Rate = 45.69 MMBTU/HR; Average Tested Emission Rate = 2.8 LB/HR and 14 PPMV@15% O2; Average Tested Operating Rate = 45.2 MMBTU/HR (LOAD 99%); Results = Passed; AFS Date = 2012-01-04 00:00:00.0; AFS ID = legacy) TESTED AT THREE ADDITIONAL LOAD CONDITIONS: NOX EMISSIONS LB/HR PPMV LOAD 97% 1.9 10 LOAD 95% 1.6 9 LOAD 92% 1.5 10
2011 | 1168 | 1483060328 | Texas Eastern Transmission - Lebanon | 1157 State Road 122 West | Lebanon | 45036 |  | Warren | P001 | 67.98 MMBtu natural gas fired turbine used for natural gas compression | 2011-11-04 | LOW NOX LEAN AIR COMBUSTOR | Nordon Corporation |  |  |  |  | 20 | Nitrogen Dioxide | PASS | NA | Y | Tested pollutants: NO2, NO; Permitted Allowable Emission Rate = 9.0 LB/HR and 40 PPMV@15%O2; Permitted Maximum Operating Rate = 45.69 MMBTU/HR; Average Tested Emission Rate = 2.8 LB/HR and 14 PPMV@15% O2; Average Tested Operating Rate = 45.2 MMBTU/HR (LOAD 99%); Results = Passed; AFS Date = 2012-01-04 00:00:00.0; AFS ID = legacy) TESTED AT THREE ADDITIONAL LOAD CONDITIONS: NOX EMISSIONS LB/HR PPMV LOAD 97% 1.9 10 LOAD 95% 1.6 9 LOAD 92% 1.5 10
2012 | 48 | 0124010117 | Dominion Transmission - Washington Compressor Station | 708 Parrott Road, N.W. | Washington Court House | 43160 |  | Fayette | B001 | Solar Centaur Combustion Turbine No. 1, 5500 HP | 2012-04-10 | Low NOx burner | Dominion Transmission |  |  |  |  | 20 | Nitrogen Dioxide | PASS | NA | Y | Tested pollutants: NO2, NO; Permitted Allowable Emission Rate = 42 ppm; 8.2 lbs/hr; Permitted Maximum Operating Rate = 100%; Average Tested Emission Rate = 20.6 ppm; 4.09 lbs/hr; Average Tested Operating Rate = 100% torque; Results = Passed; AFS Date = 2012-06-27 00:00:00.0; AFS ID = legacy) Additional test run at 93% torque resulted in 9.8 ppm and 1.85 lbs/hr NOx.
2012 | 50 | 0124010117 | Dominion Transmission - Washington Compressor Station | 708 Parrott Road, N.W. | Washington Court House | 43160 |  | Fayette | B001 | Solar Centaur Combustion Turbine No. 1, 5500 HP | 2012-04-10 | Low NOx burner | Dominion Transmission |  |  |  |  | 20 | Nitrogen Oxide | PASS | NA | Y | Tested pollutants: NO2, NO; Permitted Allowable Emission Rate = 42 ppm; 8.2 lbs/hr; Permitted Maximum Operating Rate = 100%; Average Tested Emission Rate = 20.6 ppm; 4.09 lbs/hr; Average Tested Operating Rate = 100% torque; Results = Passed; AFS Date = 2012-06-27 00:00:00.0; AFS ID = legacy) Additional test run at 93% torque resulted in 9.8 ppm and 1.85 lbs/hr NOx.
2012 | 51 | 0124010117 | Dominion Transmission - Washington Compressor Station | 708 Parrott Road, N.W. | Washington Court House | 43160 |  | Fayette | B002 | Solar Centaur Combustion Turbine No. 2, 5500 HP | 2012-04-10 | Low NOx burner | Dominion Transmission |  |  |  |  | 20 | Nitrogen Oxide | PASS | NA | Y | Tested pollutants: NO2, NO; Permitted Allowable Emission Rate = 42 ppm; 8.2 lbs/hr; Permitted Maximum Operating Rate = 100%; Average Tested Emission Rate = 34.1 ppm; 6.42 lbs/hr; Average Tested Operating Rate = 100% torque; Results = Passed; AFS Date = 2012-06-27 00:00:00.0; AFS ID = legacy) Additional test run at 94% torque resulted in 36.5 ppm and 5.75 lbs/hr NOx.
2012 | 52 | 0124010117 | Dominion Transmission - Washington Compressor Station | 708 Parrott Road, N.W. | Washington Court House | 43160 |  | Fayette | B002 | Solar Centaur Combustion Turbine No. 2, 5500 HP | 2012-04-10 | Low NOx burner | Dominion Transmission |  |  |  |  | 20 | Nitrogen Dioxide | PASS | NA | Y | Tested pollutants: NO2, NO; Permitted Allowable Emission Rate = 42 ppm; 8.2 lbs/hr; Permitted Maximum Operating Rate = 100%; Average Tested Emission Rate = 34.1 ppm; 6.42 lbs/hr; Average Tested Operating Rate = 100% torque; Results = Passed; AFS Date = 2012-06-27 00:00:00.0; AFS ID = legacy) Additional test run at 94% torque resulted in 36.5 ppm and 5.75 lbs/hr NOx.
2012 | 83 | 0124010117 | Dominion Transmission - Washington Compressor Station | 708 Parrott Road, N.W. | Washington Court House | 43160 |  | Fayette | B003 | Solar Centaur Combustion Turbine No. 3, 5500 HP | 2012-04-11 | Low NOx burner | Dominion Transmission |  |  |  |  | 20 | Nitrogen Dioxide | PASS | NA | Y | Tested pollutants: NO2, NO; Permitted Allowable Emission Rate = 42 ppm; 8.2 lbs/hr; Permitted Maximum Operating Rate = 100%; Average Tested Emission Rate = 30.5 ppm; 6.14 lbs/hr; Average Tested Operating Rate = 100% torque; Results = Passed; AFS Date = 2012-06-27 00:00:00.0; AFS ID = legacy) Additional test run at 93% torque resulted in 19.2 ppm and 3.22 lbs/hr NOx.
2012 | 84 | 0124010117 | Dominion Transmission - Washington Compressor Station | 708 Parrott Road, N.W. | Washington Court House | 43160 |  | Fayette | B003 | Solar Centaur Combustion Turbine No. 3, 5500 HP | 2012-04-11 | Low NOx burner | Dominion Transmission |  |  |  |  | 20 | Nitrogen Oxide | PASS | NA | Y | Tested pollutants: NO2, NO; Permitted Allowable Emission Rate = 42 ppm; 8.2 lbs/hr; Permitted Maximum Operating Rate = 100%; Average Tested Emission Rate = 30.5 ppm; 6.14 lbs/hr; Average Tested Operating Rate = 100% torque; Results = Passed; AFS Date = 2012-06-27 00:00:00.0; AFS ID = legacy) Additional test run at 93% torque resulted in 19.2 ppm and 3.22 lbs/hr NOx.
2012 | 141 | 0145000307 | Dominion - Newark Compressor Station | 19042 Nashport Road | Nashport | 43830 |  | Licking | B002 | Solar Centaur Combustion Turbine No. 2, 5500 HP | 2012-04-03 | none | DOMINION TRANSMISSION |  |  |  |  | 7E | Nitrogen Dioxide | PASS | NA | Y | Tested pollutants: NO2, NO; Permitted Allowable Emission Rate = 8.20 lbs/hr; Permitted Maximum Operating Rate = 5500 hp; Average Tested Emission Rate = 3.38 lbs/hr; Average Tested Operating Rate = 99% ngp; Results = Passed; AFS Date = 2012-11-30 00:00:00.0; AFS ID = legacy; Witnessed=No, but it says Witnessed By Adam Novak)
2012 | 142 | 0145000307 | Dominion - Newark Compressor Station | 19042 Nashport Road | Nashport | 43830 |  | Licking | B002 | Solar Centaur Combustion Turbine No. 2, 5500 HP | 2012-04-03 | none | DOMINION TRANSMISSION |  |  |  |  | 7E | Nitrogen Oxide | PASS | NA | Y | Tested pollutants: NO2, NO; Permitted Allowable Emission Rate = 8.20 lbs/hr; Permitted Maximum Operating Rate = 5500 hp; Average Tested Emission Rate = 3.38 lbs/hr; Average Tested Operating Rate = 99% ngp; Results = Passed; AFS Date = 2012-11-30 00:00:00.0; AFS ID = legacy; Witnessed=No, but it says Witnessed By Adam Novak)
2012 | 146 | 0145000307 | Dominion - Newark Compressor Station | 19042 Nashport Road | Nashport | 43830 |  | Licking | B003 | Solar Centaur Combustion Turbine No. 3, 5500 HP | 2012-04-03 | none | DOMINION TRANSMISSION |  |  |  |  | 7E | Nitrogen Dioxide | PASS | NA | Y | Tested pollutants: NO2, NO; Permitted Allowable Emission Rate = 8.20 lbs/hr; Permitted Maximum Operating Rate = 5500 hp; Average Tested Emission Rate = 3.50 lbs/hr; Average Tested Operating Rate = 99% ngp; Results = Passed; AFS Date = 2012-11-30 00:00:00.0; AFS ID = legacy; Witnessed=No, but it says Witnessed By Adam Novak)
2012 | 147 | 0145000307 | Dominion - Newark Compressor Station | 19042 Nashport Road | Nashport | 43830 |  | Licking | B003 | Solar Centaur Combustion Turbine No. 3, 5500 HP | 2012-04-03 | none | DOMINION TRANSMISSION |  |  |  |  | 7E | Nitrogen Oxide | PASS | NA | Y | Tested pollutants: NO2, NO; Permitted Allowable Emission Rate = 8.20 lbs/hr; Permitted Maximum Operating Rate = 5500 hp; Average Tested Emission Rate = 3.50 lbs/hr; Average Tested Operating Rate = 99% ngp; Results = Passed; AFS Date = 2012-11-30 00:00:00.0; AFS ID = legacy; Witnessed=No, but it says Witnessed By Adam Novak)
2012 | 149 | 0145000307 | Dominion - Newark Compressor Station | 19042 Nashport Road | Nashport | 43830 |  | Licking | B001 | Solar Centaur Combustion Turbine No. 1, 5500 HP | 2012-04-04 | none | DOMINION TRANSMISSION |  |  |  |  | 7E | Nitrogen Dioxide | PASS | NA | Y | Tested pollutants: NO2, NO; Permitted Allowable Emission Rate = 8.20 lbs/hr; Permitted Maximum Operating Rate = 5500 hp; Average Tested Emission Rate = 4.35 lbs/hr; Average Tested Operating Rate = 99% ngp; Results = Passed; AFS Date = 2012-11-30 00:00:00.0; AFS ID = legacy; Witnessed=No, but it says Witnessed By Adam Novak)
2012 | 150 | 0145000307 | Dominion - Newark Compressor Station | 19042 Nashport Road | Nashport | 43830 |  | Licking | B001 | Solar Centaur Combustion Turbine No. 1, 5500 HP | 2012-04-04 | none | DOMINION TRANSMISSION |  |  |  |  | 7E | Nitrogen Oxide | PASS | NA | Y | Tested pollutants: NO2, NO; Permitted Allowable Emission Rate = 8.20 lbs/hr; Permitted Maximum Operating Rate = 5500 hp; Average Tested Emission Rate = 4.35 lbs/hr; Average Tested Operating Rate = 99% ngp; Results = Passed; AFS Date = 2012-11-30 00:00:00.0; AFS ID = legacy; Witnessed=No, but it says Witnessed By Adam Novak)
2012 | 220 | 0204010193 | Cristal USA Inc., Ashtabula Complex Plant 2 | 2426 Middle Road | Ashtabula | 44004 |  | Ashtabula | B016 | 65.1 mmBtu/hr natural gas-fired combustion turbine with NOx emissions contorl technology and a 55.0 mmBtu/hr natural gas-fired duct heater/heat recovery boiler no. 5 | 2012-04-25 | none | Contastoga-Rovers & Associates |  |  |  |  | 7E | Nitrogen Dioxide | PASS | NA | Y | Tested pollutants: NO2, NO; Permitted Allowable Emission Rate = 12.53 #/hr; Permitted Maximum Operating Rate = 5500 kW; Average Tested Emission Rate = 9.1 #/hr; 15.8 ppmvd; Average Tested Operating Rate = 5304 kW (96.4% load); Results = Passed; AFS Date = 2012-11-30 00:00:00.0; AFS ID = legacy)
2012 | 221 | 0204010193 | Cristal USA Inc., Ashtabula Complex Plant 2 | 2426 Middle Road | Ashtabula | 44004 |  | Ashtabula | B016 | 65.1 mmBtu/hr natural gas-fired combustion turbine with NOx emissions contorl technology and a 55.0 mmBtu/hr natural gas-fired duct heater/heat recovery boiler no. 5 | 2012-04-25 | none | Contastoga-Rovers & Associates |  |  |  |  | 7E | Nitrogen Oxide | PASS | NA | Y | Tested pollutants: NO2, NO; Permitted Allowable Emission Rate = 12.53 #/hr; Permitted Maximum Operating Rate = 5500 kW; Average Tested Emission Rate = 9.1 #/hr; 15.8 ppmvd; Average Tested Operating Rate = 5304 kW (96.4% load); Results = Passed; AFS Date = 2012-11-30 00:00:00.0; AFS ID = legacy)
2012 | 222 | 0204010193 | Cristal USA Inc., Ashtabula Complex Plant 2 | 2426 Middle Road | Ashtabula | 44004 |  | Ashtabula | B017 | 65.1 mmBtu/hr natural gas-fired turbine with NOx emissions control technology and a heat recovery steam generator no. 1 | 2012-04-25 | steam low NOx injection system | Contastoga-Rovers & Associates |  |  |  |  | 7E | Nitrogen Oxide | PASS | NA | Y | Tested pollutants: NO2, NO; Permitted Allowable Emission Rate = 7.03 #/hr, 190 ppmvd @15% O2; Permitted Maximum Operating Rate = 5500 kW; Average Tested Emission Rate = 5.3 #/hr, 21.8 ppmbd @15% O2; Average Tested Operating Rate = 5485 kW (99.7% load); Results = Passed; AFS Date = 2012-11-30 00:00:00.0; AFS ID = legacy)
2012 | 224 | 0204010193 | Cristal USA Inc., Ashtabula Complex Plant 2 | 2426 Middle Road | Ashtabula | 44004 |  | Ashtabula | B017 | 65.1 mmBtu/hr natural gas-fired turbine with NOx emissions control technology and a heat recovery steam generator no. 1 | 2012-04-25 | steam low NOx injection system | Contastoga-Rovers & Associates |  |  |  |  | 7E | Nitrogen Dioxide | PASS | NA | Y | Tested pollutants: NO2, NO; Permitted Allowable Emission Rate = 7.03 #/hr, 190 ppmvd @15% O2; Permitted Maximum Operating Rate = 5500 kW; Average Tested Emission Rate = 5.3 #/hr, 21.8 ppmbd @15% O2; Average Tested Operating Rate = 5485 kW (99.7% load); Results = Passed; AFS Date = 2012-11-30 00:00:00.0; AFS ID = legacy)
2012 | 236 | 0204010193 | Cristal USA Inc., Ashtabula Complex Plant 2 | 2426 Middle Road | Ashtabula | 44004 |  | Ashtabula | B016 | 65.1 mmBtu/hr natural gas-fired combustion turbine with NOx emissions contorl technology and a 55.0 mmBtu/hr natural gas-fired duct heater/heat recovery boiler no. 5 | 2012-04-26 | none | Contastoga-Rovers & Associates |  |  |  |  | 7E | Nitrogen Dioxide | PASS | NA | Y | Tested pollutants: NO2, NO; Permitted Allowable Emission Rate = 12.53 #/hr; Permitted Maximum Operating Rate = 5500 kW; Average Tested Emission Rate = 9.0 #/hr; 15.6 ppmvd; Average Tested Operating Rate = 5242 kW (95.3% load); Results = Passed; AFS Date = 2012-11-30 00:00:00.0; AFS ID = legacy)
2012 | 237 | 0204010193 | Cristal USA Inc., Ashtabula Complex Plant 2 | 2426 Middle Road | Ashtabula | 44004 |  | Ashtabula | B016 | 65.1 mmBtu/hr natural gas-fired combustion turbine with NOx emissions contorl technology and a 55.0 mmBtu/hr natural gas-fired duct heater/heat recovery boiler no. 5 | 2012-04-26 | none | Contastoga-Rovers & Associates |  |  |  |  | 7E | Nitrogen Oxide | PASS | NA | Y | Tested pollutants: NO2, NO; Permitted Allowable Emission Rate = 12.53 #/hr; Permitted Maximum Operating Rate = 5500 kW; Average Tested Emission Rate = 9.0 #/hr; 15.6 ppmvd; Average Tested Operating Rate = 5242 kW (95.3% load); Results = Passed; AFS Date = 2012-11-30 00:00:00.0; AFS ID = legacy)
2012 | 238 | 0204010193 | Cristal USA Inc., Ashtabula Complex Plant 2 | 2426 Middle Road | Ashtabula | 44004 |  | Ashtabula | B017 | 65.1 mmBtu/hr natural gas-fired turbine with NOx emissions control technology and a heat recovery steam generator no. 1 | 2012-04-26 | Chen low NOx steam injection system | Contastoga-Rovers & Associates |  |  |  |  | 7E | Nitrogen Dioxide | PASS | NA | Y | Tested pollutants: NO2, NO; Permitted Allowable Emission Rate = 7.03 #/hr, 190 ppmvd @15% O2; Permitted Maximum Operating Rate = 5500 kW; Average Tested Emission Rate = 4.37 #/hr, 19.3 ppmvd @15% O2; Average Tested Operating Rate = 4930 kW (89.6% load); Results = Passed; AFS Date = 2012-11-30 00:00:00.0; AFS ID = legacy)
2012 | 239 | 0204010193 | Cristal USA Inc., Ashtabula Complex Plant 2 | 2426 Middle Road | Ashtabula | 44004 |  | Ashtabula | B017 | 65.1 mmBtu/hr natural gas-fired turbine with NOx emissions control technology and a heat recovery steam generator no. 1 | 2012-04-26 | Chen low NOx steam injection system | Contastoga-Rovers & Associates |  |  |  |  | 7E | Nitrogen Oxide | PASS | NA | Y | Tested pollutants: NO2, NO; Permitted Allowable Emission Rate = 7.03 #/hr, 190 ppmvd @15% O2; Permitted Maximum Operating Rate = 5500 kW; Average Tested Emission Rate = 4.37 #/hr, 19.3 ppmvd @15% O2; Average Tested Operating Rate = 4930 kW (89.6% load); Results = Passed; AFS Date = 2012-11-30 00:00:00.0; AFS ID = legacy)
2012 | 244 | 0204010193 | Cristal USA Inc., Ashtabula Complex Plant 2 | 2426 Middle Road | Ashtabula | 44004 |  | Ashtabula | B016 | 65.1 mmBtu/hr natural gas-fired combustion turbine with NOx emissions contorl technology and a 55.0 mmBtu/hr natural gas-fired duct heater/heat recovery boiler no. 5 | 2012-04-27 | none | Contastoga-Rovers & Associates |  |  |  |  | 7E | Nitrogen Oxide | PASS | NA | Y | Tested pollutants: NO2, NO; Permitted Allowable Emission Rate = 12.53 #/hr; Permitted Maximum Operating Rate = 5500 kW; Average Tested Emission Rate = 9.3 #/hr; 17.1 ppmvd; Average Tested Operating Rate = 4394 kW (79.9% load); Results = Passed; AFS Date = 2012-11-30 00:00:00.0; AFS ID = legacy)
2012 | 245 | 0204010193 | Cristal USA Inc., Ashtabula Complex Plant 2 | 2426 Middle Road | Ashtabula | 44004 |  | Ashtabula | B016 | 65.1 mmBtu/hr natural gas-fired combustion turbine with NOx emissions contorl technology and a 55.0 mmBtu/hr natural gas-fired duct heater/heat recovery boiler no. 5 | 2012-04-27 | none | Contastoga-Rovers & Associates |  |  |  |  | 7E | Nitrogen Dioxide | PASS | NA | Y | Tested pollutants: NO2, NO; Permitted Allowable Emission Rate = 12.53 #/hr; Permitted Maximum Operating Rate = 5500 kW; Average Tested Emission Rate = 9.3 #/hr; 17.1 ppmvd; Average Tested Operating Rate = 4394 kW (79.9% load); Results = Passed; AFS Date = 2012-11-30 00:00:00.0; AFS ID = legacy)
2012 | 246 | 0204010193 | Cristal USA Inc., Ashtabula Complex Plant 2 | 2426 Middle Road | Ashtabula | 44004 |  | Ashtabula | B017 | 65.1 mmBtu/hr natural gas-fired turbine with NOx emissions control technology and a heat recovery steam generator no. 1 | 2012-04-27 | Chen low NOx steam injection system | Contastoga-Rovers & Associates |  |  |  |  | 7E | Nitrogen Dioxide | PASS | NA | Y | Tested pollutants: NO2, NO; Permitted Allowable Emission Rate = 7.03 #/hr, 190 ppmvd @15% O2; Permitted Maximum Operating Rate = 5500 kW; Average Tested Emission Rate = 3.3#/hr, 16.7 ppmvd @15% O2; Average Tested Operating Rate = 4157 kW (75.6% load); Results = Passed; AFS Date = 2012-11-30 00:00:00.0; AFS ID = legacy)
2012 | 247 | 0204010193 | Cristal USA Inc., Ashtabula Complex Plant 2 | 2426 Middle Road | Ashtabula | 44004 |  | Ashtabula | B017 | 65.1 mmBtu/hr natural gas-fired turbine with NOx emissions control technology and a heat recovery steam generator no. 1 | 2012-04-27 | Chen low NOx steam injection system | Contastoga-Rovers & Associates |  |  |  |  | 7E | Nitrogen Oxide | PASS | NA | Y | Tested pollutants: NO2, NO; Permitted Allowable Emission Rate = 7.03 #/hr, 190 ppmvd @15% O2; Permitted Maximum Operating Rate = 5500 kW; Average Tested Emission Rate = 3.3#/hr, 16.7 ppmvd @15% O2; Average Tested Operating Rate = 4157 kW (75.6% load); Results = Passed; AFS Date = 2012-11-30 00:00:00.0; AFS ID = legacy)
2012 | 257 | 0204010193 | Cristal USA Inc., Ashtabula Complex Plant 2 | 2426 Middle Road | Ashtabula | 44004 |  | Ashtabula | B016 | 65.1 mmBtu/hr natural gas-fired combustion turbine with NOx emissions contorl technology and a 55.0 mmBtu/hr natural gas-fired duct heater/heat recovery boiler no. 5 | 2012-04-28 | none | Contastoga-Rovers & Associates |  |  |  |  | 7E | Nitrogen Dioxide | PASS | NA | Y | Tested pollutants: NO2, NO; Permitted Allowable Emission Rate = 12.53 #/hr; Permitted Maximum Operating Rate = 5500 kW; Average Tested Emission Rate = 11.2 #/hr; 21.9 ppmvd; Average Tested Operating Rate = 2930 kW (53.2% load); Results = Passed; AFS Date = 2012-11-30 00:00:00.0; AFS ID = legacy)
2012 | 258 | 0204010193 | Cristal USA Inc., Ashtabula Complex Plant 2 | 2426 Middle Road | Ashtabula | 44004 |  | Ashtabula | B016 | 65.1 mmBtu/hr natural gas-fired combustion turbine with NOx emissions contorl technology and a 55.0 mmBtu/hr natural gas-fired duct heater/heat recovery boiler no. 5 | 2012-04-28 | none | Contastoga-Rovers & Associates |  |  |  |  | 7E | Nitrogen Oxide | PASS | NA | Y | Tested pollutants: NO2, NO; Permitted Allowable Emission Rate = 12.53 #/hr; Permitted Maximum Operating Rate = 5500 kW; Average Tested Emission Rate = 11.2 #/hr; 21.9 ppmvd; Average Tested Operating Rate = 2930 kW (53.2% load); Results = Passed; AFS Date = 2012-11-30 00:00:00.0; AFS ID = legacy)
2012 | 260 | 0204010193 | Cristal USA Inc., Ashtabula Complex Plant 2 | 2426 Middle Road | Ashtabula | 44004 |  | Ashtabula | B017 | 65.1 mmBtu/hr natural gas-fired turbine with NOx emissions control technology and a heat recovery steam generator no. 1 | 2012-04-28 | Chen low NOx steam injection system | Contastoga-Rovers & Associates |  |  |  |  | 7E | Nitrogen Oxide | PASS | NA | Y | Tested pollutants: NO2, NO; Permitted Allowable Emission Rate = 7.03 #/hr, 190 ppmvd @15% O2; Permitted Maximum Operating Rate = 5500 kW; Average Tested Emission Rate = 2.7 #/hr, 17.0 ppmvd @15% O2; Average Tested Operating Rate = 54.3 kW (75.6% load); Results = Passed; AFS Date = 2012-11-30 00:00:00.0; AFS ID = legacy)
2012 | 262 | 0204010193 | Cristal USA Inc., Ashtabula Complex Plant 2 | 2426 Middle Road | Ashtabula | 44004 |  | Ashtabula | B017 | 65.1 mmBtu/hr natural gas-fired turbine with NOx emissions control technology and a heat recovery steam generator no. 1 | 2012-04-28 | Chen low NOx steam injection system | Contastoga-Rovers & Associates |  |  |  |  | 7E | Nitrogen Dioxide | PASS | NA | Y | Tested pollutants: NO2, NO; Permitted Allowable Emission Rate = 7.03 #/hr, 190 ppmvd @15% O2; Permitted Maximum Operating Rate = 5500 kW; Average Tested Emission Rate = 2.7 #/hr, 17.0 ppmvd @15% O2; Average Tested Operating Rate = 54.3 kW (75.6% load); Results = Passed; AFS Date = 2012-11-30 00:00:00.0; AFS ID = legacy)
2012 | 701 | 0660000247 | Appalachian Power Co, Dresden Plant | 9595 McGlade School Rd | Dresden | 43821 |  | Muskingum | P001 | Turbine No 1 to generate electrical power. | 2012-04-03 | SCR | Mostardi Platt |  |  |  |  | 7E | Nitrogen Oxide | PASS | NA | Y | Tested pollutants: NO2, NO; Permitted Allowable Emission Rate = 29.0 lbs/hr Duct burners on; Permitted Maximum Operating Rate = 171 MW; Average Tested Emission Rate = 20.91 lbs/hr; Average Tested Operating Rate = 170 MW; Results = Passed; AFS Date = 2012-08-01 00:00:00.0; AFS ID = legacy) Emissions limit 3.5 ppmvd @ 15% O2 -- Results 2.7 ppmvd @ 15% O2
2012 | 702 | 0660000247 | Appalachian Power Co, Dresden Plant | 9595 McGlade School Rd | Dresden | 43821 |  | Muskingum | P001 | Turbine No 1 to generate electrical power. | 2012-04-03 | SCR | Mostardi Platt |  |  |  |  | 7E | Nitrogen Dioxide | PASS | NA | Y | Tested pollutants: NO2, NO; Permitted Allowable Emission Rate = 29.0 lbs/hr Duct burners on; Permitted Maximum Operating Rate = 171 MW; Average Tested Emission Rate = 20.91 lbs/hr; Average Tested Operating Rate = 170 MW; Results = Passed; AFS Date = 2012-08-01 00:00:00.0; AFS ID = legacy) Emissions limit 3.5 ppmvd @ 15% O2 -- Results 2.7 ppmvd @ 15% O2
2012 | 707 | 0660000247 | Appalachian Power Co, Dresden Plant | 9595 McGlade School Rd | Dresden | 43821 |  | Muskingum | P001 | Turbine No 1 to generate electrical power. | 2012-04-04 | SCR | Mostardi Platt |  |  |  |  | 7E | Nitrogen Oxide | PASS | NA | Y | Tested pollutants: NO2, NO; Permitted Allowable Emission Rate = 25.0 lbs/hr Duct burners off; Permitted Maximum Operating Rate = 171 MW; Average Tested Emission Rate = 18.47 lbs/hr; Average Tested Operating Rate = 170 MW; Results = Passed; AFS Date = 2012-08-01 00:00:00.0; AFS ID = legacy) Emissions limit 3.5 ppmvd @ 15% O2 -- Results 2.8 ppmvd @ 15% O2
2012 | 711 | 0660000247 | Appalachian Power Co, Dresden Plant | 9595 McGlade School Rd | Dresden | 43821 |  | Muskingum | P001 | Turbine No 1 to generate electrical power. | 2012-04-04 | SCR | Mostardi Platt |  |  |  |  | 7E | Nitrogen Dioxide | PASS | NA | Y | Tested pollutants: NO2, NO; Permitted Allowable Emission Rate = 25.0 lbs/hr Duct burners off; Permitted Maximum Operating Rate = 171 MW; Average Tested Emission Rate = 18.47 lbs/hr; Average Tested Operating Rate = 170 MW; Results = Passed; AFS Date = 2012-08-01 00:00:00.0; AFS ID = legacy) Emissions limit 3.5 ppmvd @ 15% O2 -- Results 2.8 ppmvd @ 15% O2
2012 | 714 | 0660000247 | Appalachian Power Co, Dresden Plant | 9595 McGlade School Rd | Dresden | 43821 |  | Muskingum | P002 | Turbine No 2 to generate electrical power. | 2012-04-05 | SCR | Mostardi Platt |  |  |  |  | 7E | Nitrogen Dioxide | PASS | NA | Y | Tested pollutants: NO2, NO; Permitted Allowable Emission Rate = 29.0 lbs/hr Duct burners on; Permitted Maximum Operating Rate = 171 MW; Average Tested Emission Rate = 21.36 lbs/hr; Average Tested Operating Rate = 170 MW; Results = Passed; AFS Date = 2012-08-01 00:00:00.0; AFS ID = legacy) emissions limit 3.5 ppmvd @ 15% O2, - results - 2.8 ppmvd @ 15% O2
2012 | 715 | 0660000247 | Appalachian Power Co, Dresden Plant | 9595 McGlade School Rd | Dresden | 43821 |  | Muskingum | P002 | Turbine No 2 to generate electrical power. | 2012-04-05 | SCR | Mostardi Platt |  |  |  |  | 7E | Nitrogen Oxide | PASS | NA | Y | Tested pollutants: NO2, NO; Permitted Allowable Emission Rate = 29.0 lbs/hr Duct burners on; Permitted Maximum Operating Rate = 171 MW; Average Tested Emission Rate = 21.36 lbs/hr; Average Tested Operating Rate = 170 MW; Results = Passed; AFS Date = 2012-08-01 00:00:00.0; AFS ID = legacy) emissions limit 3.5 ppmvd @ 15% O2, - results - 2.8 ppmvd @ 15% O2
2012 | 723 | 0660000247 | Appalachian Power Co, Dresden Plant | 9595 McGlade School Rd | Dresden | 43821 |  | Muskingum | P002 | Turbine No 2 to generate electrical power. | 2012-04-06 | SCR | Mostardi Platt |  |  |  |  | 7E | Nitrogen Oxide | PASS | NA | Y | Tested pollutants: NO2, NO; Permitted Allowable Emission Rate = 25.0 lbs/hr Duct burners off; Permitted Maximum Operating Rate = 171 MW; Average Tested Emission Rate = 19.69 lbs/hr; Average Tested Operating Rate = 170 MW; Results = Passed; AFS Date = 2012-08-01 00:00:00.0; AFS ID = legacy) emissions limit 3.5 ppmvd @ 15% O2, - results - 3.1 ppmvd @ 15% O2
2012 | 724 | 0660000247 | Appalachian Power Co, Dresden Plant | 9595 McGlade School Rd | Dresden | 43821 |  | Muskingum | P002 | Turbine No 2 to generate electrical power. | 2012-04-06 | SCR | Mostardi Platt |  |  |  |  | 7E | Nitrogen Dioxide | PASS | NA | Y | Tested pollutants: NO2, NO; Permitted Allowable Emission Rate = 25.0 lbs/hr Duct burners off; Permitted Maximum Operating Rate = 171 MW; Average Tested Emission Rate = 19.69 lbs/hr; Average Tested Operating Rate = 170 MW; Results = Passed; AFS Date = 2012-08-01 00:00:00.0; AFS ID = legacy) emissions limit 3.5 ppmvd @ 15% O2, - results - 3.1 ppmvd @ 15% O2
2013 | 975 | 0387020374 | OMEGA JV2 Bowling Green Peaking Station | 811 East Poe Road | Bowling Green | 43402 |  | Wood | P001 | 422.57 mmBtu/hour natural gas-fired turbine: modification to correct the emission limitations | 2013-08-08 | Water injection | Grace Consulting, Inc. | 422.57 MMBtu/hr | 71.2 lbs/hr | 305.6 MMBtu/hr | 51.82 lbs/hr | 7E | Nitrogen Dioxide | PASS | NA | N | Low process weight rate determination made by Mohammad Smidi.
2014 | 2082 | 0661005010 | E2 Appalachian Compression LLC - Upper Hill | Opossum Run Rd and Town Hwy 120 | Sarahsville | 43779 |  | Noble | P009 | 1,680 Hp. Waukesha (L7044GSI) natural gas-fired, rich burn, turbocharged, with oxidation catalyst, compressor engine. | 2014-07-15 | C-9(Catalytic Converter): Engine Catalyst | E2 Energy Services | 1,680 Hp | 0.99 lb/hr | 1,545 Hp | 0.02 lb/hr | 7E | Nitrogen Dioxide | PASS | NA | Y
2014 | 2086 | 0661005010 | E2 Appalachian Compression LLC - Upper Hill | Opossum Run Rd and Town Hwy 120 | Sarahsville | 43779 |  | Noble | P007 | 1,680 Hp. Waukesha (L7044GSI) natural gas-fired, rich burn, turbocharged, with oxidation catalyst, compressor engine. | 2014-11-06 | C-7(Catalytic Converter): Engine Catalyst; C-8(Catalytic Converter): Engine Catalyst; C-9(Catalytic Converter): Engine Catalyst | E2 Energy Services | 1680 Hp | 0.99 lb/hr | 1528 Hp | 0.42 lb/hr | 7E | Nitrogen Dioxide | PASS | NA | Y | Method 7 E not used. Method 3A and ASTM 6348-03 used
2014 | 2089 | 0661005010 | E2 Appalachian Compression LLC - Upper Hill | Opossum Run Rd and Town Hwy 120 | Sarahsville | 43779 |  | Noble | P008 | 1,680 Hp. Waukesha (L7044GSI) natural gas-fired, rich burn, turbocharged, with oxidation catalyst, compressor engine. | 2014-11-06 | C-7(Catalytic Converter): Engine Catalyst; C-8(Catalytic Converter): Engine Catalyst; C-9(Catalytic Converter): Engine Catalyst | E2 Energy Services | 1680 Hp | 0.99 lb/hr | 1221 Hp | 0.23 lb/hr | 7E | Nitrogen Dioxide | PASS | NA | Y | Method 7 E not used. Method 3A and ASTM 6348-03 used
2014 | 2091 | 0661005010 | E2 Appalachian Compression LLC - Upper Hill | Opossum Run Rd and Town Hwy 120 | Sarahsville | 43779 |  | Noble | P009 | 1,680 Hp. Waukesha (L7044GSI) natural gas-fired, rich burn, turbocharged, with oxidation catalyst, compressor engine. | 2014-11-06 | C-7(Catalytic Converter): Engine Catalyst; C-8(Catalytic Converter): Engine Catalyst; C-9(Catalytic Converter): Engine Catalyst | E2 Energy Services | 1680 Hp | 0.99 lb/hr | 1585 Hp | 0.22 lb/hr | 7E | Nitrogen Dioxide | PASS | NA | Y | Method 7 E not used. Method 3A and ASTM 6348-03 used
2014 | 2095 | 0661005010 | E2 Appalachian Compression LLC - Upper Hill | Opossum Run Rd and Town Hwy 120 | Sarahsville | 43779 |  | Noble | P004 | 1,680 Hp. Waukesha (L7044GSI) natural gas-fired, rich burn, turbocharged, with oxidation catalyst, compressor engine. | 2014-11-10 | C-4(Catalytic Converter): Engine Catalyst | E2 Energy Services | 1680 Hp | 0.99 lb/hr | 1547 Hp | 2.68 lb/hr | 7E | Nitrogen Dioxide | FAIL | NA | Y | Method 7E not used. Method 3a and ASTM 6348-03 used
2014 | 2099 | 0661005010 | E2 Appalachian Compression LLC - Upper Hill | Opossum Run Rd and Town Hwy 120 | Sarahsville | 43779 |  | Noble | P002 | 1,680 Hp. Waukesha (L7044GSI) natural gas-fired, rich burn, turbocharged, with oxidation catalyst, compressor engine. | 2014-11-12 | C-2(Catalytic Converter): Engine Catalyst; C-3(Catalytic Converter): Engine Catalyst | E2 Energy Services | 1680 Hp | 0.99 lb/hr | 1575 Hp | 0.46 lb/hr | 7E | Nitrogen Dioxide | PASS | NA | Y | Method 7E not used. Method 3A and ASTM 6348-03 used
2014 | 2101 | 0661005010 | E2 Appalachian Compression LLC - Upper Hill | Opossum Run Rd and Town Hwy 120 | Sarahsville | 43779 |  | Noble | P003 | 1,680 Hp. Waukesha (L7044GSI) natural gas-fired, rich burn, turbocharged, with oxidation catalyst, compressor engine. | 2014-11-12 | C-2(Catalytic Converter): Engine Catalyst; C-3(Catalytic Converter): Engine Catalyst | E2 Energy Services | 1680 Hp | 0.99 lb/hr | 1512 Hp | 0.80 lb/hr | 7E | Nitrogen Dioxide | PASS | NA | Y | Method 7E not used. Method 3A and ASTM 6348-03 used
2014 | 2105 | 0661005010 | E2 Appalachian Compression LLC - Upper Hill | Opossum Run Rd and Town Hwy 120 | Sarahsville | 43779 |  | Noble | P002 | 1,680 Hp. Waukesha (L7044GSI) natural gas-fired, rich burn, turbocharged, with oxidation catalyst, compressor engine. | 2014-11-13 | C-2(Catalytic Converter): Engine Catalyst; C-3(Catalytic Converter): Engine Catalyst | E2 Energy Services | 1680 Hp | 0.99 lb/hr | 1575 Hp | 0.46 lb/hr | 7E | Nitrogen Dioxide | PASS | NA | Y | Method 7E not used. Method 3A and ASTM 6348-03 used
2014 | 2107 | 0661005010 | E2 Appalachian Compression LLC - Upper Hill | Opossum Run Rd and Town Hwy 120 | Sarahsville | 43779 |  | Noble | P003 | 1,680 Hp. Waukesha (L7044GSI) natural gas-fired, rich burn, turbocharged, with oxidation catalyst, compressor engine. | 2014-11-13 | C-2(Catalytic Converter): Engine Catalyst; C-3(Catalytic Converter): Engine Catalyst | E2 Energy Services | 1680 Hp | 0.99 lb/hr | 1512 Hp | 0.80 lb/hr | 7E | Nitrogen Dioxide | PASS | NA | Y | Method 7E not used. Method 3A and ASTM 6348-03 used
2014 | 2689 | 1483060328 | Texas Eastern Transmission - Lebanon | 1157 State Road 122 West | Lebanon | 45036 |  | Warren | P001 | 67.98 MMBtu natural gas fired turbine used for natural gas compression | 2014-04-29 | LOW NOX LEAN AIR COMBUSTOR | Nordon Corporation | 57.84 MMBtu/hr | 40 ppmvd @ 15% O2 9.0 lbs/hr | Memo | Memo | 7E | Nitrogen Oxide | PASS | NA | Y | Test Report ID = 83160 Testing to comply with 40 CFR Part 60 Subpart GG LOAD CONDITIONS: NOX EMISSIONS MMBtu/hr LB/HR PPMVD @ 15% O2 LOAD 98.7% 49.81 1.6 9.0 LOAD 97.0% 46.78 1.6 9.0 LOAD 95.0% 44.13 1.5 9.0 LOAD 92.0% 42.73 1.4 9.0
2014 | 2690 | 1483060328 | Texas Eastern Transmission - Lebanon | 1157 State Road 122 West | Lebanon | 45036 |  | Warren | P001 | 67.98 MMBtu natural gas fired turbine used for natural gas compression | 2014-04-29 | LOW NOX LEAN AIR COMBUSTOR | Nordon Corporation | 57.84 MMBtu/hr | 40 ppmvd @ 15% O2 9.0 lbs/hr | Memo | Memo | 7E | Nitrogen Dioxide | PASS | NA | Y | Test Report ID = 83160 Testing to comply with 40 CFR Part 60 Subpart GG LOAD CONDITIONS: NOX EMISSIONS MMBtu/hr LB/HR PPMVD @ 15% O2 LOAD 98.7% 49.81 1.6 9.0 LOAD 97.0% 46.78 1.6 9.0 LOAD 95.0% 44.13 1.5 9.0 LOAD 92.0% 42.73 1.4 9.0
2015 | 890 | 0661005027 | E2 Appalachian LLC - Batesville | 58380 St John Rd | Quaker City | 43773 |  | Noble | P001 | 1,680 Hp. Waukesha (L7044GSI) natural gas-fired, rich burn, turbocharged, with oxidation catalyst, compressor engine | 2015-01-26 | C2701C(Catalytic Converter): Engine Catalyst | E2 Energy Services | 1680 hp | 1.0 g/hp-hr | 1400 hp | 0.17 g/hp-hr | 6348 03 | NOx - Nitrogen Oxides | PP | NA | Y
2015 | 893 | 0661005027 | E2 Appalachian LLC - Batesville | 58380 St John Rd | Quaker City | 43773 |  | Noble | P002 | 1,680 Hp. Waukesha (L7044GSI) natural gas-fired, rich burn, turbocharged, with oxidation catalyst, compressor engine | 2015-01-26 | C2701C(Catalytic Converter): Engine Catalyst | E2 Energy Services | 1680 hp | 1.0 g/hp-hr | 1361 hp | 0.13 g/hp-hr | 6348 03 | NOx - Nitrogen Oxides | PP | NA | Y
2015 | 897 | 0661005027 | E2 Appalachian LLC - Batesville | 58380 St John Rd | Quaker City | 43773 |  | Noble | P003 | 1,680 Hp. Waukesha (L7044GSI) natural gas-fired, rich burn, turbocharged, with oxidation catalyst, compressor engine | 2015-01-27 | C2701C(Catalytic Converter): Engine Catalyst | E2 Energy Services | 1680 hp | 1.0 g/hp-hr | 1277 hp | 0.16 g/hp-hr | 6348 03 | NOx - Nitrogen Oxides | PP | NA | Y
2015 | 899 | 0661005027 | E2 Appalachian LLC - Batesville | 58380 St John Rd | Quaker City | 43773 |  | Noble | P007 | 1,680 Hp. Waukesha (L7044GSI) natural gas-fired, rich burn, turbocharged, with oxidation catalyst, compressor engine | 2015-02-19 | C2707C(Catalytic Converter): Engine Catalyst | E2 Energy Services | 1,680 hp | 1.0 g/hp-hr | 1,512 hp | 0.20 g/hp-hr | 6348 03 | NOx - Nitrogen Oxides | PP | NA | Y
2015 | 903 | 0661005027 | E2 Appalachian LLC - Batesville | 58380 St John Rd | Quaker City | 43773 |  | Noble | P008 | 1,680 Hp. Waukesha (L7044GSI) natural gas-fired, rich burn, turbocharged, with oxidation catalyst, compressor engine | 2015-02-19 | C2708C(Catalytic Converter): Engine Catalyst | E2 Energy Services | 1,680 hp | 1.0 g/hp-hr | 1,512 hp | 0.20 g/hp-hr | 6348 03 | NOx - Nitrogen Oxides | PP | NA | Y
2015 | 905 | 0661005027 | E2 Appalachian LLC - Batesville | 58380 St John Rd | Quaker City | 43773 |  | Noble | P004 | 1,680 Hp. Waukesha (L7044GSI) natural gas-fired, rich burn, turbocharged, with oxidation catalyst, compressor engine | 2015-02-20 | C2704C(Catalytic Converter): Engine Catalyst | E2 Energy Services | 1,680 hp | 1.0 g/hp-hr | 1,510 hp | 0.14 g/hp-hr | 6348 03 | NOx - Nitrogen Oxides | PP | NA | Y
2015 | 908 | 0661005027 | E2 Appalachian LLC - Batesville | 58380 St John Rd | Quaker City | 43773 |  | Noble | P005 | 1,680 Hp. Waukesha (L7044GSI) natural gas-fired, rich burn, turbocharged, with oxidation catalyst, compressor engine | 2015-02-27 | C2705C(Catalytic Converter): Engine Catalyst | E2 Energy Services | 1,680 hp | 1.0 g/hp-hr | 1,295 hp | 0.20 g/hp-hr | 6348 03 | NOx - Nitrogen Oxides | PP | NA | Y
2016 | 1144 | 0607005013 | Texas Eastern Transmission LP - Colerain | 72784 Colerain-Mt. Pleasant Rd | Colerain Twp. | 43916 |  | Belmont | P001 | turbine | 2016-04-13 | TBC-01(Other): oxidation catalyst; TBC-02(Other): oxidation catalyst | Nordon Corp. | 10,915 hp | 15 ppm | 10,584 hp | 10 ppm | 7E | Nitrogen Dioxide | PP | Y | NA
2016 | 1145 | 0607005013 | Texas Eastern Transmission LP - Colerain | 72784 Colerain-Mt. Pleasant Rd | Colerain Twp. | 43916 |  | Belmont | P002 | turbine | 2016-04-13 | TBC-01(Other): oxidation catalyst; TBC-02(Other): oxidation catalyst | Nordon Corp. | 10,915 hp | 15 ppm | 10,889 hp | 11 ppm | 7E | Nitrogen Dioxide | PP | Y | NA
2016 | 1262 | 0630005041 | E2 Energy Services - Borton | 65483 Lydick Rd | Quaker City | 43773 |  | Guernsey | P002 | 1,680 Hp. Waukesha (L7044GSI) natural gas-fired, rich burn, turbocharged, with oxidation catalyst, compressor engine (Model Year 2014) | 2016-03-02 | C-2701C(Catalytic Converter): Engine Catalyst | E2 Energy Services | 1680 hp | 0.28 g/hp-hr | 1519 hp | 0.14 g/hp-hr | 6348 03 | NOx - Nitrogen Oxides | PP | N | NA
2016 | 1266 | 0630005041 | E2 Energy Services - Borton | 65483 Lydick Rd | Quaker City | 43773 |  | Guernsey | P004 | 1,680 Hp. Waukesha (L7044GSI) natural gas-fired, rich burn, turbocharged, with oxidation catalyst, compressor engine (Model Year 2014) | 2016-05-12 | C-2703C(Catalytic Converter): Engine Catalyst | E2 Energy Services | 1680 hp | 0.28 g/hp-hr | 1348 hp | 0.278 g/hp-hr | 6348 03 | NOx - Nitrogen Oxides | PP | Y | NA
2016 | 1603 | 0661005010 | E2 Appalachian Compression LLC - Upper Hill | Opossum Run Rd and Town Hwy 120 | Sarahsville | 43779 |  | Noble | P003 | 1,680 Hp. Waukesha (L7044GSI) natural gas-fired, rich burn, turbocharged, with oxidation catalyst, compressor engine. | 2016-04-29 | C-3(Catalytic Converter): Engine Catalyst; C-9(Catalytic Converter): Engine Catalyst | Alliance Source Testing | 1680 hp | 2.0 g/hp-hr | 1658 hp | 3.19 g/hp-hr | 7E | Nitrogen Dioxide | FF | Y | NA
2016 | 1604 | 0661005010 | E2 Appalachian Compression LLC - Upper Hill | Opossum Run Rd and Town Hwy 120 | Sarahsville | 43779 |  | Noble | P009 | 1,680 Hp. Waukesha (L7044GSI) natural gas-fired, rich burn, turbocharged, with oxidation catalyst, compressor engine. | 2016-04-29 | C-3(Catalytic Converter): Engine Catalyst; C-9(Catalytic Converter): Engine Catalyst | Alliance Source Testing | 1680 hp | 2.0 g/hp-hr | 1646 hp | 0.15 g/hp-hr | 7E | Nitrogen Dioxide | PP | Y | NA
2016 | 1609 | 0661005010 | E2 Appalachian Compression LLC - Upper Hill | Opossum Run Rd and Town Hwy 120 | Sarahsville | 43779 |  | Noble | P007 | 1,680 Hp. Waukesha (L7044GSI) natural gas-fired, rich burn, turbocharged, with oxidation catalyst, compressor engine. | 2016-03-17 | C-7(Catalytic Converter): Engine Catalyst; C-8(Catalytic Converter): Engine Catalyst | Alliance Source Testing | 1680 hp | 2.0 g/hp-hr | 1464 hp | 0.22 g/hp-hr | 7E | Nitrogen Dioxide | PP | Y | NA
2016 | 1610 | 0661005010 | E2 Appalachian Compression LLC - Upper Hill | Opossum Run Rd and Town Hwy 120 | Sarahsville | 43779 |  | Noble | P008 | 1,680 Hp. Waukesha (L7044GSI) natural gas-fired, rich burn, turbocharged, with oxidation catalyst, compressor engine. | 2016-03-17 | C-7(Catalytic Converter): Engine Catalyst; C-8(Catalytic Converter): Engine Catalyst | Alliance Source Testing | 1680 hp | 2.0 g/hp-hr | 1406 hp | 0.42 g/hp-hr | 7E | Nitrogen Dioxide | PP | Y | NA
2016 | 1615 | 0661005010 | E2 Appalachian Compression LLC - Upper Hill | Opossum Run Rd and Town Hwy 120 | Sarahsville | 43779 |  | Noble | P003 | 1,680 Hp. Waukesha (L7044GSI) natural gas-fired, rich burn, turbocharged, with oxidation catalyst, compressor engine. | 2016-04-29 | C-3(Catalytic Converter): Engine Catalyst; C-9(Catalytic Converter): Engine Catalyst | Ecotest Energy Services | 1680 hp | 2.0 g/hp-hr | 1658 hp | 3.19 g/hp-hr | 6348 03 | NOx - Nitrogen Oxides | FF | Y | NA
2016 | 1620 | 0661005010 | E2 Appalachian Compression LLC - Upper Hill | Opossum Run Rd and Town Hwy 120 | Sarahsville | 43779 |  | Noble | P009 | 1,680 Hp. Waukesha (L7044GSI) natural gas-fired, rich burn, turbocharged, with oxidation catalyst, compressor engine. | 2016-04-29 | C-3(Catalytic Converter): Engine Catalyst; C-9(Catalytic Converter): Engine Catalyst | Ecotest Energy Services | 1680 hp | 2.0 g/hp-hr | 1646 hp | 0.15 g/hp-hr | 6348 03 | NOx - Nitrogen Oxides | PP | Y | NA
2016 | 1621 | 0661005010 | E2 Appalachian Compression LLC - Upper Hill | Opossum Run Rd and Town Hwy 120 | Sarahsville | 43779 |  | Noble | P002 | 1,680 Hp. Waukesha (L7044GSI) natural gas-fired, rich burn, turbocharged, with oxidation catalyst, compressor engine. | 2016-07-13 | C-2(Catalytic Converter): Engine Catalyst; C-8(Catalytic Converter): Engine Catalyst | Alliance Source Testing | 1,680 hp | 160 ppm | 1,529 hp | 7.0 ppm | 7E | Nitrogen Dioxide | PP | Y | NA
2016 | 1622 | 0661005010 | E2 Appalachian Compression LLC - Upper Hill | Opossum Run Rd and Town Hwy 120 | Sarahsville | 43779 |  | Noble | P008 | 1,680 Hp. Waukesha (L7044GSI) natural gas-fired, rich burn, turbocharged, with oxidation catalyst, compressor engine. | 2016-07-13 | C-2(Catalytic Converter): Engine Catalyst; C-8(Catalytic Converter): Engine Catalyst | Alliance Source Testing | 1,680 hp | 160 ppm | 1,528 hp | 4.3 ppm | 7E | Nitrogen Dioxide | PP | Y | NA
2016 | 1629 | 0661005027 | E2 Appalachian LLC - Batesville | 58380 St John Rd | Quaker City | 43773 |  | Noble | P001 | 1,680 Hp. Waukesha (L7044GSI) natural gas-fired, rich burn, turbocharged, with oxidation catalyst, compressor engine | 2016-04-13 | C2701C(Catalytic Converter): Engine Catalyst | E2 Appalachian | 1680 hp | 1.0 g/hp-hr | 1539 hp | 0.278 g/hp-hr | 6348 03 | NOx - Nitrogen Oxides | PP | Y | NA
2016 | 1631 | 0661005027 | E2 Appalachian LLC - Batesville | 58380 St John Rd | Quaker City | 43773 |  | Noble | P002 | 1,680 Hp. Waukesha (L7044GSI) natural gas-fired, rich burn, turbocharged, with oxidation catalyst, compressor engine | 2016-03-24 | C2702C(Catalytic Converter): Engine Catalyst | E2 Appalachian | 1680 hp | 1.0 g/hp-hr | 1473 hp | 0.1360 g/hp-hr | 6348 03 | NOx - Nitrogen Oxides | PP | Y | NA
2016 | 1634 | 0661005027 | E2 Appalachian LLC - Batesville | 58380 St John Rd | Quaker City | 43773 |  | Noble | P003 | 1,680 Hp. Waukesha (L7044GSI) natural gas-fired, rich burn, turbocharged, with oxidation catalyst, compressor engine | 2016-03-23 | C2703C(Catalytic Converter): Engine Catalyst | E2 Appalachian | 1680 hp | 1.0 g/hp-hr | 1348 hp | 0.0882 g/hp-hr | 6348 03 | NOx - Nitrogen Oxides | PP | Y | NA
2016 | 1638 | 0661005027 | E2 Appalachian LLC - Batesville | 58380 St John Rd | Quaker City | 43773 |  | Noble | P004 | 1,680 Hp. Waukesha (L7044GSI) natural gas-fired, rich burn, turbocharged, with oxidation catalyst, compressor engine | 2016-03-30 | C2704C(Catalytic Converter): Engine Catalyst | E2 Appalachian | 1680 hp | 1.0 g/hp-hr | 1470 hp | 0.1056 g/hp-hr | 6348 03 | NOx - Nitrogen Oxides | PP | Y | NA
2016 | 1639 | 0661005027 | E2 Appalachian LLC - Batesville | 58380 St John Rd | Quaker City | 43773 |  | Noble | P005 | 1,680 Hp. Waukesha (L7044GSI) natural gas-fired, rich burn, turbocharged, with oxidation catalyst, compressor engine | 2016-03-31 | C2705C(Catalytic Converter): Engine Catalyst | E2 Appalachian | 1680 hp | 1.0 g/hp-hr | 1425 hp | 0.1406 g/hp-hr | 6348 03 | NOx - Nitrogen Oxides | PP | Y | NA
2016 | 1643 | 0661005027 | E2 Appalachian LLC - Batesville | 58380 St John Rd | Quaker City | 43773 |  | Noble | P006 | 1,680 Hp. Waukesha (L7044GSI) natural gas-fired, rich burn, turbocharged, with oxidation catalyst, compressor engine | 2016-04-01 | C2705C(Catalytic Converter): Engine Catalyst | E2 Appalachian | 1680 hp | 0.268 g/hp-hr | 1551 hp | 0.3119 g/hp-hr | 6348 03 | NOx - Nitrogen Oxides | FF | Y | NA
2016 | 1645 | 0661005027 | E2 Appalachian LLC - Batesville | 58380 St John Rd | Quaker City | 43773 |  | Noble | P008 | 1,680 Hp. Waukesha (L7044GSI) natural gas-fired, rich burn, turbocharged, with oxidation catalyst, compressor engine | 2016-04-14 | C2708C(Catalytic Converter): Engine Catalyst | E2 Appalachian | 1680 hp | 1.0 g/hp-hr | 1475 hp | 0.1731 g/hp-hr | 6348 03 | NOx - Nitrogen Oxides | PP | Y | NA
2016 | 1649 | 0661005027 | E2 Appalachian LLC - Batesville | 58380 St John Rd | Quaker City | 43773 |  | Noble | P002 | 1,680 Hp. Waukesha (L7044GSI) natural gas-fired, rich burn, turbocharged, with oxidation catalyst, compressor engine | 2016-04-14 | C2702C(Catalytic Converter): Engine Catalyst | E2 Energy Services | 1680 hp | 1.0 g/hp-hr | 1473 hp | 0.122 g/hp-hr | 6348 03 | NOx - Nitrogen Oxides | PP | N | NA
2016 | 1651 | 0661005027 | E2 Appalachian LLC - Batesville | 58380 St John Rd | Quaker City | 43773 |  | Noble | P002 | 1,680 Hp. Waukesha (L7044GSI) natural gas-fired, rich burn, turbocharged, with oxidation catalyst, compressor engine | 2016-04-28 | C2702C(Catalytic Converter): Engine Catalyst | Alliance Source Testing | 1680 hp | 1.0 g/hp-hr | 1529 hp | 0.129 g/hp-hr | 7E | Nitrogen Dioxide | PP | N | NA
2016 | 1654 | 0661005027 | E2 Appalachian LLC - Batesville | 58380 St John Rd | Quaker City | 43773 |  | Noble | P001 | 1,680 Hp. Waukesha (L7044GSI) natural gas-fired, rich burn, turbocharged, with oxidation catalyst, compressor engine | 2016-07-11 | C2701C(Catalytic Converter): Engine Catalyst; C2707C(Catalytic Converter): Engine Catalyst; C2708C(Catalytic Converter): Engine Catalyst | Alliance Source Testing | 1,680 hp | 1.0 g/hp-hr | 1,529 hp | 0 g/hp-hr | 7E | Nitrogen Dioxide | PP | Y | NA
2016 | 1655 | 0661005027 | E2 Appalachian LLC - Batesville | 58380 St John Rd | Quaker City | 43773 |  | Noble | P007 | 1,680 Hp. Waukesha (L7044GSI) natural gas-fired, rich burn, turbocharged, with oxidation catalyst, compressor engine | 2016-07-11 | C2701C(Catalytic Converter): Engine Catalyst; C2707C(Catalytic Converter): Engine Catalyst; C2708C(Catalytic Converter): Engine Catalyst | Alliance Source Testing | 1,680 hp | 1.0 g/hp-hr | 1,607 hp | 0.134 g/hp-hr | 7E | Nitrogen Dioxide | PP | Y | NA
2016 | 1656 | 0661005027 | E2 Appalachian LLC - Batesville | 58380 St John Rd | Quaker City | 43773 |  | Noble | P008 | 1,680 Hp. Waukesha (L7044GSI) natural gas-fired, rich burn, turbocharged, with oxidation catalyst, compressor engine | 2016-07-11 | C2701C(Catalytic Converter): Engine Catalyst; C2707C(Catalytic Converter): Engine Catalyst; C2708C(Catalytic Converter): Engine Catalyst | Alliance Source Testing | 1,680 hp | 1.0 g/hp-hr | 1,568 hp | 0.212 g/hp-hr | 7E | Nitrogen Dioxide | PP | Y | NA
2016 | 1663 | 0661005027 | E2 Appalachian LLC - Batesville | 58380 St John Rd | Quaker City | 43773 |  | Noble | P006 | 1,680 Hp. Waukesha (L7044GSI) natural gas-fired, rich burn, turbocharged, with oxidation catalyst, compressor engine | 2016-07-12 | C2706C(Catalytic Converter): Engine Catalyst | Alliance Source Testing | 1,680 hp | 0.268 g/hp-hr | 1,490 hp | 0.037 g/hp-hr | 7E | Nitrogen Dioxide | PP | Y | NA
2016 | 1799 | 0744000150 | Hanging Rock Energy Facility | 1395 County Rd 1A | Ironton | 45638 |  | Lawrence | P001 | GE 7FA natural gas fired dry low NOx (DLN) combustion turbine No. 1, nominally rated at 2,045 MMBtu/hr, with duct burner nominally rated at 587MMBtu/hr operating in combined cycle mode controlled by Selective Calalytic Reduction (SCR) | 2016-04-07 | SCR - 1GT1(Other): Min temp - 525 F; SCR - 1GT2(Other): Min temp - 525 F; SCR - 2GT1(Other): Min temp - 525 F; SCR - 2GT2(Other): Min temp - 525 F | Mostardi Platt | 2,632 MMbtu/hr with Duct burners operating | Duct burners operating 28.7 lb/hr/2.9 ppmvd 15%O | 2,436 MMbtu/hr avg | 25.03 lb/hr and 2.7 ppmvd at 15% O2 | 7E | Nitrogen Oxide | PP | Y | NA | These tests were conducted with DUCT BURNERS OPERATING
2016 | 1800 | 0744000150 | Hanging Rock Energy Facility | 1395 County Rd 1A | Ironton | 45638 |  | Lawrence | P002 | GE 7FA natural gas fired dry low NOx (DLN) combustion turbine No. 2, nominally rated at 2,045 MMBtu/hr, with duct burner nominally rated at 587 MMBtu/hr operating in combined cycle mode controlled by Selective Calalytic Reduction (SCR) | 2016-04-07 | SCR - 1GT1(Other): Min temp - 525 F; SCR - 1GT2(Other): Min temp - 525 F; SCR - 2GT1(Other): Min temp - 525 F; SCR - 2GT2(Other): Min temp - 525 F | Mostardi Platt | 2,632 MMbtu/hr with Duct burners operating | Duct burners operating 28.7 lb/hr/2.9 ppmvd 15%O | 2,370.1 MMbtu/hr avg | 23.61 lb/hr and 2.6 ppmvd at 15% O2 | 7E | Nitrogen Oxide | PP | Y | NA | These tests were conducted with DUCT BURNERS OPERATING
2016 | 1801 | 0744000150 | Hanging Rock Energy Facility | 1395 County Rd 1A | Ironton | 45638 |  | Lawrence | P003 | GE 7FA natural gas fired dry low NOx (DLN) combustion turbine No. 3, nominally rated at 2,045 MMBtu/hr, with duct burner nominally rated at 587 MMBtu/hr operating in combined cycle mode controlled by Selective Calalytic Reduction (SCR) | 2016-04-07 | SCR - 1GT1(Other): Min temp - 525 F; SCR - 1GT2(Other): Min temp - 525 F; SCR - 2GT1(Other): Min temp - 525 F; SCR - 2GT2(Other): Min temp - 525 F | Mostardi Platt | 2,632 MMbtu/hr with Duct burners operating | Duct burners operating 28.7 lb/hr/2.9 ppmvd 15%O | 2,377.8 MMbtu/hr avg | 23.62 lb/hr and 2.7 ppmvd at 15% O2 | 7E | Nitrogen Oxide | PP | Y | NA | These tests were conducted with DUCT BURNERS OPERATING
2016 | 1802 | 0744000150 | Hanging Rock Energy Facility | 1395 County Rd 1A | Ironton | 45638 |  | Lawrence | P004 | GE 7FA natural gas fired dry low NOx (DLN) combustion turbine No. 4, nominally rated at 2,045 MMBtu/hr, with duct burner nominally rated at 587 MMBtu/hr operating in combined cycle mode controlled by Selective Calalytic Reduction (SCR) | 2016-04-07 | SCR - 1GT1(Other): Min temp - 525 F; SCR - 1GT2(Other): Min temp - 525 F; SCR - 2GT1(Other): Min temp - 525 F; SCR - 2GT2(Other): Min temp - 525 F | Mostardi Platt | 2,632 MMbtu/hr with Duct burners operating | Duct burners operating 28.7 lb/hr/2.9 ppmvd 15%O | 2,342.7 MMbtu/hr avg | 25.17 lb/hr and 2.9 ppmvd at 15% O2 | 7E | Nitrogen Oxide | PP | Y | NA | These tests were conducted with DUCT BURNERS OPERATING
2016 | 1820 | 0744000150 | Hanging Rock Energy Facility | 1395 County Rd 1A | Ironton | 45638 |  | Lawrence | P001 | GE 7FA natural gas fired dry low NOx (DLN) combustion turbine No. 1, nominally rated at 2,045 MMBtu/hr, with duct burner nominally rated at 587MMBtu/hr operating in combined cycle mode controlled by Selective Calalytic Reduction (SCR) | 2016-04-08 | SCR - 1GT1(Other): Min temp - 525 F; SCR - 1GT2(Other): Min temp - 525 F; SCR - 2GT1(Other): Min temp - 525 F; SCR - 2GT2(Other): Min temp - 525 F | Mostardi Platt | 2,045 MMbtu/hr without Duct burners operating | Without Duct burners 22.3 lb/hr/2.9 ppmvd 15%O | 1,967.2 MMbtu/hr avg | 16.13 lb/hr and 2.5 ppmvd at 15% O2 | 7E | Nitrogen Oxide | PP | Y | NA | These tests were conducted WITHOUT duct burners operating
2016 | 1821 | 0744000150 | Hanging Rock Energy Facility | 1395 County Rd 1A | Ironton | 45638 |  | Lawrence | P002 | GE 7FA natural gas fired dry low NOx (DLN) combustion turbine No. 2, nominally rated at 2,045 MMBtu/hr, with duct burner nominally rated at 587 MMBtu/hr operating in combined cycle mode controlled by Selective Calalytic Reduction (SCR) | 2016-04-08 | SCR - 1GT1(Other): Min temp - 525 F; SCR - 1GT2(Other): Min temp - 525 F; SCR - 2GT1(Other): Min temp - 525 F; SCR - 2GT2(Other): Min temp - 525 F | Mostardi Platt | 2,045 MMbtu/hr without Duct burners operating | Without Duct burners 22.3 lb/hr/2.9 ppmvd 15%O | 1,967.2 MMbtu/hr avg | 16.58 lb/hr and 2.4 ppmvd at 15% O2 | 7E | Nitrogen Oxide | PP | Y | NA | These tests were conducted WITHOUT duct burners operating
2016 | 1822 | 0744000150 | Hanging Rock Energy Facility | 1395 County Rd 1A | Ironton | 45638 |  | Lawrence | P003 | GE 7FA natural gas fired dry low NOx (DLN) combustion turbine No. 3, nominally rated at 2,045 MMBtu/hr, with duct burner nominally rated at 587 MMBtu/hr operating in combined cycle mode controlled by Selective Calalytic Reduction (SCR) | 2016-04-08 | SCR - 1GT1(Other): Min temp - 525 F; SCR - 1GT2(Other): Min temp - 525 F; SCR - 2GT1(Other): Min temp - 525 F; SCR - 2GT2(Other): Min temp - 525 F | Mostardi Platt | 2,045 MMbtu/hr without Duct burners operating | Without Duct burners 22.3 lb/hr/2.9 ppmvd 15%O | 1,945.2MMbtu/hr avg | 18.55 lb/hr and 2.6 ppmvd at 15% O2 | 7E | Nitrogen Oxide | PP | Y | NA | These tests were conducted WITHOUT duct burners operating
2016 | 1823 | 0744000150 | Hanging Rock Energy Facility | 1395 County Rd 1A | Ironton | 45638 |  | Lawrence | P004 | GE 7FA natural gas fired dry low NOx (DLN) combustion turbine No. 4, nominally rated at 2,045 MMBtu/hr, with duct burner nominally rated at 587 MMBtu/hr operating in combined cycle mode controlled by Selective Calalytic Reduction (SCR) | 2016-04-08 | SCR - 1GT1(Other): Min temp - 525 F; SCR - 1GT2(Other): Min temp - 525 F; SCR - 2GT1(Other): Min temp - 525 F; SCR - 2GT2(Other): Min temp - 525 F | Mostardi Platt | 2,045 MMbtu/hr without Duct burners operating | Without Duct burners 22.3 lb/hr/2.9 ppmvd 15%O | 1,908.2 MMbtu/hr avg | 17.93 lb/hr and 2.7 ppmvd at 15% O2 | 7E | Nitrogen Oxide | PP | Y | NA | These tests were conducted WITHOUT duct burners operating
2016 | 2209 | 1409120656 | Duke Energy Kentucky, Woodsdale Generating Station | 2100 Woodsdale Road | Trenton | 45067 | 0000 | Butler | B001 | 1034 MMBtu/Hr simple cycle combustion turbine w/ low NOx burner and water injection | 2016-11-16 | CT1 Water Injection(Other): 42-65 ppmdv @ 15% O2 | Mostardi PLatt | See memo field | See memo field | See memo field | See memo field | 7E | Nitrogen Oxide | PP | Y | NA | Load Condition MW LB/MMBTU PPM @ 15% O2 Low 6 0.069 18.70 Low/Mild 34 0.068 18.39 Mild/High 61 0.094 25.22 High 86
2016 | 2339 | 1483060328 | Texas Eastern Transmission - Lebanon | 1157 State Road 122 West | Lebanon | 45036 |  | Warren | P006 | Solar Taurus, 68.34 MMBtu/hr (ISO conditions), natural gas-fired turbine used for natural gas compression | 2016-02-11 | LOW NOX LEAN AIR COMBUSTOR | Nordon Corporation | 68.34 MMBtu/hr | 25 ppbv at 15% O2 | see memo field | see memo field | 7E | Nitrogen Oxide | PP | Y | NA | Witnessed by Stephanie Kuhn LOAD CONDITIONS: NOX EMISSIONS MMBtu/hr LB/HR PPMVD @ 15% O2 LOAD 99% 67.66 1.6 9.0 LOAD 97.0% 66.29
2016 | 2340 | 1483060328 | Texas Eastern Transmission - Lebanon | 1157 State Road 122 West | Lebanon | 45036 |  | Warren | P006 | Solar Taurus, 68.34 MMBtu/hr (ISO conditions), natural gas-fired turbine used for natural gas compression | 2016-02-11 | LOW NOX LEAN AIR COMBUSTOR | Nordon Corporation | 68.34 MMBtu/hr | 25 ppbv at 15% O2 | see memo field | see memo field | 7E | Nitrogen Dioxide | PP | Y | NA | Witnessed by Stephanie Kuhn LOAD CONDITIONS: NOX EMISSIONS MMBtu/hr LB/HR PPMVD @ 15% O2 LOAD 99% 67.66 1.6 9.0 LOAD 97.0% 66.29
2016 | 2341 | 1483060328 | Texas Eastern Transmission - Lebanon | 1157 State Road 122 West | Lebanon | 45036 |  | Warren | P006 | Solar Taurus, 68.34 MMBtu/hr (ISO conditions), natural gas-fired turbine used for natural gas compression | 2016-11-09 | P006 Ox Cat(Other): oxidation catalyst | Nordon Corporation | 68.34 MMBtu/hr | 25 ppmv @15% O2 | 61.345 MMBtu/hr | 8.25 ppmv @ 15% O2 | 7E | Nitrogen Oxide | PP | Y | NA | Stack Test Report - Compliance Report ID#130459 ITT - Compliance Report ID#129355 Permit - PTI P120361 1. An example calculation of EPA Method 4- moisture was not originally included in the emission compliance test report. The test report stated that EPA
2003 | 22 | 0682000057 | Rolling Hills Generating, LLC | 43111 State Route 160 | Wilkesville | 45695 |  | Vinton | P001 | Seimens Westinghouse Power Corp. W501F, natural gas fired turbine with dry low-NOx combusters, operating in simple cycle mode. | 2003-04-03 | scr | SOURCE TESTING CONSULTANT | 180 mw | 117 lb/hr | 173.9 mw | 82.8 lb/hr | 7 | Nitrogen Dioxide | PASS | NA | Y |  | Yes
2003 | 23 | 0682000057 | Rolling Hills Generating, LLC | 43111 State Route 160 | Wilkesville | 45695 |  | Vinton | P002 | Seimens Westinghouse Power Corp. W501F, natural gas fired turbine with dry low-NOx combusters, operating in simple cycle mode. | 2003-04-10 | scr | SOURCE TESTING CONSULTANT | 180 mw | 117 lb/hr | 185 mw | 86.1 lb/hr | 7 | Nitrogen Dioxide | PASS | NA | Y |  | Yes
2003 | 24 | 0682000057 | Rolling Hills Generating, LLC | 43111 State Route 160 | Wilkesville | 45695 |  | Vinton | P003 | Seimens Westinghouse Power Corp. W501F, natural gas fired turbine with dry low-NOx combusters, operating in simple cycle mode. | 2003-04-17 | scr | SOURCE TESTING CONSULTANT | 180 mw | 117 lb/hr | 174 mw | 84.5 lb/hr | 7 | Nitrogen Dioxide | PASS | NA | Y |  | Yes
2003 | 25 | 0682000057 | Rolling Hills Generating, LLC | 43111 State Route 160 | Wilkesville | 45695 |  | Vinton | P004 | Seimens Westinghouse Power Corp. W501F, natural gas fired turbine with dry low-NOx combusters, operating in simple cycle mode. | 2003-05-08 | scr | SOURCE TESTING CONSULTANT | 180 mw | 117 lb/hr | 175.8 mw | 78.3 lb/hr | 7 | Nitrogen Dioxide | PASS | NA | Y |  | Yes
2003 | 26 | 0682000057 | Rolling Hills Generating, LLC | 43111 State Route 160 | Wilkesville | 45695 |  | Vinton | P005 | Seimens Westinghouse Power Corp. W501F, natural gas fired turbine with dry-low-NOx combusters, operating in simple cycle mode. | 2003-05-17 | scr | SOURCE TESTING CONSULTANT | 180 mw | 117 lb/hr | 173 mw | 86.7 lb/hr | 7 | Nitrogen Dioxide | PASS | NA | Y |  | Yes
2003 | 27 | 0684000213 | AEP Generating Resources Inc., - Waterford Plant | 201 Righteous Ridge Road | Waterford | 45786 |  | Washington | P001 | GE 7FA Natural Gas Fired Dry Low NOx (DLN) Combustion Turbine - Modified | 2003-07-31 | scr, oxidation catalyst | FULLER AIR COMPLIANCE | 166 mw | 30 lb/hr | 160 mw | 22.2 lb/hr | 20 | Nitrogen Dioxide | PASS | NA | Y | Burner ON | Yes
2003 | 28 | 0684000213 | AEP Generating Resources Inc., - Waterford Plant | 201 Righteous Ridge Road | Waterford | 45786 |  | Washington | P001 | GE 7FA Natural Gas Fired Dry Low NOx (DLN) Combustion Turbine - Modified | 2003-08-01 | scr, oxidation catalyst | FULLER AIR COMPLIANCE | 166 mw | 25.0 lb/hr | 160 mw | 22.06 lb/hr | 20 | Nitrogen Dioxide | PASS | NA | Y | Burner OFF | Yes
2003 | 29 | 0684000213 | AEP Generating Resources Inc., - Waterford Plant | 201 Righteous Ridge Road | Waterford | 45786 |  | Washington | P002 | GE 7FA Natural Gas Fired Dry Low NOx (DLN) Combustion Turbine - Modified | 2003-08-04 | scr, oxidation catalyst | FULLER AIR COMPLIANCE | 166 mw | 30 lb/hr | 161 mw | 25.07 lb/hr | 20 | Nitrogen Dioxide | PASS | NA | Y | Burner ON | Yes
2003 | 30 | 0684000213 | AEP Generating Resources Inc., - Waterford Plant | 201 Righteous Ridge Road | Waterford | 45786 |  | Washington | P003 | GE 7FA Natural Gas Fired Dry Low NOx (DLN) Combustion Turbine - Modified | 2003-08-05 | scr, oxidation catalyst | FULLER AIR COMPLIANCE | 166 mw | 30 lb/hr | 160 mw | 27.42 lb/hr | 20 | Nitrogen Dioxide | PASS | NA | Y | Burner ON | Yes
2003 | 31 | 0684000213 | AEP Generating Resources Inc., - Waterford Plant | 201 Righteous Ridge Road | Waterford | 45786 |  | Washington | P003 | GE 7FA Natural Gas Fired Dry Low NOx (DLN) Combustion Turbine - Modified | 2003-08-06 | scr, oxidation catalyst | FULLER AIR COMPLIANCE | 166 mw | 25 lb/hr | 142 mw | 23.08 lb/hr | 20 | Nitrogen Dioxide | PASS | NA | Y | Burner OFF | Yes
2003 | 32 | 0684000213 | AEP Generating Resources Inc., - Waterford Plant | 201 Righteous Ridge Road | Waterford | 45786 |  | Washington | P002 | GE 7FA Natural Gas Fired Dry Low NOx (DLN) Combustion Turbine - Modified | 2003-08-07 | scr, oxidation catalyst | FULLER AIR COMPLIANCE | 166 mw | 25 lb/hr | 160 mw | 17 lb/hr | 20 | Nitrogen Dioxide | PASS | NA | Y | Burner OFF | Yes
2003 | 33 | 0744000150 | Hanging Rock Energy Facility | 1395 County Rd 1A | Ironton | 45638 |  | Lawrence | P001 | 172 MW GE 7FA natural gas fired dry low NOx (DLN) combustion turbine No. 1 with duct firing operating in combined cycle mode controlled by Selective Calalytic Reduction (SCR) | 2003-06-03 | scr | CUBIX CORPORATION | 172 mw at 59 deg f | 3.0 ppmv @15%o2 w/o duct firing | 160.1 mw | 2.9 ppmv | 7 | Nitrogen Dioxide | PASS | NA | Y |  | Yes
2003 | 34 | 0744000150 | Hanging Rock Energy Facility | 1395 County Rd 1A | Ironton | 45638 |  | Lawrence | P002 | 172 MW GE 7FA natural gas fired dry low NOx (DLN) combustion turbine No. 2 with duct firing operating in combined cycle mode controlled by Selective Catalytic Reduction (SCR) | 2003-06-03 | scr | CUBIX CORPORATION | 172 mw at 59 deg f | 27.8 lbs/hr(turbine + duct burners) | 162 mw | 18.58 lbs/hr (turbine + duct burner | 7 | Nitrogen Dioxide | PASS | NA | Y |  | Yes
2003 | 35 | 0744000150 | Hanging Rock Energy Facility | 1395 County Rd 1A | Ironton | 45638 |  | Lawrence | P001 | 172 MW GE 7FA natural gas fired dry low NOx (DLN) combustion turbine No. 1 with duct firing operating in combined cycle mode controlled by Selective Calalytic Reduction (SCR) | 2003-06-04 | scr | CUBIX CORPORATION | 172 mw at 59 deg f | 3 ppmvd(turbine + duct burners) | 163.5 mw | 2.9 ppmvd (turbine + duct burners) | 7 | Nitrogen Dioxide | PASS | NA | Y |  | Yes
2003 | 36 | 0744000150 | Hanging Rock Energy Facility | 1395 County Rd 1A | Ironton | 45638 |  | Lawrence | P002 | 172 MW GE 7FA natural gas fired dry low NOx (DLN) combustion turbine No. 2 with duct firing operating in combined cycle mode controlled by Selective Catalytic Reduction (SCR) | 2003-06-04 | scr | CUBIX CORPORATION | 172 mw at 59 deg f | 3.0 ppmv @15%o2 w/o duct burners | 164.5 mw | 2.4 ppmv @15% o2 w/o duct burners | 7 | Nitrogen Dioxide | PASS | NA | Y |  | Yes
2003 | 37 | 0744000150 | Hanging Rock Energy Facility | 1395 County Rd 1A | Ironton | 45638 |  | Lawrence | P003 | 172 MW GE 7FA natural gas fired dry low NOx (DLN) combustion turbine No. 3 with duct firing operating in combined cycle mode controlled by Selective Catalytic Reduction (SCR) | 2003-07-16 | scr | CUBIX CORPORATION | 172 mw at 59 deg f | 27.8 lbs/hr(turbine + duct burners) | 199 mw | 22.8 lbs/hr (turbine + duct burner | 7 | Nitrogen Dioxide | PASS | NA | Y |  | Yes
2003 | 38 | 0744000150 | Hanging Rock Energy Facility | 1395 County Rd 1A | Ironton | 45638 |  | Lawrence | P004 | 172 MW GE 7FA natural gas fired dry low NOx (DLN) combustion turbine No. 4 with duct firing operating in combined cycle mode controlled by Selective Catalytic Reduction (SCR) | 2003-07-16 | scr | CUBIX CORPORATION | 172 mw at 59 deg f | 3.0 ppmv @15%o2 w/o duct firing | 157 mw | 2.5 ppmv (turbine only) | 7 | Nitrogen Dioxide | PASS | NA | Y |  | Yes
2003 | 39 | 0744000150 | Hanging Rock Energy Facility | 1395 County Rd 1A | Ironton | 45638 |  | Lawrence | P003 | 172 MW GE 7FA natural gas fired dry low NOx (DLN) combustion turbine No. 3 with duct firing operating in combined cycle mode controlled by Selective Catalytic Reduction (SCR) | 2003-07-17 | scr | CUBIX CORPORATION | 172 mw at 59 deg f | 3.0 ppmv @15%o2 w/o duct firing | 176 mw | 2.6 ppmv (turbine only) | 7 | Nitrogen Dioxide | PASS | NA | Y |  | Yes
2003 | 40 | 0744000150 | Hanging Rock Energy Facility | 1395 County Rd 1A | Ironton | 45638 |  | Lawrence | P004 | 172 MW GE 7FA natural gas fired dry low NOx (DLN) combustion turbine No. 4 with duct firing operating in combined cycle mode controlled by Selective Catalytic Reduction (SCR) | 2003-07-17 | scr | CUBIX CORPORATION | 172 mw at 59 deg f | 27.8 lbs/hr(turbine + duct burners) | 227 mw | 24.3 lbs/hr (turbine + duct burner | 7 | Nitrogen Dioxide | PASS | NA | Y |  | Yes
2004 | 120 | 0165000132 | AEP Generation Resources Inc., - Darby Plant | 12509 Adkins Road | Mt. Sterling | 43143 | 9061 | Pickaway | P001 | Natural Gas or number two fuel oil-fired, simple cycle, combustion turbine having a nominal capacity of 1,115.2 MMBTU/hr (80 MW, nominal), controlled with a dry low NOx combustor; CT1 - Combustion Turbine No.1; *Modified | 2004-08-03 | n/a | SHAW ENVIRONMENTAL, INC. |  |  |  |  | 10 | Nitrogen Dioxide | PASS | NA | Y |  | Yes
2004 | 122 | 0165000132 | AEP Generation Resources Inc., - Darby Plant | 12509 Adkins Road | Mt. Sterling | 43143 | 9061 | Pickaway | P002 | Natural Gas or number two fuel oil-fired, simple cycle, combustion turbine having a nominal capacity of 1,115.2 MMBTU/hr (80 MW, nominal), controlled with a dry low NOx combustor; CT2 - Combustion Turbine No.2; *Modified | 2004-08-31 | n/a | GE ENERGY MANAGEMENT SYSTEMS |  |  |  |  | 10 | Nitrogen Dioxide | PASS | NA | Y |  | Yes
2004 | 123 | 0165000132 | AEP Generation Resources Inc., - Darby Plant | 12509 Adkins Road | Mt. Sterling | 43143 | 9061 | Pickaway | P003 | Natural Gas or number two fuel oil-fired, simple cycle, combustion turbine having a nominal capacity of 1,115.2 MMBTU/hr (80 MW, nominal), controlled with a dry low NOx combustor; CT3 - Combustion Turbine No.3; *Modified | 2004-09-01 | n/a | GE ENERGY MANAGEMENT SYSTEMS |  |  |  |  | 10 | Nitrogen Dioxide | PASS | NA | Y |  | Yes
2004 | 125 | 0165000132 | AEP Generation Resources Inc., - Darby Plant | 12509 Adkins Road | Mt. Sterling | 43143 | 9061 | Pickaway | P004 | Natural Gas or number two fuel oil-fired, simple cycle, combustion turbine having a nominal capacity of 1,115.2 MMBTU/hr (80 MW, nominal), controlled with a dry low NOx combustor; CT4 - Combustion Turbine No.4; *Modified | 2004-09-01 | n/a | GE ENERGY MANAGEMENT SYSTEMS |  |  |  |  | 10 | Nitrogen Dioxide | PASS | NA | Y |  | Yes
2004 | 127 | 0165000132 | AEP Generation Resources Inc., - Darby Plant | 12509 Adkins Road | Mt. Sterling | 43143 | 9061 | Pickaway | P005 | Natural Gas or number two fuel oil-fired, simple cycle, combustion turbine having a nominal capacity of 1,115.2 MMBTU/hr (80 MW, nominal), controlled with a dry low NOx combustor; CT5 - Combustion Turbine No.5; *Modified | 2004-09-02 | n/a | GE ENERGY MANAGEMENT SYSTEMS |  |  |  |  | 10 | Nitrogen Dioxide | PASS | NA | Y |  | Yes
2004 | 130 | 0165000132 | AEP Generation Resources Inc., - Darby Plant | 12509 Adkins Road | Mt. Sterling | 43143 | 9061 | Pickaway | P006 | Natural Gas or number two fuel oil-fired, simple cycle, combustion turbine having a nominal capacity of 1,115.2 MMBTU/hr (80 MW, nominal), controlled with a dry low NOx combustor; CT6 - Combustion Turbine No.6; *Modified | 2004-09-02 | n/a | GE ENERGY MANAGEMENT SYSTEMS |  |  |  |  | 10 | Nitrogen Dioxide | PASS | NA | Y |  | Yes
2004 | 1008 | 1409040897 | OMEGA JV2 Hamilton Peaking Station | 8000 N. Gilmore Road | Hamilton | 45015 |  | Butler | P001 | 32 MW (422.57 MMBtu./hr) Natural Gas-Fired Combustion Turbine with Water Injection | 2004-09-17 | control equipment? | GRACE |  |  |  |  | 7 | Nitrogen Oxide | PASS | Y | Y |  | Yes
2004 | 1009 | 1409040897 | OMEGA JV2 Hamilton Peaking Station | 8000 N. Gilmore Road | Hamilton | 45015 |  | Butler | P001 | 32 MW (422.57 MMBtu./hr) Natural Gas-Fired Combustion Turbine with Water Injection | 2004-09-17 | control equipment? | GRACE |  |  |  |  | 7 | Nitrogen Dioxide | PASS | Y | Y |  | Yes
2005 | 162 | 0165000132 | AEP Generation Resources Inc., - Darby Plant | 12509 Adkins Road | Mt. Sterling | 43143 | 9061 | Pickaway | P001 | Natural Gas or number two fuel oil-fired, simple cycle, combustion turbine having a nominal capacity of 1,115.2 MMBTU/hr (80 MW, nominal), controlled with a dry low NOx combustor; CT1 - Combustion Turbine No.1; *Modified | 2005-08-17 | n/a | GE Energy Management Services, Inc. |  |  |  |  | 20 | Nitrogen Oxide | PASS | NA | Y |  | Yes
2005 | 163 | 0165000132 | AEP Generation Resources Inc., - Darby Plant | 12509 Adkins Road | Mt. Sterling | 43143 | 9061 | Pickaway | P001 | Natural Gas or number two fuel oil-fired, simple cycle, combustion turbine having a nominal capacity of 1,115.2 MMBTU/hr (80 MW, nominal), controlled with a dry low NOx combustor; CT1 - Combustion Turbine No.1; *Modified | 2005-08-17 | n/a | GE Energy Management Services, Inc. |  |  |  |  | 20 | Nitrogen Dioxide | PASS | NA | Y |  | Yes
2005 | 165 | 0165000132 | AEP Generation Resources Inc., - Darby Plant | 12509 Adkins Road | Mt. Sterling | 43143 | 9061 | Pickaway | P003 | Natural Gas or number two fuel oil-fired, simple cycle, combustion turbine having a nominal capacity of 1,115.2 MMBTU/hr (80 MW, nominal), controlled with a dry low NOx combustor; CT3 - Combustion Turbine No.3; *Modified | 2005-08-18 | n/a | GE Energy Management Services, Inc. |  |  |  |  | 20 | Nitrogen Oxide | PASS | NA | Y |  | Yes
2005 | 166 | 0165000132 | AEP Generation Resources Inc., - Darby Plant | 12509 Adkins Road | Mt. Sterling | 43143 | 9061 | Pickaway | P003 | Natural Gas or number two fuel oil-fired, simple cycle, combustion turbine having a nominal capacity of 1,115.2 MMBTU/hr (80 MW, nominal), controlled with a dry low NOx combustor; CT3 - Combustion Turbine No.3; *Modified | 2005-08-18 | n/a | GE Energy Management Services, Inc. |  |  |  |  | 20 | Nitrogen Dioxide | PASS | NA | Y |  | Yes
2005 | 169 | 0165000132 | AEP Generation Resources Inc., - Darby Plant | 12509 Adkins Road | Mt. Sterling | 43143 | 9061 | Pickaway | P006 | Natural Gas or number two fuel oil-fired, simple cycle, combustion turbine having a nominal capacity of 1,115.2 MMBTU/hr (80 MW, nominal), controlled with a dry low NOx combustor; CT6 - Combustion Turbine No.6; *Modified | 2005-08-19 | n/a | GE Energy Management Services, Inc. |  |  |  |  | 20 | Nitrogen Dioxide | PASS | NA | Y |  | Yes
2005 | 217 | 0165000132 | AEP Generation Resources Inc., - Darby Plant | 12509 Adkins Road | Mt. Sterling | 43143 | 9061 | Pickaway | P006 | Natural Gas or number two fuel oil-fired, simple cycle, combustion turbine having a nominal capacity of 1,115.2 MMBTU/hr (80 MW, nominal), controlled with a dry low NOx combustor; CT6 - Combustion Turbine No.6; *Modified | 2005-08-19 | n/a | GE Energy Management Services, Inc. |  |  |  |  | 20 | Nitrogen Oxide | PASS | NA | Y |  | Yes
2005 | 992 | 1409000896 | Duke Energy Indiana, Madison Generating Station | 5657 Kennel Road | Trenton | 45067 |  | Butler | P001 | 84.65 Megawatt (Nominal) Simple-Cycle Combustion Turbine No.1 | 2005-06-14 | control equipment? | GRACE CONSULTING | 80 mw | see memo field | 75 mw | see memo field | other | Nitrogen Dioxide | PASS | NA | Y | TEST WAS A RATAALLOWABLESNOX (PPM) - RA LESS THAN OR EQUAL TO 20% OR 12 PPM MEAN DIFFERENCENOX (PPM @ 15% O2) - RA LESS THAN OR EQUAL TO 20%NOX (LB/MMBTU) - RA LESS THAN OR EQUAL TO 7.5% OR 0.015 LB/MMBTU MEAN DIFFERENCEACTUAL NOX(PPM) - 4.82% RA NOX (PPM @ 15% O2) - 5.81% RA NOX (LB/MMBTU) - 5.44% RA | Yes
2005 | 993 | 1409000896 | Duke Energy Indiana, Madison Generating Station | 5657 Kennel Road | Trenton | 45067 |  | Butler | P002 | 84.65 Megawatt (Nominal) Simple-Cycle Combustion Turbine No 2 | 2005-06-14 | control equipment? | GRACE CONSULTING | 80 mw | see memo field | 75 mw | see memo field | other | Nitrogen Dioxide | PASS | NA | Y | TEST WAS A RATAALLOWABLESNOX (PPM) - RA LESS THAN OR EQUAL TO 20% OR 12 PPM MEAN DIFFERENCENOX (PPM @ 15% O2) - RA LESS THAN OR EQUAL TO 20%NOX (LB/MMBTU) - RA LESS THAN OR EQUAL TO 7.5% OR 0.015 LB/MMBTU MEAN DIFFERENCEACTUAL NOX(PPM) - 4.82% RA NOX (PPM @ 15% O2) - 5.81% RA NOX (LB/MMBTU) - 5.44% RA | Yes
2005 | 996 | 1409000896 | Duke Energy Indiana, Madison Generating Station | 5657 Kennel Road | Trenton | 45067 |  | Butler | P003 | 84.65 Megawatt (Nominal) simple-cycle combustion turbine No. 3 | 2005-06-15 | control equipment? | GRACE CONSULTING | 80 mw | see other pollutants | 76 mw | see other pollutants | 7 | Nitrogen Dioxide | PASS | NA | Y | This data came from the old CETA system with no validation code. Some of data fields may be missing required information. | Yes
2005 | 1089 | 1409000896 | Duke Energy Indiana, Madison Generating Station | 5657 Kennel Road | Trenton | 45067 |  | Butler | P004 | 84.65 Megawatt (Nominal) simple-cycle combustion turbine No. 4 | 2005-06-15 | control equipment? | GRACE CONSULTING | 80 mw | see other pollutants | 76 mw | see other pollutants | 7 | Nitrogen Dioxide | PASS | NA | Y |  | Yes
2005 | 1090 | 1409000896 | Duke Energy Indiana, Madison Generating Station | 5657 Kennel Road | Trenton | 45067 |  | Butler | P005 | 84.65 Megawatt (Nominal) simple-cycle combustion turbine No. 5 | 2005-06-16 | control equipment? | GRACE CONSULTING | 80 mw | see other pollutants | 79 mw | see other pollutants | 7 | Nitrogen Dioxide | PASS | NA | Y |  | Yes
2005 | 1095 | 1409000896 | Duke Energy Indiana, Madison Generating Station | 5657 Kennel Road | Trenton | 45067 |  | Butler | P006 | 84.65 Megawatt (Nominal) simple-cycle combustion turbine No. 6 | 2005-06-16 | control equipment? | GRACE CONSULTING | 80 mw | see other pollutants | 78 mw | see other pollutants | 7 | Nitrogen Dioxide | PASS | NA | Y |  | Yes
2006 | 196 | 0165000132 | AEP Generation Resources Inc., - Darby Plant | 12509 Adkins Road | Mt. Sterling | 43143 | 9061 | Pickaway | P001 | Natural Gas or number two fuel oil-fired, simple cycle, combustion turbine having a nominal capacity of 1,115.2 MMBTU/hr (80 MW, nominal), controlled with a dry low NOx combustor; CT1 - Combustion Turbine No.1; *Modified | 2006-08-21 | dry low NOx combustor | Platt Environmental Services, Inc. |  |  |  |  | 7 | Nitrogen Dioxide | PASS | NA | Y |  | Yes
2006 | 198 | 0165000132 | AEP Generation Resources Inc., - Darby Plant | 12509 Adkins Road | Mt. Sterling | 43143 | 9061 | Pickaway | P001 | Natural Gas or number two fuel oil-fired, simple cycle, combustion turbine having a nominal capacity of 1,115.2 MMBTU/hr (80 MW, nominal), controlled with a dry low NOx combustor; CT1 - Combustion Turbine No.1; *Modified | 2006-08-21 | dry low NOx combustor | Platt Environmental Services, Inc. |  |  |  |  | 7 | Nitrogen Oxide | PASS | NA | Y |  | Yes
2006 | 200 | 0165000132 | AEP Generation Resources Inc., - Darby Plant | 12509 Adkins Road | Mt. Sterling | 43143 | 9061 | Pickaway | P002 | Natural Gas or number two fuel oil-fired, simple cycle, combustion turbine having a nominal capacity of 1,115.2 MMBTU/hr (80 MW, nominal), controlled with a dry low NOx combustor; CT2 - Combustion Turbine No.2; *Modified | 2006-08-21 | dry low NOx combustor | Platt Environmental Services, Inc. |  |  |  |  | 7 | Nitrogen Dioxide | PASS | NA | Y |  | Yes
2006 | 201 | 0165000132 | AEP Generation Resources Inc., - Darby Plant | 12509 Adkins Road | Mt. Sterling | 43143 | 9061 | Pickaway | P002 | Natural Gas or number two fuel oil-fired, simple cycle, combustion turbine having a nominal capacity of 1,115.2 MMBTU/hr (80 MW, nominal), controlled with a dry low NOx combustor; CT2 - Combustion Turbine No.2; *Modified | 2006-08-21 | dry low NOx combustor | Platt Environmental Services, Inc. |  |  |  |  | 7 | Nitrogen Oxide | PASS | NA | Y |  | Yes
2006 | 202 | 0165000132 | AEP Generation Resources Inc., - Darby Plant | 12509 Adkins Road | Mt. Sterling | 43143 | 9061 | Pickaway | P003 | Natural Gas or number two fuel oil-fired, simple cycle, combustion turbine having a nominal capacity of 1,115.2 MMBTU/hr (80 MW, nominal), controlled with a dry low NOx combustor; CT3 - Combustion Turbine No.3; *Modified | 2006-08-21 | dry low NOx combustor | Platt Environmental Services, Inc. |  |  |  |  | 7 | Nitrogen Oxide | PASS | NA | Y |  | Yes
2006 | 203 | 0165000132 | AEP Generation Resources Inc., - Darby Plant | 12509 Adkins Road | Mt. Sterling | 43143 | 9061 | Pickaway | P003 | Natural Gas or number two fuel oil-fired, simple cycle, combustion turbine having a nominal capacity of 1,115.2 MMBTU/hr (80 MW, nominal), controlled with a dry low NOx combustor; CT3 - Combustion Turbine No.3; *Modified | 2006-08-21 | dry low NOx combustor | Platt Environmental Services, Inc. |  |  |  |  | 7 | Nitrogen Dioxide | PASS | NA | Y |  | Yes
2006 | 205 | 0165000132 | AEP Generation Resources Inc., - Darby Plant | 12509 Adkins Road | Mt. Sterling | 43143 | 9061 | Pickaway | P004 | Natural Gas or number two fuel oil-fired, simple cycle, combustion turbine having a nominal capacity of 1,115.2 MMBTU/hr (80 MW, nominal), controlled with a dry low NOx combustor; CT4 - Combustion Turbine No.4; *Modified | 2006-08-21 | dry low NOx combustor | Platt Environmental Services, Inc. |  |  |  |  | 7 | Nitrogen Oxide | PASS | NA | Y |  | Yes
2006 | 206 | 0165000132 | AEP Generation Resources Inc., - Darby Plant | 12509 Adkins Road | Mt. Sterling | 43143 | 9061 | Pickaway | P004 | Natural Gas or number two fuel oil-fired, simple cycle, combustion turbine having a nominal capacity of 1,115.2 MMBTU/hr (80 MW, nominal), controlled with a dry low NOx combustor; CT4 - Combustion Turbine No.4; *Modified | 2006-08-21 | dry low NOx combustor | Platt Environmental Services, Inc. |  |  |  |  | 7 | Nitrogen Dioxide | PASS | NA | Y |  | Yes
2006 | 208 | 0165000132 | AEP Generation Resources Inc., - Darby Plant | 12509 Adkins Road | Mt. Sterling | 43143 | 9061 | Pickaway | P005 | Natural Gas or number two fuel oil-fired, simple cycle, combustion turbine having a nominal capacity of 1,115.2 MMBTU/hr (80 MW, nominal), controlled with a dry low NOx combustor; CT5 - Combustion Turbine No.5; *Modified | 2006-08-21 | dry low NOx combustor | Platt Environmental Services, Inc. |  |  |  |  | 7 | Nitrogen Oxide | PASS | NA | Y |  | Yes
2006 | 209 | 0165000132 | AEP Generation Resources Inc., - Darby Plant | 12509 Adkins Road | Mt. Sterling | 43143 | 9061 | Pickaway | P005 | Natural Gas or number two fuel oil-fired, simple cycle, combustion turbine having a nominal capacity of 1,115.2 MMBTU/hr (80 MW, nominal), controlled with a dry low NOx combustor; CT5 - Combustion Turbine No.5; *Modified | 2006-08-21 | dry low NOx combustor | Platt Environmental Services, Inc. |  |  |  |  | 7 | Nitrogen Dioxide | PASS | NA | Y |  | Yes
2006 | 211 | 0165000132 | AEP Generation Resources Inc., - Darby Plant | 12509 Adkins Road | Mt. Sterling | 43143 | 9061 | Pickaway | P006 | Natural Gas or number two fuel oil-fired, simple cycle, combustion turbine having a nominal capacity of 1,115.2 MMBTU/hr (80 MW, nominal), controlled with a dry low NOx combustor; CT6 - Combustion Turbine No.6; *Modified | 2006-08-21 | dry low NOx combustor | Platt Environmental Services, Inc. |  |  |  |  | 7 | Nitrogen Dioxide | PASS | NA | Y |  | Yes
2006 | 212 | 0165000132 | AEP Generation Resources Inc., - Darby Plant | 12509 Adkins Road | Mt. Sterling | 43143 | 9061 | Pickaway | P006 | Natural Gas or number two fuel oil-fired, simple cycle, combustion turbine having a nominal capacity of 1,115.2 MMBTU/hr (80 MW, nominal), controlled with a dry low NOx combustor; CT6 - Combustion Turbine No.6; *Modified | 2006-08-21 | dry low NOx combustor | Platt Environmental Services, Inc. |  |  |  |  | 7 | Nitrogen Oxide | PASS | NA | Y |  | Yes
2009 | 89 | 1409010078 | Dicks Creek Energy Facility | 632 Todhunter Road | Monroe | 45050 | 1029 | Butler | B001 | 100 MW Natural Gas/No. 2 Fuel Oil-Fired Turbine | 2009-09-22 | NA | GRACE CONSULTING, INC |  |  |  |  | 7E | Nitrogen Dioxide | PASS | NA | Y | Tested pollutants: NO2, NO; Permitted Allowable Emission Rate = NA; Permitted Maximum Operating Rate = 100 MW; Average Tested Emission Rate = 53.99 PPM @ 15%O2; Average Tested Operating Rate = 64 MW; Results = Passed; AFS Date = 2009-11-19 00:00:00.0; AFS ID = legacy) THIS TEST WAS CONDUCTED IN ACCORDANCE WITH PART 75 APPENDIX E REQUIREMENTS. THE RESULTS LISTED ON THE LEFT ABOVE ARE THE RESULTS OF THE HIGH LOAD NOX COMPLIANCE PORTION. THE COMPLETE RESULTS OF ALL LOADS ARE LISTED BELOW. LOAD MW PPM@15% 02 LB/MMBTU LOW 4 28.13 0.103 MID-LOW 24 36.58 0.135 HIGH-MID 44 45.22 0.167 HIGH 64 53.99 0.199 | Yes
2009 | 90 | 1409010078 | Dicks Creek Energy Facility | 632 Todhunter Road | Monroe | 45050 | 1029 | Butler | B001 | 100 MW Natural Gas/No. 2 Fuel Oil-Fired Turbine | 2009-09-22 | NA | GRACE CONSULTING, INC |  |  |  |  | 7E | Nitrogen Oxide | PASS | NA | Y | Tested pollutants: NO2, NO; Permitted Allowable Emission Rate = NA; Permitted Maximum Operating Rate = 100 MW; Average Tested Emission Rate = 53.99 PPM @ 15%O2; Average Tested Operating Rate = 64 MW; Results = Passed; AFS Date = 2009-11-19 00:00:00.0; AFS ID = legacy) THIS TEST WAS CONDUCTED IN ACCORDANCE WITH PART 75 APPENDIX E REQUIREMENTS. THE RESULTS LISTED ON THE LEFT ABOVE ARE THE RESULTS OF THE HIGH LOAD NOX COMPLIANCE PORTION. THE COMPLETE RESULTS OF ALL LOADS ARE LISTED BELOW. LOAD MW PPM@15% 02 LB/MMBTU LOW 4 28.13 0.103 MID-LOW 24 36.58 0.135 HIGH-MID 44 45.22 0.167 HIGH 64 53.99 0.199 | Yes
2012 | 163 | 0165000132 | AEP Generation Resources Inc., - Darby Plant | 12509 Adkins Road | Mt. Sterling | 43143 | 9061 | Pickaway | P002 | Natural Gas or number two fuel oil-fired, simple cycle, combustion turbine having a nominal capacity of 1,115.2 MMBTU/hr (80 MW, nominal), controlled with a dry low NOx combustor; CT2 - Combustion Turbine No.2; *Modified | 2012-06-28 | n/a | Mostardi Platt |  |  |  |  | 7E | Nitrogen Dioxide | PASS | NA | Y | Tested pollutants: NO2, NO; Permitted Allowable Emission Rate = 178.5 lbs/hour, all loads; 15 ppmvd at 15% O2; Permitted Maximum Operating Rate = 80 MW; Average Tested Emission Rate = 21.0 lbs/hr; 6.8ppmvd at 15% O2; Average Tested Operating Rate = 58.1 MW; Results = Passed; AFS Date = 2012-10-31 00:00:00.0; AFS ID = legacy) | Yes
2012 | 164 | 0165000132 | AEP Generation Resources Inc., - Darby Plant | 12509 Adkins Road | Mt. Sterling | 43143 | 9061 | Pickaway | P002 | Natural Gas or number two fuel oil-fired, simple cycle, combustion turbine having a nominal capacity of 1,115.2 MMBTU/hr (80 MW, nominal), controlled with a dry low NOx combustor; CT2 - Combustion Turbine No.2; *Modified | 2012-06-28 | n/a | Mostardi Platt |  |  |  |  | 7E | Nitrogen Oxide | PASS | NA | Y | Tested pollutants: NO2, NO; Permitted Allowable Emission Rate = 178.5 lbs/hour, all loads; 15 ppmvd at 15% O2; Permitted Maximum Operating Rate = 80 MW; Average Tested Emission Rate = 21.0 lbs/hr; 6.8ppmvd at 15% O2; Average Tested Operating Rate = 58.1 MW; Results = Passed; AFS Date = 2012-10-31 00:00:00.0; AFS ID = legacy) | Yes
2012 | 166 | 0165000132 | AEP Generation Resources Inc., - Darby Plant | 12509 Adkins Road | Mt. Sterling | 43143 | 9061 | Pickaway | P003 | Natural Gas or number two fuel oil-fired, simple cycle, combustion turbine having a nominal capacity of 1,115.2 MMBTU/hr (80 MW, nominal), controlled with a dry low NOx combustor; CT3 - Combustion Turbine No.3; *Modified | 2012-06-28 | n/a | Mostardi Platt |  |  |  |  | 7E | Nitrogen Dioxide | PASS | NA | Y | Tested pollutants: NO2, NO; Permitted Allowable Emission Rate = 178.5 lbs/hour, all loads; 15 ppmvd at 15% O2; Permitted Maximum Operating Rate = 80 MW; Average Tested Emission Rate = 18.56 lns/hr; 6.14 ppmvd at 15% O2; Average Tested Operating Rate = 58.1 MW; Results = Passed; AFS Date = 2012-10-31 00:00:00.0; AFS ID = legacy) | Yes
2012 | 167 | 0165000132 | AEP Generation Resources Inc., - Darby Plant | 12509 Adkins Road | Mt. Sterling | 43143 | 9061 | Pickaway | P003 | Natural Gas or number two fuel oil-fired, simple cycle, combustion turbine having a nominal capacity of 1,115.2 MMBTU/hr (80 MW, nominal), controlled with a dry low NOx combustor; CT3 - Combustion Turbine No.3; *Modified | 2012-06-28 | n/a | Mostardi Platt |  |  |  |  | 7E | Nitrogen Oxide | PASS | NA | Y | Tested pollutants: NO2, NO; Permitted Allowable Emission Rate = 178.5 lbs/hour, all loads; 15 ppmvd at 15% O2; Permitted Maximum Operating Rate = 80 MW; Average Tested Emission Rate = 18.56 lns/hr; 6.14 ppmvd at 15% O2; Average Tested Operating Rate = 58.1 MW; Results = Passed; AFS Date = 2012-10-31 00:00:00.0; AFS ID = legacy) | Yes
2012 | 169 | 0165000132 | AEP Generation Resources Inc., - Darby Plant | 12509 Adkins Road | Mt. Sterling | 43143 | 9061 | Pickaway | P006 | Natural Gas or number two fuel oil-fired, simple cycle, combustion turbine having a nominal capacity of 1,115.2 MMBTU/hr (80 MW, nominal), controlled with a dry low NOx combustor; CT6 - Combustion Turbine No.6; *Modified | 2012-06-28 | n/a | Mostardi Platt |  |  |  |  | 7E | Nitrogen Dioxide | PASS | NA | Y | Tested pollutants: NO2, NO; Permitted Allowable Emission Rate = 178.5 lbs/hour, all loads; 15 ppmvd at 15% O2; Permitted Maximum Operating Rate = 80 MW; Average Tested Emission Rate = 26.6 lbs/hr; 8.6 ppmvd at 15% O2; Average Tested Operating Rate = 58.1 MW; Results = Passed; AFS Date = 2012-10-31 00:00:00.0; AFS ID = legacy) | Yes
2012 | 170 | 0165000132 | AEP Generation Resources Inc., - Darby Plant | 12509 Adkins Road | Mt. Sterling | 43143 | 9061 | Pickaway | P006 | Natural Gas or number two fuel oil-fired, simple cycle, combustion turbine having a nominal capacity of 1,115.2 MMBTU/hr (80 MW, nominal), controlled with a dry low NOx combustor; CT6 - Combustion Turbine No.6; *Modified | 2012-06-28 | n/a | Mostardi Platt |  |  |  |  | 7E | Nitrogen Oxide | PASS | NA | Y | Tested pollutants: NO2, NO; Permitted Allowable Emission Rate = 178.5 lbs/hour, all loads; 15 ppmvd at 15% O2; Permitted Maximum Operating Rate = 80 MW; Average Tested Emission Rate = 26.6 lbs/hr; 8.6 ppmvd at 15% O2; Average Tested Operating Rate = 58.1 MW; Results = Passed; AFS Date = 2012-10-31 00:00:00.0; AFS ID = legacy) | Yes
2012 | 211 | 0204010193 | Cristal USA Inc., Ashtabula Complex Plant 2 | 2426 Middle Road | Ashtabula | 44004 |  | Ashtabula | B013 | 65.1 mmBtu/hr (4.92 MW) natural gas-fired combustion turbine with NOx emissions control technology, and a 55.0 mmBtu/hr natural gas-fired duct heater/heat recovery boiler no. 2 | 2012-04-25 | none | Contastoga-Rovers & Associates |  |  |  |  | 7E | Nitrogen Oxide | PASS | NA | Y | Tested pollutants: NO2, NO; Permitted Allowable Emission Rate = 12.53 #/hr; 190 ppmv @ 15% O2; Permitted Maximum Operating Rate = 5500 kW; Average Tested Emission Rate = 11.1 #/hr; 21.9 ppmv @ 15% O2; Average Tested Operating Rate = 2767 kW (50.3% load); Results = Passed; AFS Date = 2012-11-30 00:00:00.0; AFS ID = legacy) | Yes
2012 | 212 | 0204010193 | Cristal USA Inc., Ashtabula Complex Plant 2 | 2426 Middle Road | Ashtabula | 44004 |  | Ashtabula | B013 | 65.1 mmBtu/hr (4.92 MW) natural gas-fired combustion turbine with NOx emissions control technology, and a 55.0 mmBtu/hr natural gas-fired duct heater/heat recovery boiler no. 2 | 2012-04-25 | none | Contastoga-Rovers & Associates |  |  |  |  | 7E | Nitrogen Dioxide | PASS | NA | Y | Tested pollutants: NO2, NO; Permitted Allowable Emission Rate = 12.53 #/hr; 190 ppmv @ 15% O2; Permitted Maximum Operating Rate = 5500 kW; Average Tested Emission Rate = 11.1 #/hr; 21.9 ppmv @ 15% O2; Average Tested Operating Rate = 2767 kW (50.3% load); Results = Passed; AFS Date = 2012-11-30 00:00:00.0; AFS ID = legacy) | Yes
2012 | 214 | 0204010193 | Cristal USA Inc., Ashtabula Complex Plant 2 | 2426 Middle Road | Ashtabula | 44004 |  | Ashtabula | B014 | 65.1 mmBtu/hr (4.92 MW) natural gas-fired combustion turbine with NOx emissions control technology and a 55.0 mmBtu/hr natural gas-fired duct heater/heat recovery boiler no. 3 | 2012-04-25 | none | Contastoga-Rovers & Associates |  |  |  |  | 7E | Nitrogen Dioxide | PASS | NA | Y | Tested pollutants: NO2, NO; Permitted Allowable Emission Rate = 12.53 #/hr; 190 ppmv @ 15% O2; Permitted Maximum Operating Rate = 5500 kW; Average Tested Emission Rate = 10.4 #/hr; 20.5 ppmv @ 15% O2; Average Tested Operating Rate = 2727 kW (49.6% load); Results = Passed; AFS Date = 2012-11-30 00:00:00.0; AFS ID = legacy) | Yes
2012 | 215 | 0204010193 | Cristal USA Inc., Ashtabula Complex Plant 2 | 2426 Middle Road | Ashtabula | 44004 |  | Ashtabula | B014 | 65.1 mmBtu/hr (4.92 MW) natural gas-fired combustion turbine with NOx emissions control technology and a 55.0 mmBtu/hr natural gas-fired duct heater/heat recovery boiler no. 3 | 2012-04-25 | none | Contastoga-Rovers & Associates |  |  |  |  | 7E | Nitrogen Oxide | PASS | NA | Y | Tested pollutants: NO2, NO; Permitted Allowable Emission Rate = 12.53 #/hr; 190 ppmv @ 15% O2; Permitted Maximum Operating Rate = 5500 kW; Average Tested Emission Rate = 10.4 #/hr; 20.5 ppmv @ 15% O2; Average Tested Operating Rate = 2727 kW (49.6% load); Results = Passed; AFS Date = 2012-11-30 00:00:00.0; AFS ID = legacy) | Yes
2012 | 216 | 0204010193 | Cristal USA Inc., Ashtabula Complex Plant 2 | 2426 Middle Road | Ashtabula | 44004 |  | Ashtabula | B015 | 65.1 mmBtu/hr (4.92 MW) natural gas-fired combustion turbine with NOx emissions control technology and a 55.0 mmBtu/hr natural gas-fired duct heater/heat recovery boiler no. 4 | 2012-04-25 | none | Contastoga-Rovers & Associates |  |  |  |  | 7E | Nitrogen Oxide | PASS | NA | Y | Tested pollutants: NO2, NO; Permitted Allowable Emission Rate = 12.53 #/hr; Permitted Maximum Operating Rate = 5500 kW; Average Tested Emission Rate = 8.4 #/hr; 14.8 ppmvd; Average Tested Operating Rate = 4792 kW (87.1% load); Results = Passed; AFS Date = 2012-11-30 00:00:00.0; AFS ID = legacy) | Yes
2012 | 217 | 0204010193 | Cristal USA Inc., Ashtabula Complex Plant 2 | 2426 Middle Road | Ashtabula | 44004 |  | Ashtabula | B015 | 65.1 mmBtu/hr (4.92 MW) natural gas-fired combustion turbine with NOx emissions control technology and a 55.0 mmBtu/hr natural gas-fired duct heater/heat recovery boiler no. 4 | 2012-04-25 | none | Contastoga-Rovers & Associates |  |  |  |  | 7E | Nitrogen Dioxide | PASS | NA | Y | Tested pollutants: NO2, NO; Permitted Allowable Emission Rate = 12.53 #/hr; Permitted Maximum Operating Rate = 5500 kW; Average Tested Emission Rate = 8.4 #/hr; 14.8 ppmvd; Average Tested Operating Rate = 4792 kW (87.1% load); Results = Passed; AFS Date = 2012-11-30 00:00:00.0; AFS ID = legacy) | Yes
2012 | 226 | 0204010193 | Cristal USA Inc., Ashtabula Complex Plant 2 | 2426 Middle Road | Ashtabula | 44004 |  | Ashtabula | B013 | 65.1 mmBtu/hr (4.92 MW) natural gas-fired combustion turbine with NOx emissions control technology, and a 55.0 mmBtu/hr natural gas-fired duct heater/heat recovery boiler no. 2 | 2012-04-26 | none | Contastoga-Rovers & Associates |  |  |  |  | 7E | Nitrogen Oxide | PASS | NA | Y | Tested pollutants: NO2, NO; Permitted Allowable Emission Rate = 12.53 #/hr; 190 ppmv @ 15% O2; Permitted Maximum Operating Rate = 5500 kW; Average Tested Emission Rate = 9.3 #/hr; 18.6 ppmv @ 15% O2; Average Tested Operating Rate = 4164 kW (75.7% load); Results = Passed; AFS Date = 2012-11-30 00:00:00.0; AFS ID = legacy) | Yes
2012 | 227 | 0204010193 | Cristal USA Inc., Ashtabula Complex Plant 2 | 2426 Middle Road | Ashtabula | 44004 |  | Ashtabula | B013 | 65.1 mmBtu/hr (4.92 MW) natural gas-fired combustion turbine with NOx emissions control technology, and a 55.0 mmBtu/hr natural gas-fired duct heater/heat recovery boiler no. 2 | 2012-04-26 | none | Contastoga-Rovers & Associates |  |  |  |  | 7E | Nitrogen Dioxide | PASS | NA | Y | Tested pollutants: NO2, NO; Permitted Allowable Emission Rate = 12.53 #/hr; 190 ppmv @ 15% O2; Permitted Maximum Operating Rate = 5500 kW; Average Tested Emission Rate = 9.3 #/hr; 18.6 ppmv @ 15% O2; Average Tested Operating Rate = 4164 kW (75.7% load); Results = Passed; AFS Date = 2012-11-30 00:00:00.0; AFS ID = legacy) | Yes
2012 | 230 | 0204010193 | Cristal USA Inc., Ashtabula Complex Plant 2 | 2426 Middle Road | Ashtabula | 44004 |  | Ashtabula | B014 | 65.1 mmBtu/hr (4.92 MW) natural gas-fired combustion turbine with NOx emissions control technology and a 55.0 mmBtu/hr natural gas-fired duct heater/heat recovery boiler no. 3 | 2012-04-26 | none | Contastoga-Rovers & Associates |  |  |  |  | 7E | Nitrogen Dioxide | PASS | NA | Y | Tested pollutants: NO2, NO; Permitted Allowable Emission Rate = 12.53 #/hr; 190 ppmv @ 15% O2; Permitted Maximum Operating Rate = 5500 kW; Average Tested Emission Rate = 9.6 #/hr; 18.3 ppmv @ 15% O2; Average Tested Operating Rate = 4269 kW (77.6% load); Results = Passed; AFS Date = 2012-11-30 00:00:00.0; AFS ID = legacy) | Yes
2012 | 231 | 0204010193 | Cristal USA Inc., Ashtabula Complex Plant 2 | 2426 Middle Road | Ashtabula | 44004 |  | Ashtabula | B014 | 65.1 mmBtu/hr (4.92 MW) natural gas-fired combustion turbine with NOx emissions control technology and a 55.0 mmBtu/hr natural gas-fired duct heater/heat recovery boiler no. 3 | 2012-04-26 | none | Contastoga-Rovers & Associates |  |  |  |  | 7E | Nitrogen Oxide | PASS | NA | Y | Tested pollutants: NO2, NO; Permitted Allowable Emission Rate = 12.53 #/hr; 190 ppmv @ 15% O2; Permitted Maximum Operating Rate = 5500 kW; Average Tested Emission Rate = 9.6 #/hr; 18.3 ppmv @ 15% O2; Average Tested Operating Rate = 4269 kW (77.6% load); Results = Passed; AFS Date = 2012-11-30 00:00:00.0; AFS ID = legacy) | Yes
2012 | 232 | 0204010193 | Cristal USA Inc., Ashtabula Complex Plant 2 | 2426 Middle Road | Ashtabula | 44004 |  | Ashtabula | B015 | 65.1 mmBtu/hr (4.92 MW) natural gas-fired combustion turbine with NOx emissions control technology and a 55.0 mmBtu/hr natural gas-fired duct heater/heat recovery boiler no. 4 | 2012-04-26 | none | Contastoga-Rovers & Associates |  |  |  |  | 7E | Nitrogen Oxide | PASS | NA | Y | Tested pollutants: NO2, NO; Permitted Allowable Emission Rate = 12.53 #/hr; Permitted Maximum Operating Rate = 5500 kW; Average Tested Emission Rate = 8.7 #/hr; 15.1 ppmvd; Average Tested Operating Rate = 5286 kW (96.1% load); Results = Passed; AFS Date = 2012-11-30 00:00:00.0; AFS ID = legacy) | Yes
2012 | 235 | 0204010193 | Cristal USA Inc., Ashtabula Complex Plant 2 | 2426 Middle Road | Ashtabula | 44004 |  | Ashtabula | B015 | 65.1 mmBtu/hr (4.92 MW) natural gas-fired combustion turbine with NOx emissions control technology and a 55.0 mmBtu/hr natural gas-fired duct heater/heat recovery boiler no. 4 | 2012-04-26 | none | Contastoga-Rovers & Associates |  |  |  |  | 7E | Nitrogen Dioxide | PASS | NA | Y | Tested pollutants: NO2, NO; Permitted Allowable Emission Rate = 12.53 #/hr; Permitted Maximum Operating Rate = 5500 kW; Average Tested Emission Rate = 8.7 #/hr; 15.1 ppmvd; Average Tested Operating Rate = 5286 kW (96.1% load); Results = Passed; AFS Date = 2012-11-30 00:00:00.0; AFS ID = legacy) | Yes
2012 | 240 | 0204010193 | Cristal USA Inc., Ashtabula Complex Plant 2 | 2426 Middle Road | Ashtabula | 44004 |  | Ashtabula | B013 | 65.1 mmBtu/hr (4.92 MW) natural gas-fired combustion turbine with NOx emissions control technology, and a 55.0 mmBtu/hr natural gas-fired duct heater/heat recovery boiler no. 2 | 2012-04-27 | none | Contastoga-Rovers & Associates |  |  |  |  | 7E | Nitrogen Oxide | PASS | NA | Y | Tested pollutants: NO2, NO; Permitted Allowable Emission Rate = 12.53 #/hr; 190 ppmv @ 15% O2; Permitted Maximum Operating Rate = 5500 kW; Average Tested Emission Rate = 8.6 #/hr; 15.7 ppmv @ 15% O2; Average Tested Operating Rate = 4978 kW (90.5% load); Results = Passed; AFS Date = 2012-11-30 00:00:00.0; AFS ID = legacy) | Yes
2012 | 241 | 0204010193 | Cristal USA Inc., Ashtabula Complex Plant 2 | 2426 Middle Road | Ashtabula | 44004 |  | Ashtabula | B013 | 65.1 mmBtu/hr (4.92 MW) natural gas-fired combustion turbine with NOx emissions control technology, and a 55.0 mmBtu/hr natural gas-fired duct heater/heat recovery boiler no. 2 | 2012-04-27 | none | Contastoga-Rovers & Associates |  |  |  |  | 7E | Nitrogen Dioxide | PASS | NA | Y | Tested pollutants: NO2, NO; Permitted Allowable Emission Rate = 12.53 #/hr; 190 ppmv @ 15% O2; Permitted Maximum Operating Rate = 5500 kW; Average Tested Emission Rate = 8.6 #/hr; 15.7 ppmv @ 15% O2; Average Tested Operating Rate = 4978 kW (90.5% load); Results = Passed; AFS Date = 2012-11-30 00:00:00.0; AFS ID = legacy) | Yes
2012 | 242 | 0204010193 | Cristal USA Inc., Ashtabula Complex Plant 2 | 2426 Middle Road | Ashtabula | 44004 |  | Ashtabula | B015 | 65.1 mmBtu/hr (4.92 MW) natural gas-fired combustion turbine with NOx emissions control technology and a 55.0 mmBtu/hr natural gas-fired duct heater/heat recovery boiler no. 4 | 2012-04-27 | none | Contastoga-Rovers & Associates |  |  |  |  | 7E | Nitrogen Dioxide | PASS | NA | Y | Tested pollutants: NO2, NO; Permitted Allowable Emission Rate = 12.53 #/hr; Permitted Maximum Operating Rate = 5500 kW; Average Tested Emission Rate = 7.9 #/hr; 14.3 ppmvd; Average Tested Operating Rate = 4230 kW (76.9% load); Results = Passed; AFS Date = 2012-11-30 00:00:00.0; AFS ID = legacy) | Yes
2012 | 243 | 0204010193 | Cristal USA Inc., Ashtabula Complex Plant 2 | 2426 Middle Road | Ashtabula | 44004 |  | Ashtabula | B015 | 65.1 mmBtu/hr (4.92 MW) natural gas-fired combustion turbine with NOx emissions control technology and a 55.0 mmBtu/hr natural gas-fired duct heater/heat recovery boiler no. 4 | 2012-04-27 | none | Contastoga-Rovers & Associates |  |  |  |  | 7E | Nitrogen Oxide | PASS | NA | Y | Tested pollutants: NO2, NO; Permitted Allowable Emission Rate = 12.53 #/hr; Permitted Maximum Operating Rate = 5500 kW; Average Tested Emission Rate = 7.9 #/hr; 14.3 ppmvd; Average Tested Operating Rate = 4230 kW (76.9% load); Results = Passed; AFS Date = 2012-11-30 00:00:00.0; AFS ID = legacy) | Yes
2012 | 249 | 0204010193 | Cristal USA Inc., Ashtabula Complex Plant 2 | 2426 Middle Road | Ashtabula | 44004 |  | Ashtabula | B013 | 65.1 mmBtu/hr (4.92 MW) natural gas-fired combustion turbine with NOx emissions control technology, and a 55.0 mmBtu/hr natural gas-fired duct heater/heat recovery boiler no. 2 | 2012-04-28 | none | Contastoga-Rovers & Associates |  |  |  |  | 7E | Nitrogen Dioxide | PASS | NA | Y | Tested pollutants: NO2, NO; Permitted Allowable Emission Rate = 12.53 #/hr; 190 ppmv @ 15% O2; Permitted Maximum Operating Rate = 5500 kW; Average Tested Emission Rate = 8.4 #/hr; 15.0 ppmv @ 15% O2; Average Tested Operating Rate = 5367 kW (97.6% load); Results = Passed; AFS Date = 2012-11-30 00:00:00.0; AFS ID = legacy) | Yes
2012 | 250 | 0204010193 | Cristal USA Inc., Ashtabula Complex Plant 2 | 2426 Middle Road | Ashtabula | 44004 |  | Ashtabula | B013 | 65.1 mmBtu/hr (4.92 MW) natural gas-fired combustion turbine with NOx emissions control technology, and a 55.0 mmBtu/hr natural gas-fired duct heater/heat recovery boiler no. 2 | 2012-04-28 | none | Contastoga-Rovers & Associates |  |  |  |  | 7E | Nitrogen Oxide | PASS | NA | Y | Tested pollutants: NO2, NO; Permitted Allowable Emission Rate = 12.53 #/hr; 190 ppmv @ 15% O2; Permitted Maximum Operating Rate = 5500 kW; Average Tested Emission Rate = 8.4 #/hr; 15.0 ppmv @ 15% O2; Average Tested Operating Rate = 5367 kW (97.6% load); Results = Passed; AFS Date = 2012-11-30 00:00:00.0; AFS ID = legacy) | Yes
2012 | 252 | 0204010193 | Cristal USA Inc., Ashtabula Complex Plant 2 | 2426 Middle Road | Ashtabula | 44004 |  | Ashtabula | B014 | 65.1 mmBtu/hr (4.92 MW) natural gas-fired combustion turbine with NOx emissions control technology and a 55.0 mmBtu/hr natural gas-fired duct heater/heat recovery boiler no. 3 | 2012-04-28 | none | Contastoga-Rovers & Associates |  |  |  |  | 7E | Nitrogen Dioxide | PASS | NA | Y | Tested pollutants: NO2, NO; Permitted Allowable Emission Rate = 12.53 #/hr; 190 ppmv @ 15% O2; Permitted Maximum Operating Rate = 5500 kW; Average Tested Emission Rate = 7.9 #/hr; 14.3 ppmv @ 15% O2; Average Tested Operating Rate = 5301 kW (96.0% load); Results = Passed; AFS Date = 2012-11-30 00:00:00.0; AFS ID = legacy) | Yes
2012 | 253 | 0204010193 | Cristal USA Inc., Ashtabula Complex Plant 2 | 2426 Middle Road | Ashtabula | 44004 |  | Ashtabula | B014 | 65.1 mmBtu/hr (4.92 MW) natural gas-fired combustion turbine with NOx emissions control technology and a 55.0 mmBtu/hr natural gas-fired duct heater/heat recovery boiler no. 3 | 2012-04-28 | none | Contastoga-Rovers & Associates |  |  |  |  | 7E | Nitrogen Oxide | PASS | NA | Y | Tested pollutants: NO2, NO; Permitted Allowable Emission Rate = 12.53 #/hr; 190 ppmv @ 15% O2; Permitted Maximum Operating Rate = 5500 kW; Average Tested Emission Rate = 7.9 #/hr; 14.3 ppmv @ 15% O2; Average Tested Operating Rate = 5301 kW (96.0% load); Results = Passed; AFS Date = 2012-11-30 00:00:00.0; AFS ID = legacy) | Yes
2012 | 254 | 0204010193 | Cristal USA Inc., Ashtabula Complex Plant 2 | 2426 Middle Road | Ashtabula | 44004 |  | Ashtabula | B015 | 65.1 mmBtu/hr (4.92 MW) natural gas-fired combustion turbine with NOx emissions control technology and a 55.0 mmBtu/hr natural gas-fired duct heater/heat recovery boiler no. 4 | 2012-04-28 | none | Contastoga-Rovers & Associates |  |  |  |  | 7E | Nitrogen Dioxide | PASS | NA | Y | Tested pollutants: NO2, NO; Permitted Allowable Emission Rate = 12.53 #/hr; Permitted Maximum Operating Rate = 5500 kW; Average Tested Emission Rate = 11.3 #/hr; 21.9 ppmvd; Average Tested Operating Rate = 2767 kW (50.3% load); Results = Passed; AFS Date = 2012-11-30 00:00:00.0; AFS ID = legacy) | Yes
2012 | 256 | 0204010193 | Cristal USA Inc., Ashtabula Complex Plant 2 | 2426 Middle Road | Ashtabula | 44004 |  | Ashtabula | B015 | 65.1 mmBtu/hr (4.92 MW) natural gas-fired combustion turbine with NOx emissions control technology and a 55.0 mmBtu/hr natural gas-fired duct heater/heat recovery boiler no. 4 | 2012-04-28 | none | Contastoga-Rovers & Associates |  |  |  |  | 7E | Nitrogen Oxide | PASS | NA | Y | Tested pollutants: NO2, NO; Permitted Allowable Emission Rate = 12.53 #/hr; Permitted Maximum Operating Rate = 5500 kW; Average Tested Emission Rate = 11.3 #/hr; 21.9 ppmvd; Average Tested Operating Rate = 2767 kW (50.3% load); Results = Passed; AFS Date = 2012-11-30 00:00:00.0; AFS ID = legacy) | Yes
2012 | 864 | 0744000150 | Hanging Rock Energy Facility | 1395 County Rd 1A | Ironton | 45638 |  | Lawrence | P003 | 172 MW GE 7FA natural gas fired dry low NOx (DLN) combustion turbine No. 3 with duct firing operating in combined cycle mode controlled by Selective Catalytic Reduction (SCR) | 2012-08-22 | scr | Environmental Quality Management, Inc. |  |  |  |  | 7E | Nitrogen Oxide | PASS | NA | Y | Tested pollutants: NO2, NO; Permitted Allowable Emission Rate = 27.8 lbs/hr, 3 ppm(turbine + duct burners); Permitted Maximum Operating Rate = 175 MW; Average Tested Emission Rate = 23.35 lbs/hr, 2.64 ppm (turbine + duct burner; Average Tested Operating Rate = 229 mw; Results = Passed; AFS Date = 2013-01-22 00:00:00.0; AFS ID = legacy) | Yes
2012 | 865 | 0744000150 | Hanging Rock Energy Facility | 1395 County Rd 1A | Ironton | 45638 |  | Lawrence | P003 | 172 MW GE 7FA natural gas fired dry low NOx (DLN) combustion turbine No. 3 with duct firing operating in combined cycle mode controlled by Selective Catalytic Reduction (SCR) | 2012-08-22 | scr | Environmental Quality Management, Inc. |  |  |  |  | 7E | Nitrogen Dioxide | PASS | NA | Y | Tested pollutants: NO2, NO; Permitted Allowable Emission Rate = 27.8 lbs/hr, 3 ppm(turbine + duct burners); Permitted Maximum Operating Rate = 175 MW; Average Tested Emission Rate = 23.35 lbs/hr, 2.64 ppm (turbine + duct burner; Average Tested Operating Rate = 229 mw; Results = Passed; AFS Date = 2013-01-22 00:00:00.0; AFS ID = legacy) | Yes
2012 | 867 | 0744000150 | Hanging Rock Energy Facility | 1395 County Rd 1A | Ironton | 45638 |  | Lawrence | P004 | 172 MW GE 7FA natural gas fired dry low NOx (DLN) combustion turbine No. 4 with duct firing operating in combined cycle mode controlled by Selective Catalytic Reduction (SCR) | 2012-08-22 | scr | Environmental Quality Management, Inc. |  |  |  |  | 7E | Nitrogen Dioxide | PASS | NA | Y | Tested pollutants: NO2, NO; Permitted Allowable Emission Rate = 27.8 lbs/hr, 3 ppm(turbine + duct burners); Permitted Maximum Operating Rate = 175 MW; Average Tested Emission Rate = 26.23 lbs/hr, 2.95 ppm (turbine + duct burner; Average Tested Operating Rate = 232 mw; Results = Passed; AFS Date = 2013-01-22 00:00:00.0; AFS ID = legacy) | Yes
2012 | 868 | 0744000150 | Hanging Rock Energy Facility | 1395 County Rd 1A | Ironton | 45638 |  | Lawrence | P004 | 172 MW GE 7FA natural gas fired dry low NOx (DLN) combustion turbine No. 4 with duct firing operating in combined cycle mode controlled by Selective Catalytic Reduction (SCR) | 2012-08-22 | scr | Environmental Quality Management, Inc. |  |  |  |  | 7E | Nitrogen Oxide | PASS | NA | Y | Tested pollutants: NO2, NO; Permitted Allowable Emission Rate = 27.8 lbs/hr, 3 ppm(turbine + duct burners); Permitted Maximum Operating Rate = 175 MW; Average Tested Emission Rate = 26.23 lbs/hr, 2.95 ppm (turbine + duct burner; Average Tested Operating Rate = 232 mw; Results = Passed; AFS Date = 2013-01-22 00:00:00.0; AFS ID = legacy) | Yes
2012 | 870 | 0744000150 | Hanging Rock Energy Facility | 1395 County Rd 1A | Ironton | 45638 |  | Lawrence | P001 | 172 MW GE 7FA natural gas fired dry low NOx (DLN) combustion turbine No. 1 with duct firing operating in combined cycle mode controlled by Selective Calalytic Reduction (SCR) | 2012-08-23 | scr | Environmental Quality Management, Inc. |  |  |  |  | 7E | Nitrogen Dioxide | PASS | NA | Y | Tested pollutants: NO2, NO; Permitted Allowable Emission Rate = 27.8 lbs/hr, 3 ppm(turbine + duct burners); Permitted Maximum Operating Rate = 175 MW; Average Tested Emission Rate = 22.73 lbs/hr, 2.64 ppm (turbine + duct burner; Average Tested Operating Rate = 228 mw; Results = Passed; AFS Date = 2013-01-22 00:00:00.0; AFS ID = legacy) | Yes
2012 | 871 | 0744000150 | Hanging Rock Energy Facility | 1395 County Rd 1A | Ironton | 45638 |  | Lawrence | P001 | 172 MW GE 7FA natural gas fired dry low NOx (DLN) combustion turbine No. 1 with duct firing operating in combined cycle mode controlled by Selective Calalytic Reduction (SCR) | 2012-08-23 | scr | Environmental Quality Management, Inc. |  |  |  |  | 7E | Nitrogen Oxide | PASS | NA | Y | Tested pollutants: NO2, NO; Permitted Allowable Emission Rate = 27.8 lbs/hr, 3 ppm(turbine + duct burners); Permitted Maximum Operating Rate = 175 MW; Average Tested Emission Rate = 22.73 lbs/hr, 2.64 ppm (turbine + duct burner; Average Tested Operating Rate = 228 mw; Results = Passed; AFS Date = 2013-01-22 00:00:00.0; AFS ID = legacy) | Yes
2012 | 876 | 0744000150 | Hanging Rock Energy Facility | 1395 County Rd 1A | Ironton | 45638 |  | Lawrence | P002 | 172 MW GE 7FA natural gas fired dry low NOx (DLN) combustion turbine No. 2 with duct firing operating in combined cycle mode controlled by Selective Catalytic Reduction (SCR) | 2012-08-23 | scr | Environmental Quality Management, Inc. |  |  |  |  | 7E | Nitrogen Oxide | PASS | NA | Y | Tested pollutants: NO2, NO; Permitted Allowable Emission Rate = 27.8 lbs/hr, 3 ppm(turbine + duct burners); Permitted Maximum Operating Rate = 175 MW; Average Tested Emission Rate = 25.21 lbs/hr, 2.86 ppm (turbine + duct burner; Average Tested Operating Rate = 231 mw; Results = Passed; AFS Date = 2013-01-22 00:00:00.0; AFS ID = legacy) | Yes
2012 | 877 | 0744000150 | Hanging Rock Energy Facility | 1395 County Rd 1A | Ironton | 45638 |  | Lawrence | P002 | 172 MW GE 7FA natural gas fired dry low NOx (DLN) combustion turbine No. 2 with duct firing operating in combined cycle mode controlled by Selective Catalytic Reduction (SCR) | 2012-08-23 | scr | Environmental Quality Management, Inc. |  |  |  |  | 7E | Nitrogen Dioxide | PASS | NA | Y | Tested pollutants: NO2, NO; Permitted Allowable Emission Rate = 27.8 lbs/hr, 3 ppm(turbine + duct burners); Permitted Maximum Operating Rate = 175 MW; Average Tested Emission Rate = 25.21 lbs/hr, 2.86 ppm (turbine + duct burner; Average Tested Operating Rate = 231 mw; Results = Passed; AFS Date = 2013-01-22 00:00:00.0; AFS ID = legacy) | Yes
2012 | 986 | 0857043333 | DP&L Tait Generating Station | 2101 Arbor Boulevard | Moraine | 45439 | 1762 | Montgomery | P005 | 80 MW (1115 mmBtu/hr nominal heat input) natural gas or fuel oil fired simple cycle turbine with water injection controls, CT-1 | 2012-11-13 | CT-1(Other): Max. controlled emission rate = permit limit; CT-2(Other): Max. controlled emission rate = permit limit; CT-3(gas)(Other): Max. controlled emission rate = permit limit; CT-3(gas)(Other): Max. controlled emission rate = permit limit | Grace Consulting, Inc. | 80 MW | 25 ppmvd @15% O2 | 86 MW | 20 ppmvd @ 15% O2 | 7E | Nitrogen Dioxide | PASS | NA | Y |  | Yes
2012 | 988 | 0857043333 | DP&L Tait Generating Station | 2101 Arbor Boulevard | Moraine | 45439 | 1762 | Montgomery | P005 | 80 MW (1115 mmBtu/hr nominal heat input) natural gas or fuel oil fired simple cycle turbine with water injection controls, CT-1 | 2012-11-13 | CT-1(Other): Max. controlled emission rate = permit limit; CT-2(Other): Max. controlled emission rate = permit limit; CT-3(gas)(Other): Max. controlled emission rate = permit limit; CT-3(gas)(Other): Max. controlled emission rate = permit limit | Grace Consulting, Inc. | 80 MW | 25 ppmvd @15% O2 | 86 MW | 20 ppmvd @ 15% O2 | 7E | Nitrogen Oxide | PASS | NA | Y |  | Yes
2012 | 990 | 0857043333 | DP&L Tait Generating Station | 2101 Arbor Boulevard | Moraine | 45439 | 1762 | Montgomery | P006 | 80 MW (1115 mmBtu/hr nominal heat input) natural gas or fuel oil fired simple cycle turbine with water injection controls, CT-2 | 2012-11-13 | CT-1(Other): Max. controlled emission rate = permit limit; CT-2(Other): Max. controlled emission rate = permit limit; CT-3(gas)(Other): Max. controlled emission rate = permit limit; CT-3(gas)(Other): Max. controlled emission rate = permit limit | Grace Consulting, Inc. | 80 MW | 25 ppmvd @15% O2 | 86 MW | 22 ppmvd @ 15% O2 | 7E | Nitrogen Dioxide | PASS | NA | Y |  | Yes
2012 | 991 | 0857043333 | DP&L Tait Generating Station | 2101 Arbor Boulevard | Moraine | 45439 | 1762 | Montgomery | P006 | 80 MW (1115 mmBtu/hr nominal heat input) natural gas or fuel oil fired simple cycle turbine with water injection controls, CT-2 | 2012-11-13 | CT-1(Other): Max. controlled emission rate = permit limit; CT-2(Other): Max. controlled emission rate = permit limit; CT-3(gas)(Other): Max. controlled emission rate = permit limit; CT-3(gas)(Other): Max. controlled emission rate = permit limit | Grace Consulting, Inc. | 80 MW | 25 ppmvd @15% O2 | 86 MW | 22 ppmvd @ 15% O2 | 7E | Nitrogen Oxide | PASS | NA | Y |  | Yes
2012 | 992 | 0857043333 | DP&L Tait Generating Station | 2101 Arbor Boulevard | Moraine | 45439 | 1762 | Montgomery | P007 | 80 MW (1115 mmBtu/hr nominal heat input) natural gas or fuel oil fired simple cycle turbine with water injection and dry low NOx (DLN) combustor controls, CT-3 | 2012-11-13 | CT-1(Other): Max. controlled emission rate = permit limit; CT-2(Other): Max. controlled emission rate = permit limit; CT-3(gas)(Other): Max. controlled emission rate = permit limit; CT-3(gas)(Other): Max. controlled emission rate = permit limit | Grace Consulting, Inc. | 80 MW | 15 ppmvd @ 15% O2 | 85 MW | 11 ppmvd @ 15% O2 | 7E | Nitrogen Oxide | PASS | NA | Y |  | Yes
2012 | 994 | 0857043333 | DP&L Tait Generating Station | 2101 Arbor Boulevard | Moraine | 45439 | 1762 | Montgomery | P007 | 80 MW (1115 mmBtu/hr nominal heat input) natural gas or fuel oil fired simple cycle turbine with water injection and dry low NOx (DLN) combustor controls, CT-3 | 2012-11-13 | CT-1(Other): Max. controlled emission rate = permit limit; CT-2(Other): Max. controlled emission rate = permit limit; CT-3(gas)(Other): Max. controlled emission rate = permit limit; CT-3(gas)(Other): Max. controlled emission rate = permit limit | Grace Consulting, Inc. | 80 MW | 15 ppmvd @ 15% O2 | 85 MW | 11 ppmvd @ 15% O2 | 7E | Nitrogen Dioxide | PASS | NA | Y |  | Yes
2013 | 1347 | 0857043334 | DPL Energy LLC | 2101 Arbor Boulevard | Dayton | 45439 | 1511 | Montgomery | P001 | Natural gas and No. 2 fuel oil fired simple cycle stationary combustion turbine No. 4 - Tait CT4, with a nominal production rating of 80 MW and a nominal heat input of 1115.2 mmBtu/hour, with dry low NOx combustion and water injection controls | 2013-12-03 | Control is within the combustion zone as dry low NOx combustion | Grace Consulting, Inc. | 80 MW & 1115.2 mmBtu/hr | 15ppm NOx @ 15%O2 & 161 lb NOx/hr | 82 MW | 6.6 ppm @ 15% & 23 lb/hr | 7E | Nitrogen Oxide | PASS | NA | N | This was a subpart GG test to determine low mass emission rates. The test was conducted a all 4 loads. The following emissions measured at load stated: P001 @ 70MW yielded 6.5 ppm & 21 lb/hr, P001 @ 58MW yielded 6.5 ppm & 18 lb/hr, P001 @ 45MW yielded 6.9 ppm & 17 lb/hr. P002 @ 70MW yielded 7.5 ppm & 23 lb/hr, P002 @ 57MW yielded 6.6 ppm & 18 lb/hr, P002 @ 45MW yielded 6.8 ppm & 16 lb/hr. P003 @ 70MW yielded 7.2 ppm & 23 lb/hr, P003 @ 57MW yielded 6.8 ppm & 19 lb/hr, P003 @ 45MW yielded 6.4 ppm & 15.7 lb/hr. P004 @ 69MW yielded 6.9 ppm & 22 lb/hr, P004 @ 57MW yielded 6.5 ppm & 19 lb/hr, P004 @ 45MW yielded 6.5 ppm & 16 lb/hr. | Yes
2013 | 1348 | 0857043334 | DPL Energy LLC | 2101 Arbor Boulevard | Dayton | 45439 | 1511 | Montgomery | P001 | Natural gas and No. 2 fuel oil fired simple cycle stationary combustion turbine No. 4 - Tait CT4, with a nominal production rating of 80 MW and a nominal heat input of 1115.2 mmBtu/hour, with dry low NOx combustion and water injection controls | 2013-12-03 | Control is within the combustion zone as dry low NOx combustion | Grace Consulting, Inc. | 80 MW & 1115.2 mmBtu/hr | 15ppm NOx @ 15%O2 & 161 lb NOx/hr | 82 MW | 6.6 ppm @ 15% & 23 lb/hr | 7E | Nitrogen Dioxide | PASS | NA | N | This was a subpart GG test to determine low mass emission rates. The test was conducted a all 4 loads. The following emissions measured at load stated: P001 @ 70MW yielded 6.5 ppm & 21 lb/hr, P001 @ 58MW yielded 6.5 ppm & 18 lb/hr, P001 @ 45MW yielded 6.9 ppm & 17 lb/hr. P002 @ 70MW yielded 7.5 ppm & 23 lb/hr, P002 @ 57MW yielded 6.6 ppm & 18 lb/hr, P002 @ 45MW yielded 6.8 ppm & 16 lb/hr. P003 @ 70MW yielded 7.2 ppm & 23 lb/hr, P003 @ 57MW yielded 6.8 ppm & 19 lb/hr, P003 @ 45MW yielded 6.4 ppm & 15.7 lb/hr. P004 @ 69MW yielded 6.9 ppm & 22 lb/hr, P004 @ 57MW yielded 6.5 ppm & 19 lb/hr, P004 @ 45MW yielded 6.5 ppm & 16 lb/hr. | Yes
2013 | 1350 | 0857043334 | DPL Energy LLC | 2101 Arbor Boulevard | Dayton | 45439 | 1511 | Montgomery | P002 | Natural gas and No. 2 fuel oil fired simple cycle stationary combustion turbine No. 5 - Tait CT5, with a nominal production rating of 80 MW and a nominal heat input of 1115.2 mmBtu/hour, with dry low NOx combustion and water injection controls | 2013-12-03 | Control is within the combustion zone as dry low NOx combustion | Grace Consulting, Inc. | 80 MW & 1115.2 mmBtu/hr | 15ppm NOx @ 15%O2 & 161 lb NOx/hr | 81 MW | 5.2 ppm @ 15% & 24 lb/hr | 7E | Nitrogen Dioxide | PASS | NA | N | This was a subpart GG test to determine low mass emission rates. The test was conducted a all 4 loads. The following emissions measured at load stated: P001 @ 70MW yielded 6.5 ppm & 21 lb/hr, P001 @ 58MW yielded 6.5 ppm & 18 lb/hr, P001 @ 45MW yielded 6.9 ppm & 17 lb/hr. P002 @ 70MW yielded 7.5 ppm & 23 lb/hr, P002 @ 57MW yielded 6.6 ppm & 18 lb/hr, P002 @ 45MW yielded 6.8 ppm & 16 lb/hr. P003 @ 70MW yielded 7.2 ppm & 23 lb/hr, P003 @ 57MW yielded 6.8 ppm & 19 lb/hr, P003 @ 45MW yielded 6.4 ppm & 15.7 lb/hr. P004 @ 69MW yielded 6.9 ppm & 22 lb/hr, P004 @ 57MW yielded 6.5 ppm & 19 lb/hr, P004 @ 45MW yielded 6.5 ppm & 16 lb/hr. | Yes
2013 | 1352 | 0857043334 | DPL Energy LLC | 2101 Arbor Boulevard | Dayton | 45439 | 1511 | Montgomery | P002 | Natural gas and No. 2 fuel oil fired simple cycle stationary combustion turbine No. 5 - Tait CT5, with a nominal production rating of 80 MW and a nominal heat input of 1115.2 mmBtu/hour, with dry low NOx combustion and water injection controls | 2013-12-03 | Control is within the combustion zone as dry low NOx combustion | Grace Consulting, Inc. | 80 MW & 1115.2 mmBtu/hr | 15ppm NOx @ 15%O2 & 161 lb NOx/hr | 81 MW | 5.2 ppm @ 15% & 24 lb/hr | 7E | Nitrogen Oxide | PASS | NA | N | This was a subpart GG test to determine low mass emission rates. The test was conducted a all 4 loads. The following emissions measured at load stated: P001 @ 70MW yielded 6.5 ppm & 21 lb/hr, P001 @ 58MW yielded 6.5 ppm & 18 lb/hr, P001 @ 45MW yielded 6.9 ppm & 17 lb/hr. P002 @ 70MW yielded 7.5 ppm & 23 lb/hr, P002 @ 57MW yielded 6.6 ppm & 18 lb/hr, P002 @ 45MW yielded 6.8 ppm & 16 lb/hr. P003 @ 70MW yielded 7.2 ppm & 23 lb/hr, P003 @ 57MW yielded 6.8 ppm & 19 lb/hr, P003 @ 45MW yielded 6.4 ppm & 15.7 lb/hr. P004 @ 69MW yielded 6.9 ppm & 22 lb/hr, P004 @ 57MW yielded 6.5 ppm & 19 lb/hr, P004 @ 45MW yielded 6.5 ppm & 16 lb/hr. | Yes
2013 | 1354 | 0857043334 | DPL Energy LLC | 2101 Arbor Boulevard | Dayton | 45439 | 1511 | Montgomery | P003 | Natural gas and No. 2 fuel oil fired simple cycle stationary combustion turbine No. 6 - Tait CT6, with a nominal production rating of 80 MW and a nominal heat input of 1115.2 mmBtu/hour, with dry low NOx combustion and water injection controls | 2013-12-03 | Control is within the combustion zone as dry low NOx combustion | Grace Consulting, Inc. | 80 MW & 1115.2 mmBtu/hr | 15ppm NOx @ 15%O2 & 161 lb NOx/hr | 82 MW | 7.3 ppm @ 15% & 26 lb/hr | 7E | Nitrogen Oxide | PASS | NA | N | This was a subpart GG test to determine low mass emission rates. The test was conducted a all 4 loads. The following emissions measured at load stated: P001 @ 70MW yielded 6.5 ppm & 21 lb/hr, P001 @ 58MW yielded 6.5 ppm & 18 lb/hr, P001 @ 45MW yielded 6.9 ppm & 17 lb/hr. P002 @ 70MW yielded 7.5 ppm & 23 lb/hr, P002 @ 57MW yielded 6.6 ppm & 18 lb/hr, P002 @ 45MW yielded 6.8 ppm & 16 lb/hr. P003 @ 70MW yielded 7.2 ppm & 23 lb/hr, P003 @ 57MW yielded 6.8 ppm & 19 lb/hr, P003 @ 45MW yielded 6.4 ppm & 15.7 lb/hr. P004 @ 69MW yielded 6.9 ppm & 22 lb/hr, P004 @ 57MW yielded 6.5 ppm & 19 lb/hr, P004 @ 45MW yielded 6.5 ppm & 16 lb/hr. | Yes
2013 | 1355 | 0857043334 | DPL Energy LLC | 2101 Arbor Boulevard | Dayton | 45439 | 1511 | Montgomery | P003 | Natural gas and No. 2 fuel oil fired simple cycle stationary combustion turbine No. 6 - Tait CT6, with a nominal production rating of 80 MW and a nominal heat input of 1115.2 mmBtu/hour, with dry low NOx combustion and water injection controls | 2013-12-03 | Control is within the combustion zone as dry low NOx combustion | Grace Consulting, Inc. | 80 MW & 1115.2 mmBtu/hr | 15ppm NOx @ 15%O2 & 161 lb NOx/hr | 82 MW | 7.3 ppm @ 15% & 26 lb/hr | 7E | Nitrogen Dioxide | PASS | NA | N | This was a subpart GG test to determine low mass emission rates. The test was conducted a all 4 loads. The following emissions measured at load stated: P001 @ 70MW yielded 6.5 ppm & 21 lb/hr, P001 @ 58MW yielded 6.5 ppm & 18 lb/hr, P001 @ 45MW yielded 6.9 ppm & 17 lb/hr. P002 @ 70MW yielded 7.5 ppm & 23 lb/hr, P002 @ 57MW yielded 6.6 ppm & 18 lb/hr, P002 @ 45MW yielded 6.8 ppm & 16 lb/hr. P003 @ 70MW yielded 7.2 ppm & 23 lb/hr, P003 @ 57MW yielded 6.8 ppm & 19 lb/hr, P003 @ 45MW yielded 6.4 ppm & 15.7 lb/hr. P004 @ 69MW yielded 6.9 ppm & 22 lb/hr, P004 @ 57MW yielded 6.5 ppm & 19 lb/hr, P004 @ 45MW yielded 6.5 ppm & 16 lb/hr. | Yes
2013 | 1356 | 0857043334 | DPL Energy LLC | 2101 Arbor Boulevard | Dayton | 45439 | 1511 | Montgomery | P004 | Natural gas and No. 2 fuel oil fired simple cycle stationary combustion turbine No. 7 - Tait CT7, with a nominal production rating of 80 MW and a nominal heat input of 1115.2 mmBtu/hour, with dry low NOx combustion and water injection controls | 2013-12-03 | Control is within the combustion zone as dry low NOx combustion | Grace Consulting, Inc. | 80 MW & 1115.2 mmBtu/hr | 15ppm NOx @ 15%O2 & 161 lb NOx/hr | 81 MW | 7.1 ppm @ 15% & 25 lb/hr | 7E | Nitrogen Oxide | PASS | NA | N | This was a subpart GG test to determine low mass emission rates. The test was conducted a all 4 loads. The following emissions measured at load stated: P001 @ 70MW yielded 6.5 ppm & 21 lb/hr, P001 @ 58MW yielded 6.5 ppm & 18 lb/hr, P001 @ 45MW yielded 6.9 ppm & 17 lb/hr. P002 @ 70MW yielded 7.5 ppm & 23 lb/hr, P002 @ 57MW yielded 6.6 ppm & 18 lb/hr, P002 @ 45MW yielded 6.8 ppm & 16 lb/hr. P003 @ 70MW yielded 7.2 ppm & 23 lb/hr, P003 @ 57MW yielded 6.8 ppm & 19 lb/hr, P003 @ 45MW yielded 6.4 ppm & 15.7 lb/hr. P004 @ 69MW yielded 6.9 ppm & 22 lb/hr, P004 @ 57MW yielded 6.5 ppm & 19 lb/hr, P004 @ 45MW yielded 6.5 ppm & 16 lb/hr. | Yes
2013 | 1358 | 0857043334 | DPL Energy LLC | 2101 Arbor Boulevard | Dayton | 45439 | 1511 | Montgomery | P004 | Natural gas and No. 2 fuel oil fired simple cycle stationary combustion turbine No. 7 - Tait CT7, with a nominal production rating of 80 MW and a nominal heat input of 1115.2 mmBtu/hour, with dry low NOx combustion and water injection controls | 2013-12-03 | Control is within the combustion zone as dry low NOx combustion | Grace Consulting, Inc. | 80 MW & 1115.2 mmBtu/hr | 15ppm NOx @ 15%O2 & 161 lb NOx/hr | 81 MW | 7.1 ppm @ 15% & 25 lb/hr | 7E | Nitrogen Dioxide | PASS | NA | N | This was a subpart GG test to determine low mass emission rates. The test was conducted a all 4 loads. The following emissions measured at load stated: P001 @ 70MW yielded 6.5 ppm & 21 lb/hr, P001 @ 58MW yielded 6.5 ppm & 18 lb/hr, P001 @ 45MW yielded 6.9 ppm & 17 lb/hr. P002 @ 70MW yielded 7.5 ppm & 23 lb/hr, P002 @ 57MW yielded 6.6 ppm & 18 lb/hr, P002 @ 45MW yielded 6.8 ppm & 16 lb/hr. P003 @ 70MW yielded 7.2 ppm & 23 lb/hr, P003 @ 57MW yielded 6.8 ppm & 19 lb/hr, P003 @ 45MW yielded 6.4 ppm & 15.7 lb/hr. P004 @ 69MW yielded 6.9 ppm & 22 lb/hr, P004 @ 57MW yielded 6.5 ppm & 19 lb/hr, P004 @ 45MW yielded 6.5 ppm & 16 lb/hr. | Yes
2014 | 83 | 0165000132 | AEP Generation Resources Inc., - Darby Plant | 12509 Adkins Road | Mt. Sterling | 43143 | 9061 | Pickaway | P004 | Natural Gas or number two fuel oil-fired, simple cycle, combustion turbine having a nominal capacity of 1,115.2 MMBTU/hr (80 MW, nominal), controlled with a dry low NOx combustor; CT4 - Combustion Turbine No.4; *Modified | 2014-08-19 | dry low NOx combustor | Mostardi Platt | 80 MW | 178.5 lb/hr (all loads) 15 ppmvd @ 15% oxygen | 41.3, 55.7, 68, &81.0 MW | 47.25 lb/hr (high) 12.17 ppmvd @ 15% | 7E | Nitrogen Oxide | PASS | NA | Y |  | Yes
2014 | 85 | 0165000132 | AEP Generation Resources Inc., - Darby Plant | 12509 Adkins Road | Mt. Sterling | 43143 | 9061 | Pickaway | P005 | Natural Gas or number two fuel oil-fired, simple cycle, combustion turbine having a nominal capacity of 1,115.2 MMBTU/hr (80 MW, nominal), controlled with a dry low NOx combustor; CT5 - Combustion Turbine No.5; *Modified | 2014-08-19 | dry low NOx combustor | Mostardi Platt | 80 MW | 178.5 lb/hr (all loads) 15 ppmvd @ 15% oxygen | 41.3, 55.3, 69 & 80.7 MW | 63.58 lb/hr (high) 14.52 ppmvd @ 15% | 7E | Nitrogen Oxide | PASS | NA | Y |  | Yes
2014 | 87 | 0165000132 | AEP Generation Resources Inc., - Darby Plant | 12509 Adkins Road | Mt. Sterling | 43143 | 9061 | Pickaway | P004 | Natural Gas or number two fuel oil-fired, simple cycle, combustion turbine having a nominal capacity of 1,115.2 MMBTU/hr (80 MW, nominal), controlled with a dry low NOx combustor; CT4 - Combustion Turbine No.4; *Modified | 2014-08-20 | dry low NOx combustor | Mostardi Platt | 80 MW | 178.5 lb/hr (all loads) 15 ppmvd @ 15% oxygen | 41.3, 55.7, 68, &81.0 MW | 47.25 lb/hr (high) 12.17 ppmvd @ 15% | 7E | Nitrogen Oxide | PASS | NA | Y |  | Yes
2014 | 90 | 0165000132 | AEP Generation Resources Inc., - Darby Plant | 12509 Adkins Road | Mt. Sterling | 43143 | 9061 | Pickaway | P005 | Natural Gas or number two fuel oil-fired, simple cycle, combustion turbine having a nominal capacity of 1,115.2 MMBTU/hr (80 MW, nominal), controlled with a dry low NOx combustor; CT5 - Combustion Turbine No.5; *Modified | 2014-08-20 | dry low NOx combustor | Mostardi Platt | 80 MW | 178.5 lb/hr (all loads) 15 ppmvd @ 15% oxygen | 41.3, 55.3, 69 & 80.7 MW | 63.58 lb/hr (high) 14.52 ppmvd @ 15% | 7E | Nitrogen Oxide | PASS | NA | Y |  | Yes
2014 | 91 | 0165000132 | AEP Generation Resources Inc., - Darby Plant | 12509 Adkins Road | Mt. Sterling | 43143 | 9061 | Pickaway | P001 | Natural Gas or number two fuel oil-fired, simple cycle, combustion turbine having a nominal capacity of 1,115.2 MMBTU/hr (80 MW, nominal), controlled with a dry low NOx combustor; CT1 - Combustion Turbine No.1; *Modified | 2014-08-21 | dry low NOx combustor | Mostardi Platt | 80 MW | 178.5 lb/hr (all loads) 15 ppmvd @ 15% oxygen | 41, 55.3, 68, & 83.3 MW | 55.03 lb/hr (high) 13.89 ppmvd @ 15% oxygen | 7E | Nitrogen Oxide | PASS | NA | Y |  | Yes
2014 | 93 | 0165000132 | AEP Generation Resources Inc., - Darby Plant | 12509 Adkins Road | Mt. Sterling | 43143 | 9061 | Pickaway | P001 | Natural Gas or number two fuel oil-fired, simple cycle, combustion turbine having a nominal capacity of 1,115.2 MMBTU/hr (80 MW, nominal), controlled with a dry low NOx combustor; CT1 - Combustion Turbine No.1; *Modified | 2014-08-22 | dry low NOx combustor | Mostardi Platt | 80 MW | 178.5 lb/hr (all loads) 15 ppmvd @ 15% oxygen | 41, 55.3, 68, & 83.3 MW | 55.03 lb/hr (high) 13.89 ppmvd @ 15% oxygen | 7E | Nitrogen Oxide | PASS | NA | Y |  | Yes
2014 | 769 | 0247080487 | West Lorain Plant | 7101 WEST ERIE AVENUE | Lorain | 44053 | 0000 | Lorain | B001 | Distillate oil fired, 810.7 mmBtu/hr heat input rated, Combustion Turbine for electric generation. | 2014-01-25 | None | Grace Consulting, Inc. | 60MW | Corr. curve development @ 30%,50%,75%,80% load | 15MW,29MW,43.67MW,60MW | 25.23ppm,41.77ppm,75.7ppm,129.87ppm | 7E | Nitrogen Oxide | PASS | NA | Y | These results are just the corrected ppm values of NOx that will be used to develop the Correlation Curves for Appendix E certification. These are not to be used for final compliance . Just a report of results. See attached reports for breakdown of NOx emissions. | Yes
2014 | 770 | 0247080487 | West Lorain Plant | 7101 WEST ERIE AVENUE | Lorain | 44053 | 0000 | Lorain | B002 | Distillate oil fired, 810.7 mmBtu/hr heat input rated, Combustion Turbine for electric generation. | 2014-01-25 | None | Grace Consulting, Inc. | 60MW | Corr. curve development @ 30%,50%,75%,80% load | 12MW,30MW,44MW,56MW | 37.32ppm,64.96ppm,93.95ppm,123.93ppm | 7E | Nitrogen Oxide | PASS | NA | Y | These results are just the corrected ppm values of NOx that will be used to develop the Correlation Curves for Appendix E certification. These are not to be used for final compliance . Just a report of results. See attached reports for breakdown of NOx emissions. | Yes
2014 | 2175 | 0684000212 | Washington Energy Facility | 859 Ohio 83 | Beverly | 45715 | 1329 | Washington | P001 | 170 MW GE 7FA natural gas fired dry low NOx (DLN) combustion turbine with duct firing operating in combined cycle mode controlled by Selective Catalytic Reduction (SCR)- Modified | 2014-12-02 | SCR #1(Other): 32.3 lb/hr with duct burner firing(24.7 lb/hr w/o) | Mostardi Platt | 170 MW | 28.6 lb/shr | 181 MW | 23.07 lbs/hr | 6348 03 | NOx - Nitrogen Oxides | PASS | NA | Y | duct burners on Ammonia allowable- 28.1 lbs/hr emission rate-0.81 lb/hr formaldehyde allowable-0.82 lb/hr emission rate-<0.41 lb/hr | Yes
2014 | 2177 | 0684000212 | Washington Energy Facility | 859 Ohio 83 | Beverly | 45715 | 1329 | Washington | P001 | 170 MW GE 7FA natural gas fired dry low NOx (DLN) combustion turbine with duct firing operating in combined cycle mode controlled by Selective Catalytic Reduction (SCR)- Modified | 2014-12-03 | SCR #1(Other): 32.3 lb/hr with duct burner firing(24.7 lb/hr w/o) | Mostardi Platt | 170 MW | 24.7 lbs/hr | 180 MW | 19.07 lbs/hr | 6348 03 | NOx - Nitrogen Oxides | PASS | NA | Y | duct burners off ammonia allowable-26.6 lbs/hr emission rate-0.61 lbs/hr formaldehyde allowable-0.8 lb/hr emission rate-<0.41 lb/hr | Yes
2014 | 2184 | 0684000212 | Washington Energy Facility | 859 Ohio 83 | Beverly | 45715 | 1329 | Washington | P002 | 170 MW GE 7FA natural gas fired dry low NOx (DLN) combustion turbine with duct firing operating in combined cycle mode controlled with Selective Catalytic Reduction (SCR)- Modified | 2014-12-04 | SCR #2(Other): 32.3 lb/hr with duct burner firing(24.7 lb/hr w/o) | Mostardi Platt | 170 MW | 28.bs/hr | 186 MW | 19.88 lbs/lhr | 6348 03 | NOx - Nitrogen Oxides | PASS | NA | Y | ammonia allowable-28.1 lbs/hr emission rate-1.39 lbs/hr formaldehyde allowable-0.82 lb/hr emission rate-<0.43 lb/hr duct burners on | Yes
2014 | 2186 | 0684000212 | Washington Energy Facility | 859 Ohio 83 | Beverly | 45715 | 1329 | Washington | P002 | 170 MW GE 7FA natural gas fired dry low NOx (DLN) combustion turbine with duct firing operating in combined cycle mode controlled with Selective Catalytic Reduction (SCR)- Modified | 2014-12-05 | SCR #2(Other): 32.3 lb/hr with duct burner firing(24.7 lb/hr w/o) | Mostardi Platt | 170 MW | 24.7 lbs/hr | 181 MW | 14.68 lb/hr | 6348 03 | NOx - Nitrogen Oxides | PASS | NA | Y | duct burners off ammonia allowable-26.6 lbs/hr emission rate-0.73 lb/hr formaldehyde allowable 0.8 lb/hr emission rate-<0.41 lb/hr | Yes
2014 | 2250 | 0819070237 | Buckeye Power Greenville Station | 5119 Sebring Warner Road | Greenville | 45331 |  | Darke | B001 | 269.71 mmBtu/hr natural gas/No. 2 oil, simple cycle combustion turbine with water injection nitrogen oxides reduction system; G1CT1 | 2014-06-09 | WATER INJECTION | Mostardi Platt | 25 MW | 29.9 lb NOx/hr; <25ppmvd @ 15% O2 | 26 MW | 16.4 lb NOx/hr; 14 ppmvd @ 15% O2 | 7E | Nitrogen Dioxide | PASS | NA | Y | Unit G1CT1Low Mass Emission Test HIGH Load Demonstration: Facility tested to provide data to support it as a Low Mass Emitter per 40 CFR 75.19 and to establish emission rates for NOx and Carbon Monoxide. The water to fuel ratio submitted at 1.14. Heat Input measured 271 mmBtu/hr. Natural gas usage approx. 263730 cf. Actual test date 06/10/2014. This HIGH Load demonstration exceeded the permit allowable. The facility performed another LME late July and August to re-establish the water to fuel ratio while showing passing results. | Yes
2014 | 2251 | 0819070237 | Buckeye Power Greenville Station | 5119 Sebring Warner Road | Greenville | 45331 |  | Darke | B001 | 269.71 mmBtu/hr natural gas/No. 2 oil, simple cycle combustion turbine with water injection nitrogen oxides reduction system; G1CT1 | 2014-06-09 | WATER INJECTION | Mostardi Platt | 25 MW | 29.9 lb NOx/hr; <25ppmvd @ 15% O2 | 26 MW | 16.4 lb NOx/hr; 14 ppmvd @ 15% O2 | 7E | Nitrogen Oxide | PASS | NA | Y | Unit G1CT1Low Mass Emission Test HIGH Load Demonstration: Facility tested to provide data to support it as a Low Mass Emitter per 40 CFR 75.19 and to establish emission rates for NOx and Carbon Monoxide. The water to fuel ratio submitted at 1.14. Heat Input measured 271 mmBtu/hr. Natural gas usage approx. 263730 cf. Actual test date 06/10/2014. This HIGH Load demonstration exceeded the permit allowable. The facility performed another LME late July and August to re-establish the water to fuel ratio while showing passing results. | Yes
2014 | 2254 | 0819070237 | Buckeye Power Greenville Station | 5119 Sebring Warner Road | Greenville | 45331 |  | Darke | B002 | 269.71 mmBtu/hr natural gas/No. 2 oil, simple cycle combustion turbine with water injection nitrogen oxides reduction system; G1CT2 | 2014-06-09 | WATER INJECTION | Mostardi Platt | 25 MW | 29.9 lb NOx/hr; <25 ppmvd @ 15%O2 | 27 MW | 18.1 lb NOx/hr; 18 ppmvd @ 15% O2 | 7E | Nitrogen Dioxide | PASS | NA | Y | Unit G1CT2Low Mass Emission Test HIGH Load Demonstration: Facility tested to provide data to support it as a Low Mass Emitter per 40 CFR 75.19 and to establish emission rates for NOx and Carbon Monoxide. The water to fuel ratio submitted at 1.14. Heat Input measured 282 mmBtu/hr. Natural gas usage approx. 274323 cf. Actual test date 06/10/2014. | Yes
2014 | 2255 | 0819070237 | Buckeye Power Greenville Station | 5119 Sebring Warner Road | Greenville | 45331 |  | Darke | B002 | 269.71 mmBtu/hr natural gas/No. 2 oil, simple cycle combustion turbine with water injection nitrogen oxides reduction system; G1CT2 | 2014-06-09 | WATER INJECTION | Mostardi Platt | 25 MW | 29.9 lb NOx/hr; <25 ppmvd @ 15%O2 | 27 MW | 18.1 NOx/hr; 18 ppmvd @ 15% O2 | 7E | Nitrogen Oxide | PASS | NA | Y | Unit G1CT2Low Mass Emission Test HIGH Load Demonstration: Facility tested to provide data to support it as a Low Mass Emitter per 40 CFR 75.19 and to establish emission rates for NOx and Carbon Monoxide. The water to fuel ratio submitted at 1.14. Heat Input measured 282 mmBtu/hr. Natural gas usage approx. 274323 cf. Actual test date 06/10/2014. | Yes
2014 | 2256 | 0819070237 | Buckeye Power Greenville Station | 5119 Sebring Warner Road | Greenville | 45331 |  | Darke | B001 | 269.71 mmBtu/hr natural gas/No. 2 oil, simple cycle combustion turbine with water injection nitrogen oxides reduction system; G1CT1 | 2014-06-10 | WATER INJECTION | Mostardi Platt | 25 WM | 29.9 lb NOx/hr; <25ppmvd @ 15%O2 | 11 MW | 12.1 lb NOx/hr; 20 ppmvd @ 15% O2 | 7E | Nitrogen Dioxide | PASS | NA | Y | Unit G1CT1Low Mass Emission Test LOW Load Demonstration: Facility tested to provide data to support it as a Low Mass Emitter per 40 CFR 75.19 and to establish emission rates for NOx and Carbon Monoxide. The water to fuel ratio submitted at 0.78. Heat Input measured 142 mmBtu/hr. Natural gas usage approx. 137817 cf. | Yes
2014 | 2258 | 0819070237 | Buckeye Power Greenville Station | 5119 Sebring Warner Road | Greenville | 45331 |  | Darke | B001 | 269.71 mmBtu/hr natural gas/No. 2 oil, simple cycle combustion turbine with water injection nitrogen oxides reduction system; G1CT1 | 2014-06-10 | WATER INJECTION | Mostardi Platt | 25 MW | 29.9 lb NOx/hr; <25ppmvd @ 15%O2 | 11 MW | 12.1 lb NOx/hr; 20 ppmvd @ 15% O2 | 7E | Nitrogen Oxide | PASS | NA | Y | Unit G1CT1Low Mass Emission Test LOW Load Demonstration: Facility tested to provide data to support it as a Low Mass Emitter per 40 CFR 75.19 and to establish emission rates for NOx and Carbon Monoxide. The water to fuel ratio submitted at 0.78. Heat Input measured 142 mmBtu/hr. Natural gas usage approx. 137817 cf. | Yes
2014 | 2260 | 0819070237 | Buckeye Power Greenville Station | 5119 Sebring Warner Road | Greenville | 45331 |  | Darke | B002 | 269.71 mmBtu/hr natural gas/No. 2 oil, simple cycle combustion turbine with water injection nitrogen oxides reduction system; G1CT2 | 2014-06-10 | WATER INJECTION | Mostardi Platt | 25 MW | 29.9 lb NOx/hr; <25 ppmvd @ 15%O2 | 13 MW | 15.5 lb NOx/hr; 18 ppmvd @ 15% O2 | 7E | Nitrogen Oxide | PASS | NA | Y | Unit G1CT2Low Mass Emission Test LOW Load Demonstration: Facility tested to provide data to support it as a Low Mass Emitter per 40 CFR 75.19 and to establish emission rates for NOx and Carbon Monoxide. The water to fuel ratio submitted at 0.82. Heat Input measured 162 mmBtu/hr. Natural gas usage approx. 157690 cf. | Yes
2014 | 2261 | 0819070237 | Buckeye Power Greenville Station | 5119 Sebring Warner Road | Greenville | 45331 |  | Darke | B002 | 269.71 mmBtu/hr natural gas/No. 2 oil, simple cycle combustion turbine with water injection nitrogen oxides reduction system; G1CT2 | 2014-06-10 | WATER INJECTION | Mostardi Platt | 25 MW | 29.9 lb NOx/hr; <25 ppmvd @ 15%O2 | 13 MW | 15.5 lb NOx/hr; 18 ppmvd @ 15% O2 | 7E | Nitrogen Dioxide | PASS | NA | Y | Unit G1CT2Low Mass Emission Test LOW Load Demonstration: Facility tested to provide data to support it as a Low Mass Emitter per 40 CFR 75.19 and to establish emission rates for NOx and Carbon Monoxide. The water to fuel ratio submitted at 0.82. Heat Input measured 162 mmBtu/hr. Natural gas usage approx. 157690 cf. | Yes
2014 | 2263 | 0819070237 | Buckeye Power Greenville Station | 5119 Sebring Warner Road | Greenville | 45331 |  | Darke | B001 | 269.71 mmBtu/hr natural gas/No. 2 oil, simple cycle combustion turbine with water injection nitrogen oxides reduction system; G1CT1 | 2014-06-11 | WATER INJECTION | Mostardi Platt | 25 MW | 29.9 lb NOx/hr; <25ppmvd @ 15% O2 | 17 MW | 16.4 lb NOx/hr; 14 ppmvd @ 15% O2 | 7E | Nitrogen Oxide | PASS | NA | Y | Unit G1CT1Low Mass Emission Test LOW/MID Load Demonstration: Facility tested to provide data to support it as a Low Mass Emitter per 40 CFR 75.19 and to establish emission rates for NOx and Carbon Monoxide. The water to fuel ratio submitted at 0.88. Heat Input measured 187 mmBtu/hr. Natural gas usage approx. 182163 cf. Actual test date 06/10/2014. This HIGH Load demonstration exceeded the permit allowable. The facility performed another LME late July and August to re-establish the water to fuel ratio while showing passing results. | Yes
2014 | 2264 | 0819070237 | Buckeye Power Greenville Station | 5119 Sebring Warner Road | Greenville | 45331 |  | Darke | B001 | 269.71 mmBtu/hr natural gas/No. 2 oil, simple cycle combustion turbine with water injection nitrogen oxides reduction system; G1CT1 | 2014-06-11 | WATER INJECTION | Mostardi Platt | 25 MW | 29.9 lb NOx/hr; <25ppmvd @ 15% O2 | 17 MW | 16.4 lb NOx/hr; 14 ppmvd @ 15% O2 | 7E | Nitrogen Dioxide | PASS | NA | Y | Unit G1CT1Low Mass Emission Test LOW/MID Load Demonstration: Facility tested to provide data to support it as a Low Mass Emitter per 40 CFR 75.19 and to establish emission rates for NOx and Carbon Monoxide. The water to fuel ratio submitted at 0.88. Heat Input measured 187 mmBtu/hr. Natural gas usage approx. 182163 cf. Actual test date 06/10/2014. This HIGH Load demonstration exceeded the permit allowable. The facility performed another LME late July and August to re-establish the water to fuel ratio while showing passing results. | Yes
2014 | 2266 | 0819070237 | Buckeye Power Greenville Station | 5119 Sebring Warner Road | Greenville | 45331 |  | Darke | B002 | 269.71 mmBtu/hr natural gas/No. 2 oil, simple cycle combustion turbine with water injection nitrogen oxides reduction system; G1CT2 | 2014-06-11 | WATER INJECTION | Mostardi Platt | 25 MW | 29.9 lb NOx/hr; <25 ppmvd @ 15%O2 | 17 MW | 17.6 lb NOx/hr; 20 ppmvd @ 15% O2 | 7E | Nitrogen Dioxide | PASS | NA | Y | Unit G1CT2Low Mass Emission Test LOW/MID Load Demonstration: Facility tested to provide data to support it as a Low Mass Emitter per 40 CFR 75.19 and to establish emission rates for NOx and Carbon Monoxide. The water to fuel ratio submitted at 0.88. Heat Input measured 200 mmBtu/hr. Natural gas usage approx. 194107 cf. | Yes
2014 | 2267 | 0819070237 | Buckeye Power Greenville Station | 5119 Sebring Warner Road | Greenville | 45331 |  | Darke | B002 | 269.71 mmBtu/hr natural gas/No. 2 oil, simple cycle combustion turbine with water injection nitrogen oxides reduction system; G1CT2 | 2014-06-11 | WATER INJECTION | Mostardi Platt | 25 MW | 29.9 lb NOx/hr; <25 ppmvd @ 15%O2 | 17 MW | 17.6 lb NOx/ hr; 20 ppmvd @ 15% O2 | 7E | Nitrogen Oxide | PASS | NA | Y | Unit G1CT2Low Mass Emission Test LOW/MID Load Demonstration: Facility tested to provide data to support it as a Low Mass Emitter per 40 CFR 75.19 and to establish emission rates for NOx and Carbon Monoxide. The water to fuel ratio submitted at 0.88. Heat Input measured 200 mmBtu/hr. Natural gas usage approx. 194107 cf. | Yes
2014 | 2269 | 0819070237 | Buckeye Power Greenville Station | 5119 Sebring Warner Road | Greenville | 45331 |  | Darke | B001 | 269.71 mmBtu/hr natural gas/No. 2 oil, simple cycle combustion turbine with water injection nitrogen oxides reduction system; G1CT1 | 2014-06-12 | WATER INJECTION | Mostardi Platt | 25 MW | 29.9 lb NOx/hr; <25ppmvd @ 15% O2 | 21 MW | 19 lb NOx/hr; 20 ppmvd @ 15% O2 | 7E | Nitrogen Dioxide | PASS | NA | Y | Unit G1CT1Low Mass Emission Test MID/HIGH Load Demonstration: Facility tested to provide data to support it as a Low Mass Emitter per 40 CFR 75.19 and to establish emission rates for NOx and Carbon Monoxide. The water to fuel ratio submitted at 0.92. Heat Input measured 224 mmBtu/hr. Natural gas usage approx. 217363 cf. Actual test date 06/11/2014. | Yes
2014 | 2270 | 0819070237 | Buckeye Power Greenville Station | 5119 Sebring Warner Road | Greenville | 45331 |  | Darke | B001 | 269.71 mmBtu/hr natural gas/No. 2 oil, simple cycle combustion turbine with water injection nitrogen oxides reduction system; G1CT1 | 2014-06-12 | WATER INJECTION | Mostardi Platt | 25 MW | 29.9 lb NOx/hr; <25ppmvd @ 15% O2 | 21 MW | 19 lb NOx/hr; 20 ppmvd @ 15% O2 | 7E | Nitrogen Oxide | PASS | NA | Y | Unit G1CT1Low Mass Emission Test MID/HIGH Load Demonstration: Facility tested to provide data to support it as a Low Mass Emitter per 40 CFR 75.19 and to establish emission rates for NOx and Carbon Monoxide. The water to fuel ratio submitted at 0.92. Heat Input measured 224 mmBtu/hr. Natural gas usage approx. 217363 cf. Actual test date 06/11/2014. | Yes
2014 | 2272 | 0819070237 | Buckeye Power Greenville Station | 5119 Sebring Warner Road | Greenville | 45331 |  | Darke | B002 | 269.71 mmBtu/hr natural gas/No. 2 oil, simple cycle combustion turbine with water injection nitrogen oxides reduction system; G1CT2 | 2014-06-12 | WATER INJECTION | Mostardi Platt | 25 MW | 29.9 lb NOx/hr; < 25ppmvd @ 15%O2 | 22 MW | 21.2 lb NOx/hr; 23ppmvd @ 15%O2 | 7E | Nitrogen Oxide | PASS | NA | Y | Unit G1CT2 Low Mass Emission Test MID/HIGH Load Demonstration: Facility tested to provide data to support it as a Low Mass Emitter per 40 CFR 75.19 and to establish emission rates for NOx and Carbon Monoxide. The water to fuel ratio submitted at 0.93. Heat Input measured 240 mmBtu/hr. Natural gas usage approx. 233750 cf. Actual test date 06/11/2014. | Yes
2014 | 2273 | 0819070237 | Buckeye Power Greenville Station | 5119 Sebring Warner Road | Greenville | 45331 |  | Darke | B002 | 269.71 mmBtu/hr natural gas/No. 2 oil, simple cycle combustion turbine with water injection nitrogen oxides reduction system; G1CT2 | 2014-06-12 | WATER INJECTION | Mostardi Platt | 25 MW | 29.9 lb NOx/hr; < 25ppmvd @ 15%O2 | 22 MW | 21.2 lb NOx/hr; 23ppmvd @ 15%O2 | 7E | Nitrogen Dioxide | PASS | NA | Y | Unit G1CT2 Low Mass Emission Test MID/HIGH Load Demonstration: Facility tested to provide data to support it as a Low Mass Emitter per 40 CFR 75.19 and to establish emission rates for NOx and Carbon Monoxide. The water to fuel ratio submitted at 0.93. Heat Input measured 240 mmBtu/hr. Natural gas usage approx. 233750 cf. Actual test date 06/11/2014. | Yes
2014 | 2274 | 0819070237 | Buckeye Power Greenville Station | 5119 Sebring Warner Road | Greenville | 45331 |  | Darke | B005 | 269.71 mmBtu/hr natural gas/No. 2 oil, simple cycle combustion turbine with water injection nitrogen oxides reduction system; G3CT1 | 2014-06-12 | WATER INJECTION | Mostardi Platt | 25 MW | 29.9 lb NOx/hr; <25 ppmvd @15%O2 | 12 MW | 15.4 lb NOx/hr; 22 ppmvd@15%O2 | 7E | Nitrogen Dioxide | PASS | NA | Y | Unit G3CT1 Low Mass Emission Test LOW Load Demonstration: Facility tested to provide data to support it as a Low Mass Emitter per 40 CFR 75.19 and to establish emission rates for NOx and Carbon Monoxide. The water to fuel ratio submitted at 0.80. Heat Input measured 164 mmBtu/hr. Natural gas usage approx. 159150 cf. | Yes
2014 | 2276 | 0819070237 | Buckeye Power Greenville Station | 5119 Sebring Warner Road | Greenville | 45331 |  | Darke | B005 | 269.71 mmBtu/hr natural gas/No. 2 oil, simple cycle combustion turbine with water injection nitrogen oxides reduction system; G3CT1 | 2014-06-12 | WATER INJECTION | Mostardi Platt | 25 MW | 29.9 lb NOx/hr; <25 ppmvd @15%O2 | 12 MW | 15.4 lb NOx/hr; 22 ppmvd@15%O2 | 7E | Nitrogen Oxide | PASS | NA | Y | Unit G3CT1 Low Mass Emission Test LOW Load Demonstration: Facility tested to provide data to support it as a Low Mass Emitter per 40 CFR 75.19 and to establish emission rates for NOx and Carbon Monoxide. The water to fuel ratio submitted at 0.80. Heat Input measured 164 mmBtu/hr. Natural gas usage approx. 159150 cf. | Yes
2014 | 2277 | 0819070237 | Buckeye Power Greenville Station | 5119 Sebring Warner Road | Greenville | 45331 |  | Darke | B005 | 269.71 mmBtu/hr natural gas/No. 2 oil, simple cycle combustion turbine with water injection nitrogen oxides reduction system; G3CT1 | 2014-06-13 | WATER INJECTION | Mostardi Platt | 25 MW | 29.9 lbNOx/hr; < 25ppmvd@15%O2 | 17 MW | 15.8 lb NOx/hr; 18ppmvd @15%O2 | 7E | Nitrogen Dioxide | PASS | NA | Y | Unit G3CT1 Low Mass Emission Test LOW/MID Load Demonstration: Facility tested to provide data to support it as a Low Mass Emitter per 40 CFR 75.19 and to establish emission rates for NOx and Carbon Monoxide. The water to fuel ratio submitted at 0.97. Heat Input measured 207 mmBtu/hr. Natural gas usage approx. 205217 cf. | Yes
2014 | 2278 | 0819070237 | Buckeye Power Greenville Station | 5119 Sebring Warner Road | Greenville | 45331 |  | Darke | B005 | 269.71 mmBtu/hr natural gas/No. 2 oil, simple cycle combustion turbine with water injection nitrogen oxides reduction system; G3CT1 | 2014-06-13 | WATER INJECTION | Mostardi Platt | 25 MW | 29.9 lbNOx/hr; < 25ppmvd@15%O2 | 17 MW | 15.8 lb NOx/hr; 18ppmvd @15%O2 | 7E | Nitrogen Oxide | PASS | NA | Y | Unit G3CT1 Low Mass Emission Test LOW/MID Load Demonstration: Facility tested to provide data to support it as a Low Mass Emitter per 40 CFR 75.19 and to establish emission rates for NOx and Carbon Monoxide. The water to fuel ratio submitted at 0.97. Heat Input measured 207 mmBtu/hr. Natural gas usage approx. 205217 cf. | Yes
2014 | 2280 | 0819070237 | Buckeye Power Greenville Station | 5119 Sebring Warner Road | Greenville | 45331 |  | Darke | B005 | 269.71 mmBtu/hr natural gas/No. 2 oil, simple cycle combustion turbine with water injection nitrogen oxides reduction system; G3CT1 | 2014-06-14 | WATER INJECTION | Mostardi Platt | 25 MW | 29.9 lbNOx/hr; < 25ppmvd@15%O2 | 22 MW | 18 lb NOx/hr; 19 ppmvd @15%O2 | 7E | Nitrogen Dioxide | PASS | NA | Y | Unit G3CT1 Low Mass Emission Test MID/HIGH Load Demonstration: Facility tested to provide data to support it as a Low Mass Emitter per 40 CFR 75.19 and to establish emission rates for NOx and Carbon Monoxide. The water to fuel ratio submitted at 1.07. Heat Input measured 249 mmBtu/hr. Natural gas usage approx. 242490 cf. Actual test date 06/13/2014. | Yes
2014 | 2282 | 0819070237 | Buckeye Power Greenville Station | 5119 Sebring Warner Road | Greenville | 45331 |  | Darke | B005 | 269.71 mmBtu/hr natural gas/No. 2 oil, simple cycle combustion turbine with water injection nitrogen oxides reduction system; G3CT1 | 2014-06-14 | WATER INJECTION | Mostardi Platt | 25 MW | 29.9 lbNOx/hr; < 25ppmvd@15%O2 | 22 MW | 18 lb NOx/hr; 19 ppmvd @15%O2 | 7E | Nitrogen Oxide | PASS | NA | Y | Unit G3CT1 Low Mass Emission Test MID/HIGH Load Demonstration: Facility tested to provide data to support it as a Low Mass Emitter per 40 CFR 75.19 and to establish emission rates for NOx and Carbon Monoxide. The water to fuel ratio submitted at 1.07. Heat Input measured 249 mmBtu/hr. Natural gas usage approx. 242490 cf. Actual test date 06/13/2014. | Yes
2014 | 2283 | 0819070237 | Buckeye Power Greenville Station | 5119 Sebring Warner Road | Greenville | 45331 |  | Darke | B005 | 269.71 mmBtu/hr natural gas/No. 2 oil, simple cycle combustion turbine with water injection nitrogen oxides reduction system; G3CT1 | 2014-06-15 | WATER INJECTION | Mostardi Platt | 25 MW | 29.9 lbNOx/hr; < 25ppmvd@15%O2 | 25 MW | 17.2 lb NOx/hr; 15 ppmvd @15%O2 | 7E | Nitrogen Dioxide | PASS | NA | Y | Unit G3CT1 Low Mass Emission Test HIGH Load Demonstration: Facility tested to provide data to support it as a Low Mass Emitter per 40 CFR 75.19 and to establish emission rates for NOx and Carbon Monoxide. The water to fuel ratio submitted at 1.14. Heat Input measured 278 mmBtu/hr. Natural gas usage approx. 206709 cf. Actual test date 06/12/2014. | Yes
2014 | 2285 | 0819070237 | Buckeye Power Greenville Station | 5119 Sebring Warner Road | Greenville | 45331 |  | Darke | B005 | 269.71 mmBtu/hr natural gas/No. 2 oil, simple cycle combustion turbine with water injection nitrogen oxides reduction system; G3CT1 | 2014-06-15 | WATER INJECTION | Mostardi Platt | 25 MW | 29.9 lbNOx/hr; < 25ppmvd@15%O2 | 25 MW | 17.2 lb NOx/hr; 15 ppmvd @15%O2 | 7E | Nitrogen Oxide | PASS | NA | Y | Unit G3CT1 Low Mass Emission Test HIGH Load Demonstration: Facility tested to provide data to support it as a Low Mass Emitter per 40 CFR 75.19 and to establish emission rates for NOx and Carbon Monoxide. The water to fuel ratio submitted at 1.14. Heat Input measured 278 mmBtu/hr. Natural gas usage approx. 206709 cf. Actual test date 06/12/2014. | Yes
2014 | 2287 | 0819070237 | Buckeye Power Greenville Station | 5119 Sebring Warner Road | Greenville | 45331 |  | Darke | B001 | 269.71 mmBtu/hr natural gas/No. 2 oil, simple cycle combustion turbine with water injection nitrogen oxides reduction system; G1CT1 | 2014-07-28 | WATER INJECTION | Mostardi Platt | 25 MW | 29.9 lb NOx/hr; <25 ppmvd@15%O2 | 25 MW | 24 lb NOx/hr; 22 ppmvd@15%O2 | 7E | Nitrogen Dioxide | PASS | NA | Y | Unit G1CT1 Mass Emission Test HIGH Load Demonstration: Facility tested to provide data to support it as a Low Mass Emitter per 40 CFR 75.19 and to establish emission rates for NOx and Carbon Monoxide. This was a repeated testing effort as first attempt in June showed exceedances of CO emission rates at higher operating levels apparently due to facility calculation error and establishment of wrong water to fuel ratio. The water to fuel ratio submitted at 0.98. Heat Input measured 268 lb/MMbtu. Natural Gas usage approx. 254987 cf. This test was conducted on 07/29/14 but labled 07/28 to allow file savings. | Yes
2014 | 2288 | 0819070237 | Buckeye Power Greenville Station | 5119 Sebring Warner Road | Greenville | 45331 |  | Darke | B001 | 269.71 mmBtu/hr natural gas/No. 2 oil, simple cycle combustion turbine with water injection nitrogen oxides reduction system; G1CT1 | 2014-07-28 | WATER INJECTION | Mostardi Platt | 25 MW | 29.9 lb NOx/hr; <25 ppmvd@15%O2 | 25 MW | 24 lb NOx/hr; 22 ppmvd@15%O2 | 7E | Nitrogen Oxide | PASS | NA | Y | Unit G1CT1 Mass Emission Test HIGH Load Demonstration: Facility tested to provide data to support it as a Low Mass Emitter per 40 CFR 75.19 and to establish emission rates for NOx and Carbon Monoxide. This was a repeated testing effort as first attempt in June showed exceedances of CO emission rates at higher operating levels apparently due to facility calculation error and establishment of wrong water to fuel ratio. The water to fuel ratio submitted at 0.98. Heat Input measured 268 lb/MMbtu. Natural Gas usage approx. 254987 cf. This test was conducted on 07/29/14 but labled 07/28 to allow file savings. | Yes
2014 | 2290 | 0819070237 | Buckeye Power Greenville Station | 5119 Sebring Warner Road | Greenville | 45331 |  | Darke | B002 | 269.71 mmBtu/hr natural gas/No. 2 oil, simple cycle combustion turbine with water injection nitrogen oxides reduction system; G1CT2 | 2014-07-28 | WATER INJECTION | Mostardi Platt | 25 MW | 29.9 lbNOx/hr; <25ppmvdNOx@15%O2 | 22 MW | 24.3 lb NOx/hr; 22.5ppmvd@15%O2 | 7E | Nitrogen Dioxide | PASS | NA | Y | Unit G1CT2 Mass Emission Test MID/HIGH Load Demonstration: Facility tested to provide data to support it as a Low Mass Emitter per 40 CFR 75.19 and to establish emission rates for NOx and Carbon Monoxide. This was a repeated testing effort as first attempt in June showed exceedances of CO emission rates at higher operating levels apparently due to facility calculation error and establishment of wrong water to fuel ratio. The water to fuel ratio submitted at 0.97. Heat Input measured 242 lb/MMbtu. Natural Gas usage approx. 230653 cf. Actual test date 07/30/14. | Yes
2014 | 2291 | 0819070237 | Buckeye Power Greenville Station | 5119 Sebring Warner Road | Greenville | 45331 |  | Darke | B002 | 269.71 mmBtu/hr natural gas/No. 2 oil, simple cycle combustion turbine with water injection nitrogen oxides reduction system; G1CT2 | 2014-07-28 | WATER INJECTION | Mostardi Platt | 25 MW | 29.9 lbNOx/hr; <25ppmvdNOx@15%O2 | 22 MW | 24.3 lb NOx/hr; 22.5ppmvd@15%O2 | 7E | Nitrogen Oxide | PASS | NA | Y | Unit G1CT2 Mass Emission Test MID/HIGH Load Demonstration: Facility tested to provide data to support it as a Low Mass Emitter per 40 CFR 75.19 and to establish emission rates for NOx and Carbon Monoxide. This was a repeated testing effort as first attempt in June showed exceedances of CO emission rates at higher operating levels apparently due to facility calculation error and establishment of wrong water to fuel ratio. The water to fuel ratio submitted at 0.97. Heat Input measured 242 lb/MMbtu. Natural Gas usage approx. 230653 cf. Actual test date 07/30/14. | Yes
2014 | 2293 | 0819070237 | Buckeye Power Greenville Station | 5119 Sebring Warner Road | Greenville | 45331 |  | Darke | B001 | 269.71 mmBtu/hr natural gas/No. 2 oil, simple cycle combustion turbine with water injection nitrogen oxides reduction system; G1CT1 | 2014-07-29 | WATER INJECTION | Mostardi Platt | 25 MW | 29.9 lb NOx/hr; <25 ppmvd@15%O2 | 11 MW | 12.6 lb NOx/hr; 21.9 ppmvd@15%O2 | 7E | Nitrogen Oxide | PASS | NA | Y | Unit G1CT1Low Mass Emission Test Low Load Demonstration: Facility tested to provide data to support it as a Low Mass Emitter per 40 CFR 75.19 and to establish emission rates for NOx and Carbon Monoxide. This was a repeated testing effort as first attempt in June showed exceedances of CO emission rates at higher operating levels apparently due to facility calculation error and establishment of wrong water to fuel ratio. The water to fuel ratio submitted at 0.84. Heat Input measured 146 mmBtu/hr. Natural gas usage approx. 138633 cf. | Yes
2014 | 2294 | 0819070237 | Buckeye Power Greenville Station | 5119 Sebring Warner Road | Greenville | 45331 |  | Darke | B001 | 269.71 mmBtu/hr natural gas/No. 2 oil, simple cycle combustion turbine with water injection nitrogen oxides reduction system; G1CT1 | 2014-07-29 | WATER INJECTION | Mostardi Platt | 25 MW | 29.9 lb NOx/hr; <25 ppmvd@15%O2 | 11 MW | 12.6 lb NOx/hr; 21.9 ppmvd@15%O2 | 7E | Nitrogen Dioxide | PASS | NA | Y | Unit G1CT1Low Mass Emission Test Low Load Demonstration: Facility tested to provide data to support it as a Low Mass Emitter per 40 CFR 75.19 and to establish emission rates for NOx and Carbon Monoxide. This was a repeated testing effort as first attempt in June showed exceedances of CO emission rates at higher operating levels apparently due to facility calculation error and establishment of wrong water to fuel ratio. The water to fuel ratio submitted at 0.84. Heat Input measured 146 mmBtu/hr. Natural gas usage approx. 138633 cf. | Yes
2014 | 2296 | 0819070237 | Buckeye Power Greenville Station | 5119 Sebring Warner Road | Greenville | 45331 |  | Darke | B002 | 269.71 mmBtu/hr natural gas/No. 2 oil, simple cycle combustion turbine with water injection nitrogen oxides reduction system; G1CT2 | 2014-07-29 | WATER INJECTION | Mostardi Platt | 25 MW | 29.9 lb NOx/hr; <25ppmvd@15%O2 | 13 MW | 14.6 lb NOx/ hr; 22ppmvd@15%O2 | 7E | Nitrogen Oxide | PASS | NA | Y | Unit G1CT2 Mass Emission Test LOW Load Demonstration: Facility tested to provide data to support it as a Low Mass Emitter per 40 CFR 75.19 and to establish emission rates for NOx and Carbon Monoxide. This was a repeated testing effort as first attempt in June showed exceedances of CO emission rates at higher operating levels apparently due to facility calculation error and establishment of wrong water to fuel ratio. The water to fuel ratio submitted at 0.88. Heat Input measured 166 lb/MMbtu. Natural Gas usage approx. 158307 cf. | Yes
2014 | 2297 | 0819070237 | Buckeye Power Greenville Station | 5119 Sebring Warner Road | Greenville | 45331 |  | Darke | B002 | 269.71 mmBtu/hr natural gas/No. 2 oil, simple cycle combustion turbine with water injection nitrogen oxides reduction system; G1CT2 | 2014-07-29 | WATER INJECTION | Mostardi Platt | 25 MW | 29.9 lb NOx/hr; <25ppmvd@15%O2 | 13 MW | 14.6 lb NOx/ hr; 22ppmvd@15%O2 | 7E | Nitrogen Dioxide | PASS | NA | Y | Unit G1CT2 Mass Emission Test LOW Load Demonstration: Facility tested to provide data to support it as a Low Mass Emitter per 40 CFR 75.19 and to establish emission rates for NOx and Carbon Monoxide. This was a repeated testing effort as first attempt in June showed exceedances of CO emission rates at higher operating levels apparently due to facility calculation error and establishment of wrong water to fuel ratio. The water to fuel ratio submitted at 0.88. Heat Input measured 166 lb/MMbtu. Natural Gas usage approx. 158307 cf. | Yes
2014 | 2298 | 0819070237 | Buckeye Power Greenville Station | 5119 Sebring Warner Road | Greenville | 45331 |  | Darke | B001 | 269.71 mmBtu/hr natural gas/No. 2 oil, simple cycle combustion turbine with water injection nitrogen oxides reduction system; G1CT1 | 2014-07-30 | WATER INJECTION | Mostardi Platt | 25 MW | 29.9 lb NOx/hr; <25ppmvd NOx@15%O2 | 16 MW | 16.3 lb NOx/hr; 21ppmvd NOx@15%O2 | 7E | Nitrogen Dioxide | PASS | NA | Y | Unit G1CT1 Mass Emission Test LOW/MID Load Demonstration: Facility tested to provide data to support it as a Low Mass Emitter per 40 CFR 75.19 and to establish emission rates for NOx and Carbon Monoxide. This was a repeated testing effort as first attempt in June showed exceedances of CO emission rates at higher operating levels apparently due to facility calculation error and establishment of wrong water to fuel ratio. The water to fuel ratio submitted at 0.91. Heat Input measured 190 lb/MMbtu. Natural Gas usage approx. 180800 cf. | Yes
2014 | 2300 | 0819070237 | Buckeye Power Greenville Station | 5119 Sebring Warner Road | Greenville | 45331 |  | Darke | B001 | 269.71 mmBtu/hr natural gas/No. 2 oil, simple cycle combustion turbine with water injection nitrogen oxides reduction system; G1CT1 | 2014-07-30 | WATER INJECTION | Mostardi Platt | 25 MW | 29.9 lb NOx/hr; <25ppmvd NOx@15%O2 | 16 MW | 16.3 lb NOx/hr; 21ppmvd NOx@15%O2 | 7E | Nitrogen Oxide | PASS | NA | Y | Unit G1CT1 Mass Emission Test LOW/MID Load Demonstration: Facility tested to provide data to support it as a Low Mass Emitter per 40 CFR 75.19 and to establish emission rates for NOx and Carbon Monoxide. This was a repeated testing effort as first attempt in June showed exceedances of CO emission rates at higher operating levels apparently due to facility calculation error and establishment of wrong water to fuel ratio. The water to fuel ratio submitted at 0.91. Heat Input measured 190 lb/MMbtu. Natural Gas usage approx. 180800 cf. | Yes
2014 | 2302 | 0819070237 | Buckeye Power Greenville Station | 5119 Sebring Warner Road | Greenville | 45331 |  | Darke | B002 | 269.71 mmBtu/hr natural gas/No. 2 oil, simple cycle combustion turbine with water injection nitrogen oxides reduction system; G1CT2 | 2014-07-30 | WATER INJECTION | Mostardi Platt | 25 MW | 29.9 lbNOx/hr; <25ppmvdNOx@15%O2 | 18 MW | 19.0 lb NOx/hr; 22ppmvd@15%O3 | 7E | Nitrogen Dioxide | PASS | NA | Y | Unit G1CT2 Mass Emission Test LOW/MID Load Demonstration: Facility tested to provide data to support it as a Low Mass Emitter per 40 CFR 75.19 and to establish emission rates for NOx and Carbon Monoxide. This was a repeated testing effort as first attempt in June showed exceedances of CO emission rates at higher operating levels apparently due to facility calculation error and establishment of wrong water to fuel ratio. The water to fuel ratio submitted at 0.90. Heat Input measured 205 lb/MMbtu. Natural Gas usage approx. 195240 cf. | Yes
2014 | 2303 | 0819070237 | Buckeye Power Greenville Station | 5119 Sebring Warner Road | Greenville | 45331 |  | Darke | B002 | 269.71 mmBtu/hr natural gas/No. 2 oil, simple cycle combustion turbine with water injection nitrogen oxides reduction system; G1CT2 | 2014-07-30 | WATER INJECTION | Mostardi Platt | 25 MW | 29.9 lbNOx/hr; <25ppmvdNOx@15%O2 | 18 MW | 19.0 lb NOx/hr; 22ppmvd@15%O3 | 7E | Nitrogen Oxide | PASS | NA | Y | Unit G1CT2 Mass Emission Test LOW/MID Load Demonstration: Facility tested to provide data to support it as a Low Mass Emitter per 40 CFR 75.19 and to establish emission rates for NOx and Carbon Monoxide. This was a repeated testing effort as first attempt in June showed exceedances of CO emission rates at higher operating levels apparently due to facility calculation error and establishment of wrong water to fuel ratio. The water to fuel ratio submitted at 0.90. Heat Input measured 205 lb/MMbtu. Natural Gas usage approx. 195240 cf. | Yes
2014 | 2304 | 0819070237 | Buckeye Power Greenville Station | 5119 Sebring Warner Road | Greenville | 45331 |  | Darke | B005 | 269.71 mmBtu/hr natural gas/No. 2 oil, simple cycle combustion turbine with water injection nitrogen oxides reduction system; G3CT1 | 2014-07-30 | WATER INJECTION | Mostardi Platt | 25 MW | 29.9 lb NOx/hr; <25ppmvd @ 15%O2 | 25 MW | 24.0 lbNOx/hr; 21ppmvd @ 15%O2 | 7E | Nitrogen Oxide | PASS | NA | Y | Unit G3CT1 Mass Emission Test HIGH Load Demonstration: Facility tested to provide data to support it as a Low Mass Emitter per 40 CFR 75.19 and to establish emission rates for NOx and Carbon Monoxide. This was a repeated testing effort as first attempt in June showed exceedances of CO emission rates at higher operating levels apparently due to facility calculation error and establishment of wrong water to fuel ratio. The water to fuel ratio submitted at 1.01. Heat Input measured 277 lb/MMbtu. Natural Gas usage approx. 263970 cf. Actual test date 07/31/2014. | Yes
2014 | 2305 | 0819070237 | Buckeye Power Greenville Station | 5119 Sebring Warner Road | Greenville | 45331 |  | Darke | B005 | 269.71 mmBtu/hr natural gas/No. 2 oil, simple cycle combustion turbine with water injection nitrogen oxides reduction system; G3CT1 | 2014-07-30 | WATER INJECTION | Mostardi Platt | 25 MW | 29.9 lb NOx/hr; <25ppmvd @ 15%O2 | 25 MW | 24.0 lbNOx/hr; 21ppmvd @ 15%O2 | 7E | Nitrogen Dioxide | PASS | NA | Y | Unit G3CT1 Mass Emission Test HIGH Load Demonstration: Facility tested to provide data to support it as a Low Mass Emitter per 40 CFR 75.19 and to establish emission rates for NOx and Carbon Monoxide. This was a repeated testing effort as first attempt in June showed exceedances of CO emission rates at higher operating levels apparently due to facility calculation error and establishment of wrong water to fuel ratio. The water to fuel ratio submitted at 1.01. Heat Input measured 277 lb/MMbtu. Natural Gas usage approx. 263970 cf. Actual test date 07/31/2014. | Yes
2014 | 2307 | 0819070237 | Buckeye Power Greenville Station | 5119 Sebring Warner Road | Greenville | 45331 |  | Darke | B001 | 269.71 mmBtu/hr natural gas/No. 2 oil, simple cycle combustion turbine with water injection nitrogen oxides reduction system; G1CT1 | 2014-07-31 | WATER INJECTION | Mostardi Platt | 25 MW | 29.9 lb NOx/hr; <25ppmvd NOx@15%O2 | 20 MW | 20.6 lb NOx/hr; 22 ppmvd NOx@15%O2 | 7E | Nitrogen Dioxide | PASS | NA | Y | Unit G1CT1 Mass Emission Test MID/HIGH Load Demonstration: Facility tested to provide data to support it as a Low Mass Emitter per 40 CFR 75.19 and to establish emission rates for NOx and Carbon Monoxide. This was a repeated testing effort as first attempt in June showed exceedances of CO emission rates at higher operating levels apparently due to facility calculation error and establishment of wrong water to fuel ratio. The water to fuel ratio submitted at 0.95. Heat Input measured 222 lb/MMbtu. Natural Gas usage approx. 211117 cf. Actual test date 07/30/2014. | Yes
2014 | 2308 | 0819070237 | Buckeye Power Greenville Station | 5119 Sebring Warner Road | Greenville | 45331 |  | Darke | B001 | 269.71 mmBtu/hr natural gas/No. 2 oil, simple cycle combustion turbine with water injection nitrogen oxides reduction system; G1CT1 | 2014-07-31 | WATER INJECTION | Mostardi Platt | 25 MW | 29.9 lb NOx/hr; <25ppmvd NOx@15%O2 | 20 MW | 20.6 lb NOx/hr; 22ppmvd NOx@15%O2 | 7E | Nitrogen Oxide | PASS | NA | Y | Unit G1CT1 Mass Emission Test MID/HIGH Load Demonstration: Facility tested to provide data to support it as a Low Mass Emitter per 40 CFR 75.19 and to establish emission rates for NOx and Carbon Monoxide. This was a repeated testing effort as first attempt in June showed exceedances of CO emission rates at higher operating levels apparently due to facility calculation error and establishment of wrong water to fuel ratio. The water to fuel ratio submitted at 0.95. Heat Input measured 222 lb/MMbtu. Natural Gas usage approx. 211117 cf. Actual test date 07/30/2014. | Yes
2014 | 2310 | 0819070237 | Buckeye Power Greenville Station | 5119 Sebring Warner Road | Greenville | 45331 |  | Darke | B002 | 269.71 mmBtu/hr natural gas/No. 2 oil, simple cycle combustion turbine with water injection nitrogen oxides reduction system; G1CT2 | 2014-07-31 | WATER INJECTION | Mostardi Platt | 25 MW | 29.9 lb NOx/hr; <25ppmvd@15%O2 | 27 MW | 27.4 lb NOx/ hr; 22ppmvd@15%O2 | 7E | Nitrogen Oxide | PASS | NA | Y | Unit G1CT2 Mass Emission Test HIGH Load Demonstration: Facility tested to provide data to support it as a Low Mass Emitter per 40 CFR 75.19 and to establish emission rates for NOx and Carbon Monoxide. This was a repeated testing effort as first attempt in June showed exceedances of CO emission rates at higher operating levels apparently due to facility calculation error and establishment of wrong water to fuel ratio. The water to fuel ratio submitted at 0.99. Heat Input measured 286 lb/MMbtu. Natural Gas usage approx. 272474 cf. Actual test date 07/29/14. | Yes
2014 | 2312 | 0819070237 | Buckeye Power Greenville Station | 5119 Sebring Warner Road | Greenville | 45331 |  | Darke | B002 | 269.71 mmBtu/hr natural gas/No. 2 oil, simple cycle combustion turbine with water injection nitrogen oxides reduction system; G1CT2 | 2014-07-31 | WATER INJECTION | Mostardi Platt | 25 MW | 29.9 lb NOx/hr; <25ppmvd@15%O2 | 27 MW | 27.4 lb NOx/ hr; 22ppmvd@15%O2 | 7E | Nitrogen Dioxide | PASS | NA | Y | Unit G1CT2 Mass Emission Test HIGH Load Demonstration: Facility tested to provide data to support it as a Low Mass Emitter per 40 CFR 75.19 and to establish emission rates for NOx and Carbon Monoxide. This was a repeated testing effort as first attempt in June showed exceedances of CO emission rates at higher operating levels apparently due to facility calculation error and establishment of wrong water to fuel ratio. The water to fuel ratio submitted at 0.99. Heat Input measured 286 lb/MMbtu. Natural Gas usage approx. 272474 cf. Actual test date 07/29/14. | Yes
2014 | 2313 | 0819070237 | Buckeye Power Greenville Station | 5119 Sebring Warner Road | Greenville | 45331 |  | Darke | B005 | 269.71 mmBtu/hr natural gas/No. 2 oil, simple cycle combustion turbine with water injection nitrogen oxides reduction system; G3CT1 | 2014-07-31 | WATER INJECTION | Mostardi Platt | 25 MW | 29.9 lb NOx/hr; <25ppmvd @ 15%O2 | 12 MW | 13.8 lb NOx /hr; 20.4ppmvd @ 15%O2 | 7E | Nitrogen Dioxide | PASS | NA | Y | Unit G3CT1 Mass Emission Test LOW Load Demonstration: Facility tested to provide data to support it as a Low Mass Emitter per 40 CFR 75.19 and to establish emission rates for NOx and Carbon Monoxide. This was a repeated testing effort as first attempt in June showed exceedances of CO emission rates at higher operating levels apparently due to facility calculation error and establishment of wrong water to fuel ratio. The water to fuel ratio submitted at 0.90. Heat Input measured 168 lb/MMbtu. Natural Gas usage approx. 159980 cf. | Yes
2014 | 2314 | 0819070237 | Buckeye Power Greenville Station | 5119 Sebring Warner Road | Greenville | 45331 |  | Darke | B005 | 269.71 mmBtu/hr natural gas/No. 2 oil, simple cycle combustion turbine with water injection nitrogen oxides reduction system; G3CT1 | 2014-07-31 | WATER INJECTION | Mostardi Platt | 25 MW | 29.9 lb NOx/hr; <25ppmvd @ 15%O2 | 12 MW | 13.8 lb NOx /hr; 20.4ppmvd @ 15%O2 | 7E | Nitrogen Oxide | PASS | NA | Y | Unit G3CT1 Mass Emission Test LOW Load Demonstration: Facility tested to provide data to support it as a Low Mass Emitter per 40 CFR 75.19 and to establish emission rates for NOx and Carbon Monoxide. This was a repeated testing effort as first attempt in June showed exceedances of CO emission rates at higher operating levels apparently due to facility calculation error and establishment of wrong water to fuel ratio. The water to fuel ratio submitted at 0.90. Heat Input measured 168 lb/MMbtu. Natural Gas usage approx. 159980 cf. | Yes
2014 | 2316 | 0819070237 | Buckeye Power Greenville Station | 5119 Sebring Warner Road | Greenville | 45331 |  | Darke | B005 | 269.71 mmBtu/hr natural gas/No. 2 oil, simple cycle combustion turbine with water injection nitrogen oxides reduction system; G3CT1 | 2014-08-01 | WATER INJECTION | Mostardi Platt | 25 MW | 29.9 lb NOx/hr; <25ppmvd @ 15%O2 | 16 MW | 16.2 lbNOx/hr; 20ppmvd @ 15%O2 | 7E | Nitrogen Dioxide | PASS | NA | Y | Unit G3CT1 Mass Emission Test LOW/MID Load Demonstration: Facility tested to provide data to support it as a Low Mass Emitter per 40 CFR 75.19 and to establish emission rates for NOx and Carbon Monoxide. This was a repeated testing effort as first attempt in June showed exceedances of CO emission rates at higher operating levels apparently due to facility calculation error and establishment of wrong water to fuel ratio. The water to fuel ratio submitted at 0.96. Heat Input measured 203 lb/MMbtu. Natural Gas usage approx. 193097 cf. | Yes
2014 | 2317 | 0819070237 | Buckeye Power Greenville Station | 5119 Sebring Warner Road | Greenville | 45331 |  | Darke | B005 | 269.71 mmBtu/hr natural gas/No. 2 oil, simple cycle combustion turbine with water injection nitrogen oxides reduction system; G3CT1 | 2014-08-01 | WATER INJECTION | Mostardi Platt | 25 MW | 29.9 lb NOx/hr; <25ppmvd @ 15%O2 | 16 MW | 16.2 lbNOx/hr; 20ppmvd @ 15%O2 | 7E | Nitrogen Oxide | PASS | NA | Y | Unit G3CT1 Mass Emission Test LOW/MID Load Demonstration: Facility tested to provide data to support it as a Low Mass Emitter per 40 CFR 75.19 and to establish emission rates for NOx and Carbon Monoxide. This was a repeated testing effort as first attempt in June showed exceedances of CO emission rates at higher operating levels apparently due to facility calculation error and establishment of wrong water to fuel ratio. The water to fuel ratio submitted at 0.96. Heat Input measured 203 lb/MMbtu. Natural Gas usage approx. 193097 cf. | Yes
2014 | 2319 | 0819070237 | Buckeye Power Greenville Station | 5119 Sebring Warner Road | Greenville | 45331 |  | Darke | B005 | 269.71 mmBtu/hr natural gas/No. 2 oil, simple cycle combustion turbine with water injection nitrogen oxides reduction system; G3CT1 | 2014-08-02 | WATER INJECTION | Mostardi Platt | 25 MW | 29.9 lb NOx/hr; <25ppmvd @ 15%O2 | 21 MW | 20.3 lbNOx/hr; 20ppmvd @ 15%O2 | 7E | Nitrogen Oxide | PASS | NA | Y | Unit G3CT1 Mass Emission Test MID/HIGH Load Demonstration: Facility tested to provide data to support it as a Low Mass Emitter per 40 CFR 75.19 and to establish emission rates for NOx and Carbon Monoxide. This was a repeated testing effort as first attempt in June showed exceedances of CO emission rates at higher operating levels apparently due to facility calculation error and establishment of wrong water to fuel ratio. The water to fuel ratio submitted at 1.05. Heat Input measured 246 lb/MMbtu. Natural Gas usage approx. 234293 cf. Actual test date 08/01/2014 | Yes
2014 | 2320 | 0819070237 | Buckeye Power Greenville Station | 5119 Sebring Warner Road | Greenville | 45331 |  | Darke | B005 | 269.71 mmBtu/hr natural gas/No. 2 oil, simple cycle combustion turbine with water injection nitrogen oxides reduction system; G3CT1 | 2014-08-02 | WATER INJECTION | Mostardi Platt | 25 MW | 29.9 lb NOx/hr; <25ppmvd @ 15%O2 | 21 MW | 20.3 lbNOx/hr; 20ppmvd @ 15%O2 | 7E | Nitrogen Dioxide | PASS | NA | Y | Unit G3CT1 Mass Emission Test MID/HIGH Load Demonstration: Facility tested to provide data to support it as a Low Mass Emitter per 40 CFR 75.19 and to establish emission rates for NOx and Carbon Monoxide. This was a repeated testing effort as first attempt in June showed exceedances of CO emission rates at higher operating levels apparently due to facility calculation error and establishment of wrong water to fuel ratio. The water to fuel ratio submitted at 1.05. Heat Input measured 246 lb/MMbtu. Natural Gas usage approx. 234293 cf. Actual test date 08/01/2014 | Yes
2014 | 2413 | 0857043333 | DP&L Tait Generating Station | 2101 Arbor Boulevard | Moraine | 45439 | 1762 | Montgomery | P007 | 80 MW (1115 mmBtu/hr nominal heat input) natural gas or fuel oil fired simple cycle turbine with water injection and dry low NOx (DLN) combustor controls, CT-3 | 2014-05-22 | CT-1(Other): Max. controlled emission rate = permit limit; CT-2(Other): Max. controlled emission rate = permit limit; CT-3(gas)(Other): Max. controlled emission rate = permit limit; CT-3(gas)(Other): Max. controlled emission rate = permit limit | Grace Consulting, Inc. | 80 MW | 15 ppmvd @ 15% O2 | 72 MW | 12 ppmvd @ 15% O2 | 7E | Nitrogen Oxide | PASS | NA | Y | Retest due to maintenance on unit. Facility supplied support to operate this retest at one operating load based on capacity factor. The Reference temperature averaged at 2032 degrees Fahrenheit. | Yes
2014 | 2414 | 0857043333 | DP&L Tait Generating Station | 2101 Arbor Boulevard | Moraine | 45439 | 1762 | Montgomery | P007 | 80 MW (1115 mmBtu/hr nominal heat input) natural gas or fuel oil fired simple cycle turbine with water injection and dry low NOx (DLN) combustor controls, CT-3 | 2014-05-22 | CT-1(Other): Max. controlled emission rate = permit limit; CT-2(Other): Max. controlled emission rate = permit limit; CT-3(gas)(Other): Max. controlled emission rate = permit limit; CT-3(gas)(Other): Max. controlled emission rate = permit limit | Grace Consulting, Inc. | 80 MW | 15 ppmvd @ 15% O2 | 72 MW | 12 ppmvd @ 15% O2 | 7E | Nitrogen Dioxide | PASS | NA | Y | Retest due to maintenance on unit. Facility supplied support to operate this retest at one operating load based on capacity factor. The Reference temperature averaged at 2032 degrees Fahrenheit. | Yes
2014 | 2415 | 0857043333 | DP&L Tait Generating Station | 2101 Arbor Boulevard | Moraine | 45439 | 1762 | Montgomery | P005 | 80 MW (1115 mmBtu/hr nominal heat input) natural gas or fuel oil fired simple cycle turbine with water injection controls, CT-1 | 2014-12-18 | CT-1(Other): Max. controlled emission rate = permit limit; CT-2(Other): Max. controlled emission rate = permit limit; CT-3(gas)(Other): Max. controlled emission rate = permit limit; CT-3(gas)(Other): Max. controlled emission rate = permit limit | Grace Consulting, Inc. | 80MW | 25ppmvd@15%O2 | 86MW | 21ppmvd | 7E | Nitrogen Dioxide | PASS | NA | Y | Another LME retest due to the installation of a new water injection system. The requirement then being to re-establish the water to fuel ratio. This test was run at the same load as the initial December 2012 tests. | Yes
2014 | 2416 | 0857043333 | DP&L Tait Generating Station | 2101 Arbor Boulevard | Moraine | 45439 | 1762 | Montgomery | P005 | 80 MW (1115 mmBtu/hr nominal heat input) natural gas or fuel oil fired simple cycle turbine with water injection controls, CT-1 | 2014-12-18 | CT-1(Other): Max. controlled emission rate = permit limit; CT-2(Other): Max. controlled emission rate = permit limit; CT-3(gas)(Other): Max. controlled emission rate = permit limit; CT-3(gas)(Other): Max. controlled emission rate = permit limit | Grace Consulting, Inc. | 80MW | 25ppmvd@15%O2 | 86MW | 21ppmvd | 7E | Nitrogen Oxide | PASS | NA | Y | Another LME retest due to the installation of a new water injection system. The requirement then being to re-establish the water to fuel ratio. This test was run at the same load as the initial December 2012 tests. | Yes
2015 | 974 | 0684015015 | DTE Marietta | 17005 State Route 7 | Marietta | 45750 |  | Washington | P001 | 8 MW Turbine and heat recovery steam generator (HRSG) - Natural Gas | 2015-03-02 | SCR(NOx Reduction Technology): Selective Catalytic Reduction (SCR) | Montrose Environmental Group | 83.3 mm btu/hr | 25.0 ppm | 75 mm btu/hr 91% steam load | 16.7 ppm | 7E | Nitrogen Dioxide | PP | NA | Y | turbine and HRSG combined | Yes
2016 | 989 | 0381000043 | Robert P. Mone Plant | 4406 Mentzer Road | Convoy | 45832 |  | Van Wert | P001 | GE-7FA simple cycle combustion turbine | 2016-02-02 | Low NOx burners/water injection system | Mostardi Platt | 180 MW | 42 ppmvd at 15% O2 347 lbs/hr | 188.7 MW | 36.0 ppmvd at 15% O2 281.46 lbs/hr | 7E | Nitrogen Dioxide | PP | Y | NA | Fuel was no. 2 oil/distillate oil | Yes
2016 | 992 | 0381000043 | Robert P. Mone Plant | 4406 Mentzer Road | Convoy | 45832 |  | Van Wert | P002 | GE-7FA simple cycle combustion turbine | 2016-02-03 | Low NOx burners/water injection system | Mostardi Platt | 178 MW | 42 ppmvd at 15% O2 347 lbs/hr | 185 MW | 39.9 ppmvd at 15% O2 314.54 lbs/hr | 7E | Nitrogen Dioxide | PP | Y | NA | Emission rate of 39.9 ppmvd at 15% O2 is a one hour average Fuel was No. 2 oil/distillate oil | Yes
2016 | 995 | 0381000043 | Robert P. Mone Plant | 4406 Mentzer Road | Convoy | 45832 |  | Van Wert | P003 | GE-7FA simple cycle combustion turbine | 2016-02-04 | Low NOx burners/water injection system | Mostardi Platt | 189 MW | 42 ppmvd at15% O2 347.0 lbs/hr | 196 MW | 37.9 ppmvd at 15% O2 314.34 lbs/hr | 7E | Nitrogen Dioxide | PP | Y | NA | Emission rate of 37.9 ppmvd is a one hour average. The allowable emission rate of 42 ppmvd is a one hour average. Fuel was No. 2 oil/distillate oil. | Yes
2016 | 1765 | 0684000212 | Washington Energy Facility | 859 Ohio 83 | Beverly | 45715 | 1329 | Washington | P001 | Nominally Rated 207 MW GE 7FA - Natural-Gas Fired Dry Low NOx (DLN) Combustion Turbine with duct firing operating in combined cycle mode controlled by Selective Catalytic Reduction (SCR) | 2016-06-29 | SCR #1(Other): 32.3 lb/hr with duct burner firing(24.7 lb/hr w/o); SCR #2(Other): 32.3 lb/hr with duct burner firing(24.7 lb/hr w/o) | Mostardi Platt | 207 MW | 31.5 lb/hr burners on 25.0 lb/hr burners off | 187 MW | 19.5 lbs/hr 24.2 lbs/hr | 7E | Nitrogen Dioxide | PP | Y | NA |  | Yes
2016 | 1766 | 0684000212 | Washington Energy Facility | 859 Ohio 83 | Beverly | 45715 | 1329 | Washington | P002 | Nominally Rated 207 MW GE 7FA - Natural-Gas Fired Dry Low NOx (DLN) Combustion Turbine with duct firing operating in combined cycle mode controlled by Selective Catalytic Reduction (SCR) | 2016-06-29 | SCR #1(Other): 32.3 lb/hr with duct burner firing(24.7 lb/hr w/o); SCR #2(Other): 32.3 lb/hr with duct burner firing(24.7 lb/hr w/o) | Mostardi Platt | 185 MW 186 MW | 31.5 lbs/hr burners on 25.0 lbs/hr burners off | 185 MW 186 MW | 23.5 lbs/hr 18.7 lbs/hr | 7E | Nitrogen Dioxide | PP | Y | NA |  | Yes
2016 | 1912 | 0857043333 | DP&L Tait Generating Station | 2101 Arbor Boulevard | Moraine | 45439 | 1762 | Montgomery | P005 | 80 MW (1115 mmBtu/hr nominal heat input) natural gas or fuel oil fired simple cycle turbine with water injection controls, CT-1 | 2016-03-11 | CT-1(Other): Max. controlled emission rate = permit limit; CT-2(Other): Max. controlled emission rate = permit limit; CT-3(gas)(Other): Max. controlled emission rate = permit limit; CT-3(gas)(Other): Max. controlled emission rate = permit limit | Mostardi Platt, Inc. | 80MW | 42ppmvd@15%O2;195lb/hrNOx | 81MW | 26ppmvd@15%O2; 99 lb/hr NOx | 7E | Nitrogen Oxide | PP | Y | NA | Low Mass Emissions test to determine unit emissions while burning #2 fuel oil. Additional tests at differing loads where performed to establish water to fuel ratios. At standard operations, P005 water to fuel ration was 1.27 at 80MW. With additional wa | Yes
2016 | 1913 | 0857043333 | DP&L Tait Generating Station | 2101 Arbor Boulevard | Moraine | 45439 | 1762 | Montgomery | P005 | 80 MW (1115 mmBtu/hr nominal heat input) natural gas or fuel oil fired simple cycle turbine with water injection controls, CT-1 | 2016-03-11 | CT-1(Other): Max. controlled emission rate = permit limit; CT-2(Other): Max. controlled emission rate = permit limit; CT-3(gas)(Other): Max. controlled emission rate = permit limit; CT-3(gas)(Other): Max. controlled emission rate = permit limit | Mostardi Platt, Inc. | 80MW | 42ppmvd@15%O2;195lb/hrNOx | 81MW | 26ppmvd@15%O2; 99 lb/hr NOx | 7E | Nitrogen Dioxide | PP | Y | NA | Low Mass Emissions test to determine unit emissions while burning #2 fuel oil. Additional tests at differing loads where performed to establish water to fuel ratios. At standard operations, P005 water to fuel ration was 1.27 at 80MW. With additional wa | Yes
2016 | 1914 | 0857043333 | DP&L Tait Generating Station | 2101 Arbor Boulevard | Moraine | 45439 | 1762 | Montgomery | P006 | 80 MW (1115 mmBtu/hr nominal heat input) natural gas or fuel oil fired simple cycle turbine with water injection controls, CT-2 | 2016-03-11 | CT-1(Other): Max. controlled emission rate = permit limit; CT-2(Other): Max. controlled emission rate = permit limit; CT-3(gas)(Other): Max. controlled emission rate = permit limit; CT-3(gas)(Other): Max. controlled emission rate = permit limit | Mostardi Platt, Inc. | 80MW | 42ppmvd@15%O2;195lb/hrNOx | 81MW | 25ppmvd@15%O2; 93 lb/hr NOx | 7E | Nitrogen Dioxide | PP | Y | NA | Low Mass Emissions test to determine unit emissions while burning #2 fuel oil. Additional tests at differing loads where performed to establish water to fuel ratios. At standard operations, P005 water to fuel ration was 1.27 at 80MW. With additional wa | Yes
2016 | 1915 | 0857043333 | DP&L Tait Generating Station | 2101 Arbor Boulevard | Moraine | 45439 | 1762 | Montgomery | P006 | 80 MW (1115 mmBtu/hr nominal heat input) natural gas or fuel oil fired simple cycle turbine with water injection controls, CT-2 | 2016-03-11 | CT-1(Other): Max. controlled emission rate = permit limit; CT-2(Other): Max. controlled emission rate = permit limit; CT-3(gas)(Other): Max. controlled emission rate = permit limit; CT-3(gas)(Other): Max. controlled emission rate = permit limit | Mostardi Platt, Inc. | 80MW | 42ppmvd@15%O2;195lb/hrNOx | 81MW | 25ppmvd@15%O2; 93 lb/hr NOx | 7E | Nitrogen Oxide | PP | Y | NA | Low Mass Emissions test to determine unit emissions while burning #2 fuel oil. Additional tests at differing loads where performed to establish water to fuel ratios. At standard operations, P005 water to fuel ration was 1.27 at 80MW. With additional wa | Yes
2016 | 1916 | 0857043333 | DP&L Tait Generating Station | 2101 Arbor Boulevard | Moraine | 45439 | 1762 | Montgomery | P007 | 80 MW (1115 mmBtu/hr nominal heat input) natural gas or fuel oil fired simple cycle turbine with water injection and dry low NOx (DLN) combustor controls, CT-3 | 2016-03-11 | CT-1(Other): Max. controlled emission rate = permit limit; CT-2(Other): Max. controlled emission rate = permit limit; CT-3(gas)(Other): Max. controlled emission rate = permit limit; CT-3(gas)(Other): Max. controlled emission rate = permit limit | Mostardi Platt, Inc. | 80MW | 42ppmvd@15%O2;195lb/hrNOx | 80MW | 28ppmvd@15%O2; 100 lb/hr NOx | 7E | Nitrogen Dioxide | PP | Y | NA | Low Mass Emissions test to determine unit emissions while burning #2 fuel oil. Additional tests at differing loads where performed to establish water to fuel ratios. At standard operations, P005 water to fuel ration was 1.27 at 80MW. With additional wa | Yes
2016 | 1917 | 0857043333 | DP&L Tait Generating Station | 2101 Arbor Boulevard | Moraine | 45439 | 1762 | Montgomery | P007 | 80 MW (1115 mmBtu/hr nominal heat input) natural gas or fuel oil fired simple cycle turbine with water injection and dry low NOx (DLN) combustor controls, CT-3 | 2016-03-11 | CT-1(Other): Max. controlled emission rate = permit limit; CT-2(Other): Max. controlled emission rate = permit limit; CT-3(gas)(Other): Max. controlled emission rate = permit limit; CT-3(gas)(Other): Max. controlled emission rate = permit limit | Mostardi Platt, Inc. | 80MW | 42ppmvd@15%O2;195lb/hrNOx | 80MW | 28ppmvd@15%O2; 100 lb/hr NOx | 7E | Nitrogen Oxide | PP | Y | NA | Low Mass Emissions test to determine unit emissions while burning #2 fuel oil. Additional tests at differing loads where performed to establish water to fuel ratios. At standard operations, P005 water to fuel ration was 1.27 at 80MW. With additional wa | Yes
2016 | 2207 | 1409120656 | Duke Energy Kentucky, Woodsdale Generating Station | 2100 Woodsdale Road | Trenton | 45067 | 0000 | Butler | B002 | 1034 MMBtu/Hr simple cycle combustion turbine w/ low NOx burner and water injection | 2016-05-18 | NA | Mostardi Platt | 90 MW | 0.253 lb/MMBtu; 42 ppm@15% O2 | See Memo Field | See Memo Field | 7E | Nitrogen Oxide | PP | Y | NA | ITT in STARS 2 - Compliance Report ID #101883 Test Report in STARS 2 - Compliance Report ID#102558 LOAD MW LB/MMBTU PPM@15% O2 High 89.5 0.106 28.69 Mid-High 60.6 | Yes
2016 | 2208 | 1409120656 | Duke Energy Kentucky, Woodsdale Generating Station | 2100 Woodsdale Road | Trenton | 45067 | 0000 | Butler | B002 | 1034 MMBtu/Hr simple cycle combustion turbine w/ low NOx burner and water injection | 2016-05-18 | NA | Mostardi Platt | 90 MW | 0.253 lb/MMBtu; 42 ppm@15% O2 | See Memo Field | See Memo Field | 7E | Nitrogen Dioxide | PP | Y | NA | ITT in STARS 2 - Compliance Report ID #101883 Test Report in STARS 2 - Compliance Report ID#102558 LOAD MW LB/MMBTU PPM@15% O2 High 89.5 0.106 28.69 Mid-High 60.6 | Yes
2016 | 324 | 0165000132 | AEP Generation Resources Inc., - Darby Plant | 12509 Adkins Road | Mt. Sterling | 43143 | 9061 | Pickaway | P001 | Natural Gas or number two fuel oil-fired, simple cycle, combustion turbine having a nominal capacity of 1,115.2 MMBTU/hr (80 MW, nominal), controlled with a dry low NOx combustor; CT1 - Combustion Turbine No.1; *Modified | 2016-12-14 | PCT1(Other): Water Injection for NOx reduction during periods when distillate oil is used as fuel.; PCT2(Other): Water Injection for NOx reduction during periods when distillate oil is used as fuel; PCT3(Other): Water injection for NOx reduction during pe | Mostardi Platt | 80 MW, nominal | 269.0 lb/hr and 42 ppmvd @ 15% oxygen | 92 MWe | 166.8 lb/hr and 37 ppmvd @ 15% oxygen | 7E | Nitrogen Oxide | PP | Y | NA | This test was conducted to establish fuel-and-unit specific NOx emissions rates while burning No. 2 fuel oil in accordance with the low mass emissions unit provisions in 40 CFR 75.19. Emissions units P001, P002, P003, and P004 are identical units and qu | Yes
2016 | 325 | 0165000132 | AEP Generation Resources Inc., - Darby Plant | 12509 Adkins Road | Mt. Sterling | 43143 | 9061 | Pickaway | P002 | Natural Gas or number two fuel oil-fired, simple cycle, combustion turbine having a nominal capacity of 1,115.2 MMBTU/hr (80 MW, nominal), controlled with a dry low NOx combustor; CT2 - Combustion Turbine No.2; *Modified | 2016-12-14 | PCT1(Other): Water Injection for NOx reduction during periods when distillate oil is used as fuel.; PCT2(Other): Water Injection for NOx reduction during periods when distillate oil is used as fuel; PCT3(Other): Water injection for NOx reduction during pe | Mostardi Platt | 80 MW, nominal | 269.0 lb/hr and 42 ppmvd @ 15% oxygen | 92 MWe | 161.0 lb/hr and 38 ppmvd @ 15% oxygen | 7E | Nitrogen Oxide | PP | Y | NA | This test was conducted to establish fuel-and-unit specific NOx emissions rates while burning No. 2 fuel oil in accordance with the low mass emissions unit provisions in 40 CFR 75.19. Emissions units P001, P002, P003, and P004 are identical units and qu | Yes
2016 | 326 | 0165000132 | AEP Generation Resources Inc., - Darby Plant | 12509 Adkins Road | Mt. Sterling | 43143 | 9061 | Pickaway | P003 | Natural Gas or number two fuel oil-fired, simple cycle, combustion turbine having a nominal capacity of 1,115.2 MMBTU/hr (80 MW, nominal), controlled with a dry low NOx combustor; CT3 - Combustion Turbine No.3; *Modified | 2016-12-14 | PCT1(Other): Water Injection for NOx reduction during periods when distillate oil is used as fuel.; PCT2(Other): Water Injection for NOx reduction during periods when distillate oil is used as fuel; PCT3(Other): Water injection for NOx reduction during pe | Mostardi Platt | 80 MW, nominal | 269.0 lb/hr and 42 ppmvd @ 15% oxygen | 98 MWe | 200.3 lb/hr and 42 ppmvd @ 15% oxygen | 7E | Nitrogen Oxide | PP | Y | NA | This test was conducted to establish fuel-and-unit specific NOx emissions rates while burning No. 2 fuel oil in accordance with the low mass emissions unit provisions in 40 CFR 75.19. Emissions units P001, P002, P003, and P004 are identical units and qu | Yes
2016 | 327 | 0165000132 | AEP Generation Resources Inc., - Darby Plant | 12509 Adkins Road | Mt. Sterling | 43143 | 9061 | Pickaway | P004 | Natural Gas or number two fuel oil-fired, simple cycle, combustion turbine having a nominal capacity of 1,115.2 MMBTU/hr (80 MW, nominal), controlled with a dry low NOx combustor; CT4 - Combustion Turbine No.4; *Modified | 2016-12-14 | PCT1(Other): Water Injection for NOx reduction during periods when distillate oil is used as fuel.; PCT2(Other): Water Injection for NOx reduction during periods when distillate oil is used as fuel; PCT3(Other): Water injection for NOx reduction during pe | Mostardi Platt | 80 MW, nominal | 269.0 lb/hr and 42 ppmvd @ 15% oxygen | 93 MWe | 189.3 lb/hr and 41 ppmvd @ 15% oxygen | 7E | Nitrogen Oxide | PP | Y | NA | This test was conducted to establish fuel-and-unit specific NOx emissions rates while burning No. 2 fuel oil in accordance with the low mass emissions unit provisions in 40 CFR 75.19. Emissions units P001, P002, P003, and P004 are identical units and qu | Yes
2016 | 336 | 0165000132 | AEP Generation Resources Inc., - Darby Plant | 12509 Adkins Road | Mt. Sterling | 43143 | 9061 | Pickaway | P005 | Natural Gas or number two fuel oil-fired, simple cycle, combustion turbine having a nominal capacity of 1,115.2 MMBTU/hr (80 MW, nominal), controlled with a dry low NOx combustor; CT5 - Combustion Turbine No.5; *Modified | 2016-12-14 | PCT5(Other): Water injection for NOx reduction during periods when distillate oil is used as fuel.; PCT6(Other): Water injection for NOx reduction during periods when distillate oil is used for fuel. | Mostardi Platt | 80 MW, nominal | 269.0 lb/hr and 42 ppmvd @ 15% oxygen | 98 MWe | 169.7 lb/hr and 35.4 ppmvd @ 15% oxygen | 7E | Nitrogen Oxide | PP | Y | NA | This test was conducted to establish fuel-and-unit specific NOx emissions rates while burning No. 2 fuel oil in accordance with the low mass emissions unit provisions in 40 CFR 75.19. Emissions units P005 and P006 are identical units and qualify for sin | Yes
2016 | 337 | 0165000132 | AEP Generation Resources Inc., - Darby Plant | 12509 Adkins Road | Mt. Sterling | 43143 | 9061 | Pickaway | P006 | Natural Gas or number two fuel oil-fired, simple cycle, combustion turbine having a nominal capacity of 1,115.2 MMBTU/hr (80 MW, nominal), controlled with a dry low NOx combustor; CT6 - Combustion Turbine No.6; *Modified | 2016-12-14 | PCT5(Other): Water injection for NOx reduction during periods when distillate oil is used as fuel.; PCT6(Other): Water injection for NOx reduction during periods when distillate oil is used for fuel. | Mostardi Platt | 80 MW, nominal | 269.0 lb/hr and 42 ppmvd @ 15% oxygen | 98 MWe | 165.6 lb/hr and 36.5 ppmvd @ 15% oxygen | 7E | Nitrogen Oxide | PP | Y | NA | This test was conducted to establish fuel-and-unit specific NOx emissions rates while burning No. 2 fuel oil in accordance with the low mass emissions unit provisions in 40 CFR 75.19. Emissions units P005 and P006 are identical units and qualify for sin | Yes
2016 | 1927 | 0857043334 | AES Ohio Generation, LLC | 2101 Arbor Boulevard | Dayton | 45439 | 1511 | Montgomery | P003 | Natural gas and No. 2 fuel oil fired simple cycle stationary combustion turbine No. 6 - Tait CT6, with a nominal production rating of 80 MW and a nominal heat input of 1115.2 mmBtu/hour, with dry low NOx combustion and water injection controls | 2016-10-27 | Control is within the combustion zone as dry low NOx combustion | Mostardi Platt | 80 MW | 42ppmvd@15%O2; 269 lb/hr | 84 MW | 34.5pppmvd@15%; 134 lb/hr | 7E | Nitrogen Dioxide | PP | Y | NA | This test was designed to show compliance with permit allowables using #2 fuel oil. | Yes
2016 | 1931 | 0857043334 | AES Ohio Generation, LLC | 2101 Arbor Boulevard | Dayton | 45439 | 1511 | Montgomery | P003 | Natural gas and No. 2 fuel oil fired simple cycle stationary combustion turbine No. 6 - Tait CT6, with a nominal production rating of 80 MW and a nominal heat input of 1115.2 mmBtu/hour, with dry low NOx combustion and water injection controls | 2016-10-31 | Control is within the combustion zone as dry low NOx combustion | Mostardi Platt | 80 MW | 42ppmvd@15%O2; 269 lb/hr | 84 MW | 40 pppmvd@15%; 160 lb/hr | 7E | Nitrogen Dioxide | PP | Y | NA | This test was designed to show compliance with permit allowables using diesel fuel. This part of the water injection testing devised to determine water to fuel operating ratios. At 40 MW, 42 ppmvd@15%O2; 99 lb/hr NOX. At 60 MW, 40ppmvd@15%O2 and 120 lb | Yes
2016 | 1949 | 0857043334 | AES Ohio Generation, LLC | 2101 Arbor Boulevard | Dayton | 45439 | 1511 | Montgomery | P001 | Natural gas and No. 2 fuel oil fired simple cycle stationary combustion turbine No. 4 - Tait CT4, with a nominal production rating of 80 MW and a nominal heat input of 1115.2 mmBtu/hour, with dry low NOx combustion and water injection controls | 2016-11-22 | Control is within the combustion zone as dry low NOx combustion | Mostardi Platt | 80 MW | 42ppmvd@15%O2; 269 lb/hr | 76 MW | 36 ppmvd@15%O2;125 lb/hr | 7E | Nitrogen Dioxide | PP | Y | NA | This test was designed to show compliance with permit allowables using #2 fuel oil at base load. | Yes
2016 | 1950 | 0857043334 | AES Ohio Generation, LLC | 2101 Arbor Boulevard | Dayton | 45439 | 1511 | Montgomery | P002 | Natural gas and No. 2 fuel oil fired simple cycle stationary combustion turbine No. 5 - Tait CT5, with a nominal production rating of 80 MW and a nominal heat input of 1115.2 mmBtu/hour, with dry low NOx combustion and water injection controls | 2016-11-22 | Control is within the combustion zone as dry low NOx combustion | Mostardi Platt | 80 MW | 42ppmvd@15%O2; 269 lb/hr | 80 MW | 34 ppmvd@15%O2; 122 lb/hr | 7E | Nitrogen Dioxide | PP | Y | NA | This test was designed to show compliance with permit allowables using #2 fuel oil at base load. | Yes
2016 | 1951 | 0857043334 | AES Ohio Generation, LLC | 2101 Arbor Boulevard | Dayton | 45439 | 1511 | Montgomery | P004 | Natural gas and No. 2 fuel oil fired simple cycle stationary combustion turbine No. 7 - Tait CT7, with a nominal production rating of 80 MW and a nominal heat input of 1115.2 mmBtu/hour, with dry low NOx combustion and water injection controls | 2016-11-22 | Control is within the combustion zone as dry low NOx combustion | Mostardi Platt | 80 MW | 42ppmvd@15%O2; 269 lb/hr | 90 MW | 33 ppmvd@15%O2; 122 lb/hr | 7E | Nitrogen Dioxide | PP | Y | NA | This test was designed to show compliance with permit allowables using #2 fuel oil at base load. | Yes
2016 | 1953 | 0857043334 | AES Ohio Generation, LLC | 2101 Arbor Boulevard | Dayton | 45439 | 1511 | Montgomery | P002 | Natural gas and No. 2 fuel oil fired simple cycle stationary combustion turbine No. 5 - Tait CT5, with a nominal production rating of 80 MW and a nominal heat input of 1115.2 mmBtu/hour, with dry low NOx combustion and water injection controls | 2016-11-03 | Control is within the combustion zone as dry low NOx combustion | Mostardi Platt | 80 MW | 42ppmvd@15%O2; 269 lb/hr | 79 MW | 40ppmvd@15%O2; 143 lb/hr | 7E | Nitrogen Dioxide | PP | Y | NA | This test was designed to show compliance with permit allowables using diesel fuel. This part of the WATER INJECTION testing devised to determine water to fuel operating ratios at different operating loads. At 40 MW, 42 ppm; 95 lb/hr. At 60 MW, 40 ppm@ | Yes
2016 | 1954 | 0857043334 | AES Ohio Generation, LLC | 2101 Arbor Boulevard | Dayton | 45439 | 1511 | Montgomery | P001 | Natural gas and No. 2 fuel oil fired simple cycle stationary combustion turbine No. 4 - Tait CT4, with a nominal production rating of 80 MW and a nominal heat input of 1115.2 mmBtu/hour, with dry low NOx combustion and water injection controls | 2016-11-02 | Control is within the combustion zone as dry low NOx combustion | Mostardi Platt | 80 MW | 42ppmvd@15%O2; 269 lb/hr | 76 MW | 40ppmvd@15%O2; 139 lb/hr | 7E | Nitrogen Dioxide | PP | Y | NA | This test was designed to show compliance with permit allowables using diesel fuel. This part of the WATER INJECTION testing devised to determine water to fuel operating ratios at different operating loads. At 40 MW, 41 ppm; 93 lb/hr. At 60 MW, 41 ppm@ | Yes
2016 | 1957 | 0857043334 | AES Ohio Generation, LLC | 2101 Arbor Boulevard | Dayton | 45439 | 1511 | Montgomery | P004 | Natural gas and No. 2 fuel oil fired simple cycle stationary combustion turbine No. 7 - Tait CT7, with a nominal production rating of 80 MW and a nominal heat input of 1115.2 mmBtu/hour, with dry low NOx combustion and water injection controls | 2016-11-05 | Control is within the combustion zone as dry low NOx combustion | Mostardi Platt | 80 MW | 42ppmvd@15%O2; 269 lb/hr | 83 MW | 40ppmvd@15%O2;150 lb/hr | 7E | Nitrogen Dioxide | PP | Y | NA | This test was designed to show compliance with permit allowables using diesel fuel. This part of the WATER INJECTION testing devised to determine water to fuel operating ratios at different operating loads. At 40 MW, 41 ppm; 96 lb/hr. At 60 MW, 40 ppm@ | Yes
2005 | 578 | 0387000377 | Troy Energy, LLC | 22379 Pemberville Road | Luckey | 43443 |  | Wood | P004 | 1,570 mmBTU/hr combustion turbine | 2005-07-22 | none | TRC ENVIRONMENTAL CORPORATION | 1988.7 mmbtu/hr | 351.0 lbs/hr; 0.1765 lbs/mmbtu | 1790.1 mmbtu/hr | 282.3 lbs/hr; 0.158 lbs/mmbtu | 7 | Nitrogen Dioxide | PASS | NA | Y | Generator fuel was fuel oil.Also tested for NOx ppm:actual: 35.8 ppmvd at 15% oxygenallowable: 42 ppmvd at 15% oxygen
2004 | 1155 | 1431070849 | University of Cincinnati | Clifton Campus | Cincinnati | 45221 |  | Hamilton | P003 | 13.5 MW Natural Gas/ No. 2 Fuel Oil-fired Turbines with 98.5 mmBtu/hr duct burner | 2004-05-28 | control equipment? | RMC | 14.5mw/hr | 25ppm nox and 14.7 lb/hr | 12 mw/hr | 14.4 ppm and 8.35 lb/hr | 7 | Nitrogen Dioxide | PASS | Y | Y |  | Yes
2004 | 1161 | 1431070849 | University of Cincinnati | Clifton Campus | Cincinnati | 45221 |  | Hamilton | P004 | 13.5 MW Natural Gas/ No. 2 Fuel Oil-fired Turbines with 98.5 mmBtu/hr duct burner | 2004-05-28 | cat | RMC | 14.5mw/hr | 25ppm nox and 14.7 lb/hr | 12 mw/hr | 16.9 ppm and 9.2 lb/hr | 7 | Nitrogen Dioxide | PASS | Y | Y |  | Yes
2004 | 1163 | 1431070849 | University of Cincinnati | Clifton Campus | Cincinnati | 45221 |  | Hamilton | P003 | 13.5 MW Natural Gas/ No. 2 Fuel Oil-fired Turbines with 98.5 mmBtu/hr duct burner | 2004-09-08 | control equipment? | RMC | 14.5mw/hr | 96ppm nox and 54.9 lb/hr | 12 mw/hr | 63 ppm and 34lb/hr | 7 | Nitrogen Dioxide | PASS | Y | Y |  | Yes
2004 | 1165 | 1431070849 | University of Cincinnati | Clifton Campus | Cincinnati | 45221 |  | Hamilton | P004 | 13.5 MW Natural Gas/ No. 2 Fuel Oil-fired Turbines with 98.5 mmBtu/hr duct burner | 2004-09-08 | cat | RMC | 14.5mw/hr | 25ppm nox and 14.7 lb/hr | 12 mw/hr | 14.4 ppm and 8 lb/hr | 7 | Nitrogen Dioxide | PASS | Y | Y |  | Yes
2005 | 1203 | 1431070849 | University of Cincinnati | Clifton Campus | Cincinnati | 45221 |  | Hamilton | P003 | 13.5 MW Natural Gas/ No. 2 Fuel Oil-fired Turbines with 98.5 mmBtu/hr duct burner | 2005-05-18 | control equipment? | RMC | 14.5mw/hr | 20%ra | 12.7 mw/hr | 8%ra | 7 | Nitrogen Dioxide | PASS | Y | Y |  | Yes
2005 | 1205 | 1431070849 | University of Cincinnati | Clifton Campus | Cincinnati | 45221 |  | Hamilton | P004 | 13.5 MW Natural Gas/ No. 2 Fuel Oil-fired Turbines with 98.5 mmBtu/hr duct burner | 2005-05-18 | control equipment? | RMC |  |  |  |  | 7 | Nitrogen Dioxide | PASS | Y | Y |  | Yes
2005 | 1208 | 1431070849 | University of Cincinnati | Clifton Campus | Cincinnati | 45221 |  | Hamilton | P003 | 13.5 MW Natural Gas/ No. 2 Fuel Oil-fired Turbines with 98.5 mmBtu/hr duct burner | 2005-11-30 | HRSG & DUCT BURNERS | RMC | 12 MW | <20% RA LB/MMBTU,LB/HR,PPM@15%O2 | 11 MW | 10.3%, 10.2%, 12.0% RA | 7 | Nitrogen Dioxide | PASS | NA | Y |  | Yes
2005 | 1210 | 1431070849 | University of Cincinnati | Clifton Campus | Cincinnati | 45221 |  | Hamilton | P004 | 13.5 MW Natural Gas/ No. 2 Fuel Oil-fired Turbines with 98.5 mmBtu/hr duct burner | 2005-11-30 | HRSG & DUCT BURNERS | RMC | 12 MW | <20% RA LB/MMBTU,LB/HR,PPM@15%O2 | 12 MW | 5.5%, 5.7%, 6.1% RA | 7 | Nitrogen Dioxide | PASS | NA | Y |  | Yes
2006 | 1410 | 1431070849 | University of Cincinnati | Clifton Campus | Cincinnati | 45221 |  | Hamilton | P003 | 13.5 MW Natural Gas/ No. 2 Fuel Oil-fired Turbines with 98.5 mmBtu/hr duct burner | 2006-11-15 | HRSG & DUCT BURNERS | RMC | 12 MW | <20% RA LB/MMBTU,LB/HR,PPM@15%O2 | 12 MW | 4.20%, 5.10%, 4.21% RA | 7 | Nitrogen Dioxide | PASS | NA | Y |  | Yes
2006 | 1412 | 1431070849 | University of Cincinnati | Clifton Campus | Cincinnati | 45221 |  | Hamilton | P004 | 13.5 MW Natural Gas/ No. 2 Fuel Oil-fired Turbines with 98.5 mmBtu/hr duct burner | 2006-11-15 | HRSG & DUCT BURNERS | RMC | 12 MW | <20% RA LB/MMBTU,LB/HR,PPM@15%O2 | 12 MW | 12.15%, 12.90%, 12.30% RA | 7 | Nitrogen Dioxide | PASS | NA | Y |  | Yes
2003 | 11 | 0320010006 | Richland Substation Peaker Facility | Carpenter Rd. S/U.S. 24 | Defiance | 43512 |  | Defiance | P003 | 1673 mmBtu/hr natural gas-fired simple cycle turbine generator, with distillate oil backup, controlled with a water-injection NOx reduction system | 2003-07-30 | control equipment? | FIRST ENERGY CORP | 1431 mmbtu/hr | 25 ppmvd at 15% o2 | 1555.4 mmbtu/hr | 21.4 ppmvd at 15% o2 | 7 | Nitrogen Dioxide | PASS | NA | Y | Test performed as part of RATA testing.
2005 | 477 | 0320010006 | Richland Substation Peaker Facility | Carpenter Rd. S/U.S. 24 | Defiance | 43512 |  | Defiance | P001 | 1673 mmBtu/hr natural gas-fired simple cycle turbine generator, with distillate oil backup, controlled with water injection NOx reduction system | 2005-08-09 | none | GRACE CONSULTING, INC. |  |  |  |  | 7 | Nitrogen Dioxide | PASS | NA | Y
2005 | 478 | 0320010006 | Richland Substation Peaker Facility | Carpenter Rd. S/U.S. 24 | Defiance | 43512 |  | Defiance | P001 | 1673 mmBtu/hr natural gas-fired simple cycle turbine generator, with distillate oil backup, controlled with water injection NOx reduction system | 2005-08-09 | none | GRACE CONSULTING, INC. |  |  |  |  | 7 | Nitrogen Oxide | PASS | NA | Y
2009 | 33 | 0320010006 | Richland Substation Peaker Facility | Carpenter Rd. S/U.S. 24 | Defiance | 43512 |  | Defiance | P001 | 1673 mmBtu/hr natural gas-fired simple cycle turbine generator, with distillate oil backup, controlled with water injection NOx reduction system | 2009-08-11 | Water injection, NOx reduction system | Grace Consulting, Inc. |  |  |  |  | 7E | Nitrogen Dioxide | PASS | NA | Y
2009 | 34 | 0320010006 | Richland Substation Peaker Facility | Carpenter Rd. S/U.S. 24 | Defiance | 43512 |  | Defiance | P001 | 1673 mmBtu/hr natural gas-fired simple cycle turbine generator, with distillate oil backup, controlled with water injection NOx reduction system | 2009-08-11 | Water injection, NOx reduction system | Grace Consulting, Inc. |  |  |  |  | 7E | Nitrogen Oxide | PASS | NA | Y
2013 | 758 | 0320010006 | Richland Substation Peaker Facility | Carpenter Rd. S/U.S. 24 | Defiance | 43512 |  | Defiance | P003 | 1673 mmBtu/hr natural gas-fired simple cycle turbine generator, with distillate oil backup, controlled with a water-injection NOx reduction system | 2013-10-29 | NOx Controls(Other): NOx Reduction System; watr inject3(Other): water injection NOx reduction system | Grace Consulting, Inc. | 1673 MMBtu/hr | 251.4 lbs/hr, 25 ppmvd at 15% O2 as 4 hr avg | 1603.2 MMBtu/hr | 129.0 lbs/hr, 24 ppmvd at 15% O2 as 4 hr avg | 7E | Nitrogen Dioxide | PASS | NA | Y | Natural gas was used as the fuel for this test.
2014 | 1203 | 0320010006 | Richland Substation Peaker Facility | Carpenter Rd. S/U.S. 24 | Defiance | 43512 |  | Defiance | P001 | 1673 mmBtu/hr natural gas-fired simple cycle turbine generator, with distillate oil backup, controlled with water injection NOx reduction system | 2014-08-13 | NOx Controls(Other): NOx Reduction System; watr inject1(Other): water injection NOx reduction system | Grace Consulting, Inc. | 1673 MMBtu/hr | 251.4 lbs/hr 25 ppmvd at 15% O2 (4 hr avg) | 1458 MMBtu/hr | 109.61 lbs/hr 22.7 pppmvd at 15% O2 (4 hr avg) | 7E | Nitrogen Dioxide | PASS | NA | Y | The natural gas fuel was sampled and analyzed subsequent to the test and was found to have a sulfur content of 1.171 ppmv.
2011 | 1204 | 1667040085 | Kent State University Heating Plant | P.O. Box 5190 | Kent | 44242 | 0001 | Portage | B010 | Combustion Turbine CT 2 | 2011-12-01 | None | Air Compliance Testing Inc | 76 MMBtu/hr | 0.10 lb/MMBtu 33.3 TPY | 76 MMBtu/hr | 0.037 lb/MMBtu 12.48 TPY | 7E | Nitrogen Oxide | PASS | NA | Y | Method 7E Passed
2015 | 1391 | 1667040085 | Kent State University Heating Plant | P.O. Box 5190 | Kent | 44242 | 0001 | Portage | B010 | Combustion Turbine CT 2 | 2015-01-15 | none | Air Compliance Testing, Inc. | 7 MW | 0.10 lb/mmBtu | 7 MW | 0.048 lb/mmBtu | 7E | Nitrogen Oxide | PP | NA | Y |  | Yes
2007 | 1513 | 1409000353 | MillerCoors LLC | 2525 WAYNE MADISON ROAD | Trenton | 45067 | 9760 | Butler | B001 | 238 MMBtu/hr pulverized coal/fuel oil-fired boiler (including 20 MMBtu natural gas burners for startup and supplemental fuel), equipped with baghouse and steam turbine | 2007-03-13 | baghouse | FBT TESTING & ENVIRONMENTAL |  |  |  |  | 7 | Nitrogen Oxide | PASS | NA | Y
2007 | 1516 | 1409000353 | MillerCoors LLC | 2525 WAYNE MADISON ROAD | Trenton | 45067 | 9760 | Butler | B001 | 238 MMBtu/hr pulverized coal/fuel oil-fired boiler (including 20 MMBtu natural gas burners for startup and supplemental fuel), equipped with baghouse and steam turbine | 2007-03-13 | baghouse | FBT TESTING & ENVIRONMENTAL |  |  |  |  | 7 | Nitrogen Dioxide | PASS | NA | Y
2007 | 1521 | 1409000353 | MillerCoors LLC | 2525 WAYNE MADISON ROAD | Trenton | 45067 | 9760 | Butler | B002 | 238 MMBtu/hr pulverized coal/fuel oil-fired boiler (including 20 MMBtu natural gas burners for startup and supplemental fuel), equipped with baghouse and steam turbine | 2007-05-30 | baghouse | FBT TESTING & ENVIRONMENTAL |  |  |  |  | 7 | Nitrogen Dioxide | PASS | NA | Y
2007 | 1522 | 1409000353 | MillerCoors LLC | 2525 WAYNE MADISON ROAD | Trenton | 45067 | 9760 | Butler | B002 | 238 MMBtu/hr pulverized coal/fuel oil-fired boiler (including 20 MMBtu natural gas burners for startup and supplemental fuel), equipped with baghouse and steam turbine | 2007-05-30 | baghouse | FBT TESTING & ENVIRONMENTAL |  |  |  |  | 7 | Nitrogen Oxide | PASS | NA | Y
2007 | 1524 | 1409000353 | MillerCoors LLC | 2525 WAYNE MADISON ROAD | Trenton | 45067 | 9760 | Butler | B002 | 238 MMBtu/hr pulverized coal/fuel oil-fired boiler (including 20 MMBtu natural gas burners for startup and supplemental fuel), equipped with baghouse and steam turbine | 2007-10-10 | BAGHOUSE | FBT TESTING & ENVIRONMENTAL SERVICES |  |  |  |  | 7E | Nitrogen Oxide | PASS | NA | N
2007 | 1525 | 1409000353 | MillerCoors LLC | 2525 WAYNE MADISON ROAD | Trenton | 45067 | 9760 | Butler | B002 | 238 MMBtu/hr pulverized coal/fuel oil-fired boiler (including 20 MMBtu natural gas burners for startup and supplemental fuel), equipped with baghouse and steam turbine | 2007-10-10 | BAGHOUSE | FBT TESTING & ENVIRONMENTAL SERVICES |  |  |  |  | 7E | Nitrogen Dioxide | PASS | NA | N
2014 | 2513 | 1409000353 | MillerCoors LLC | 2525 WAYNE MADISON ROAD | Trenton | 45067 | 9760 | Butler | B001 | 238 MMBtu/hr pulverized coal/fuel oil-fired boiler (including 20 MMBtu natural gas burners for startup and supplemental fuel), equipped with baghouse and steam turbine | 2014-02-25 | baghouse | KBD Technic | 180 KPPH steam | 0.7 lbs/MMBtu | 83-114 KPPH steam | 0.4 lbs/MMBtu | 7E | Nitrogen Oxide | PASS | NA | Y | Source is right at the limit for particulate emissions. Discussion with permitting folks and information from the facility led to the decision to not request a retest. Test Report - Report ID# 79618 ITT - Report ID# 77506
2014 | 2514 | 1409000353 | MillerCoors LLC | 2525 WAYNE MADISON ROAD | Trenton | 45067 | 9760 | Butler | B001 | 238 MMBtu/hr pulverized coal/fuel oil-fired boiler (including 20 MMBtu natural gas burners for startup and supplemental fuel), equipped with baghouse and steam turbine | 2014-02-25 | baghouse | KBD Technic | 180 KPPH steam | 0.7 lbs/MMBtu | 83-114 KPPH steam | 0.4 lbs/MMBtu | 7E | Nitrogen Dioxide | PASS | NA | Y | Source is right at the limit for particulate emissions. Discussion with permitting folks and information from the facility led to the decision to not request a retest. Test Report - Report ID# 79618 ITT - Report ID# 77506
2014 | 2516 | 1409000353 | MillerCoors LLC | 2525 WAYNE MADISON ROAD | Trenton | 45067 | 9760 | Butler | B002 | 238 MMBtu/hr pulverized coal/fuel oil-fired boiler (including 20 MMBtu natural gas burners for startup and supplemental fuel), equipped with baghouse and steam turbine | 2014-05-29 | baghouse | EQM | 238 MMBtu/hr | 0.7 lb/MMBtu | 124 MMBtu/hr 107 KPPH Steam | 0.7 lb/MMBtu | 7E | Nitrogen Oxide | PASS | NA | Y | Source is right at the limit for NOx emissions. Information pertaining to the tested operating rate of B002 can be found in the observer's report or the communications attachments below. Test Report - Report ID# 83637 ITT - Report ID# 77506
2014 | 2517 | 1409000353 | MillerCoors LLC | 2525 WAYNE MADISON ROAD | Trenton | 45067 | 9760 | Butler | B002 | 238 MMBtu/hr pulverized coal/fuel oil-fired boiler (including 20 MMBtu natural gas burners for startup and supplemental fuel), equipped with baghouse and steam turbine | 2014-05-29 | baghouse | EQM | 238 MMBtu/hr | 0.7 lb/MMBtu | 124 MMBtu/hr 107 KPPH Steam | 0.7 lb/MMBtu | 7E | Nitrogen Dioxide | PASS | NA | Y | Source is right at the limit for NOx emissions. Information pertaining to the tested operating rate of B002 can be found in the observer's report or the communications attachments below. Test Report - Report ID# 83637 ITT - Report ID# 77506
2011 | 316 | 0247100408 | OBERLIN COLLEGE | 173 W. Lorain St. | Oberlin | 44074 | 1092 | Lorain | B003 | 63 mmBtu/hr natural gas fired boiler no. 3 with a low NOx burner for campus steam production. Or steam generated by the boiler can be diverted to a turbine generator to generate electric power for distribution to a general electric grid. | 2011-02-03 | none | Grace Consulting, Inc. |  |  |  |  | 7E | Nitrogen Dioxide | FAIL | NA | Y | Tested pollutants: NO2, NO; Permitted Allowable Emission Rate = 0.10 lb NOx/mmBtu; Permitted Maximum Operating Rate = 50,000 lbs steam/hr; Average Tested Emission Rate = 0.424 lb NOx/mmBtu; Average Tested Operating Rate = 45,500 lbs steam/hr; Results = Failed; AFS Date = 2011-04-20 00:00:00.0; AFS ID = legacy) Average of 16.7 mcf/hr of natural gas combusted.
2011 | 317 | 0247100408 | OBERLIN COLLEGE | 173 W. Lorain St. | Oberlin | 44074 | 1092 | Lorain | B003 | 63 mmBtu/hr natural gas fired boiler no. 3 with a low NOx burner for campus steam production. Or steam generated by the boiler can be diverted to a turbine generator to generate electric power for distribution to a general electric grid. | 2011-02-03 | none | Grace Consulting, Inc. |  |  |  |  | 7E | Nitrogen Oxide | FAIL | NA | Y | Tested pollutants: NO2, NO; Permitted Allowable Emission Rate = 0.10 lb NOx/mmBtu; Permitted Maximum Operating Rate = 50,000 lbs steam/hr; Average Tested Emission Rate = 0.424 lb NOx/mmBtu; Average Tested Operating Rate = 45,500 lbs steam/hr; Results = Failed; AFS Date = 2011-04-20 00:00:00.0; AFS ID = legacy) Average of 16.7 mcf/hr of natural gas combusted.
2016 | 578 | 0247100408 | OBERLIN COLLEGE | 173 W. Lorain St. | Oberlin | 44074 | 1092 | Lorain | B003 | 63 mmBtu/hr natural gas fired boiler equipped with a low NOx burner. Steam is used for heating campus buildings or to power a turbine to generate electric power. | 2016-02-11 | Low Nox Burner | Grace Consulting, Inc. | 50 KPPH | 0.10 lb/mmbtu | 45 KPPH | .044 lb/mmbtu | 7E | Nitrogen Dioxide | PP | Y | NA | An average of 540,030 scfh of gas was used, per run, during the three run test event.
2003 | 59 | 1413100008 | Duke Energy Ohio, W.C. Beckjord Station | 757 US Route 52 | New Richmond | 45157 | 9709 | Clermont | B007 | No. 2 fuel oil-fired combustion turbine #1, having a nominal capacity of 766 MMBtu/hr (53 MW) | 2003-04-08 | None | GRACE CONSULTING, INC. | 53 MW | None | Max 74 MW | 0.593 lb/mmbtu | other | Nitrogen Dioxide | PASS | NA | Y |  | Yes
2003 | 60 | 1413100008 | Duke Energy Ohio, W.C. Beckjord Station | 757 US Route 52 | New Richmond | 45157 | 9709 | Clermont | B008 | No. 2 fuel oil-fired combustion turbine #2, having a nominal capacity of 766 MMBtu/hr (53 MW) | 2003-04-08 | None | GRACE CONSULTING, INC. | 53 MW | None | Max 74 MW | 0.543 lb/mmbtu | other | Nitrogen Dioxide | PASS | NA | Y |  | Yes
2003 | 61 | 1413100008 | Duke Energy Ohio, W.C. Beckjord Station | 757 US Route 52 | New Richmond | 45157 | 9709 | Clermont | B009 | No. 2 fuel oil-fired combustion turbine #3, having a nominal capacity of 766 MMBtu/hr (53 MW) | 2003-04-09 | None | GRACE CONSULTING, INC. | 53 MW | None | Max 74 MW | 0.603 lb/mmbtu | other | Nitrogen Dioxide | PASS | NA | Y |  | Yes
2003 | 62 | 1413100008 | Duke Energy Ohio, W.C. Beckjord Station | 757 US Route 52 | New Richmond | 45157 | 9709 | Clermont | B010 | No. 2 fuel oil-fired combustion turbine #4, having a nominal capacity of 766 MMBtu/hr (53 MW) | 2003-04-09 | None | GRACE CONSULTING, INC. | 53 MW | None | Max 74 MW | 0.556 lb/mmbtu | other | Nitrogen Dioxide | PASS | NA | Y |  | Yes
2008 | 1735 | 1413100008 | Duke Energy Ohio, W.C. Beckjord Station | 757 US Route 52 | New Richmond | 45157 | 9709 | Clermont | B007 | No. 2 fuel oil-fired combustion turbine #1, having a nominal capacity of 766 MMBtu/hr (53 MW) | 2008-03-11 | NA | GRACE CONSULTING, INC. |  |  |  |  | 7E | Nitrogen Dioxide | PASS | NA | Y |  | Yes
2008 | 1736 | 1413100008 | Duke Energy Ohio, W.C. Beckjord Station | 757 US Route 52 | New Richmond | 45157 | 9709 | Clermont | B007 | No. 2 fuel oil-fired combustion turbine #1, having a nominal capacity of 766 MMBtu/hr (53 MW) | 2008-03-11 | NA | GRACE CONSULTING, INC. |  |  |  |  | 7E | Nitrogen Oxide | PASS | NA | Y |  | Yes
2008 | 1737 | 1413100008 | Duke Energy Ohio, W.C. Beckjord Station | 757 US Route 52 | New Richmond | 45157 | 9709 | Clermont | B008 | No. 2 fuel oil-fired combustion turbine #2, having a nominal capacity of 766 MMBtu/hr (53 MW) | 2008-03-11 | NA | GRACE CONSULTING, INC. |  |  |  |  | 7E | Nitrogen Dioxide | PASS | NA | Y |  | Yes
2008 | 1738 | 1413100008 | Duke Energy Ohio, W.C. Beckjord Station | 757 US Route 52 | New Richmond | 45157 | 9709 | Clermont | B008 | No. 2 fuel oil-fired combustion turbine #2, having a nominal capacity of 766 MMBtu/hr (53 MW) | 2008-03-11 | NA | GRACE CONSULTING, INC. |  |  |  |  | 7E | Nitrogen Oxide | PASS | NA | Y |  | Yes
2008 | 1739 | 1413100008 | Duke Energy Ohio, W.C. Beckjord Station | 757 US Route 52 | New Richmond | 45157 | 9709 | Clermont | B009 | No. 2 fuel oil-fired combustion turbine #3, having a nominal capacity of 766 MMBtu/hr (53 MW) | 2008-03-12 | NA | GRACE CONSULTING, INC. |  |  |  |  | 7E | Nitrogen Oxide | PASS | NA | Y |  | Yes
2008 | 1740 | 1413100008 | Duke Energy Ohio, W.C. Beckjord Station | 757 US Route 52 | New Richmond | 45157 | 9709 | Clermont | B009 | No. 2 fuel oil-fired combustion turbine #3, having a nominal capacity of 766 MMBtu/hr (53 MW) | 2008-03-12 | NA | GRACE CONSULTING, INC. |  |  |  |  | 7E | Nitrogen Dioxide | PASS | NA | Y |  | Yes
2008 | 1741 | 1413100008 | Duke Energy Ohio, W.C. Beckjord Station | 757 US Route 52 | New Richmond | 45157 | 9709 | Clermont | B010 | No. 2 fuel oil-fired combustion turbine #4, having a nominal capacity of 766 MMBtu/hr (53 MW) | 2008-03-12 | NA | GRACE CONSULTING, INC. |  |  |  |  | 7E | Nitrogen Oxide | PASS | NA | Y |  | Yes
2008 | 1742 | 1413100008 | Duke Energy Ohio, W.C. Beckjord Station | 757 US Route 52 | New Richmond | 45157 | 9709 | Clermont | B010 | No. 2 fuel oil-fired combustion turbine #4, having a nominal capacity of 766 MMBtu/hr (53 MW) | 2008-03-12 | NA | GRACE CONSULTING, INC. |  |  |  |  | 7E | Nitrogen Dioxide | PASS | NA | Y |  | Yes
2013 | 1541 | 1413100008 | Duke Energy Ohio, W.C. Beckjord Station | 757 US Route 52 | New Richmond | 45157 | 9709 | Clermont | B007 | No. 2 fuel oil-fired combustion turbine #1, having a nominal capacity of 766 MMBtu/hr (53 MW) | 2013-03-19 | NA | GRACE CONSULTING, INC. | 53 MW | NA | NA | NA | 7E | Nitrogen Oxide | PASS | NA | Y | THIS TESTING WAS CONDUCTED IN ACCORDANCE WITH 40 CFR PART 75 APPENDIX E REQUIREMENTS. THREE RUNS WERE PERFORMED AT FOUR LOADS. TEST RESULTS FROM EACH LOAD ARE SHOWN BELOW. Report ID: 65450 LOAD MW NOX LB/MMBTU O2% LOW 5 0.121 17.03 MID-LOW 23 0.251 17.00 MID-HIGH 41 0.447 16.67 HIGH 53 0.547 15.80 | Yes
2013 | 1542 | 1413100008 | Duke Energy Ohio, W.C. Beckjord Station | 757 US Route 52 | New Richmond | 45157 | 9709 | Clermont | B007 | No. 2 fuel oil-fired combustion turbine #1, having a nominal capacity of 766 MMBtu/hr (53 MW) | 2013-03-19 | NA | GRACE CONSULTING, INC. | 53 MW | NA | 53 MW | 0.547 lb/mmBtu | 7E | Nitrogen Dioxide | PASS | NA | Y | THIS TESTING WAS CONDUCTED IN ACCORDANCE WITH 40 CFR PART 75 APPENDIX E REQUIREMENTS. THREE RUNS WERE PERFORMED AT FOUR LOADS. TEST RESULTS FROM EACH LOAD ARE SHOWN BELOW. Report ID: 65450 LOAD MW NOX LB/MMBTU O2% LOW 5 0.121 17.03 MID-LOW 23 0.251 17.00 MID-HIGH 41 0.447 16.67 HIGH 53 0.547 15.80 | Yes
2013 | 1543 | 1413100008 | Duke Energy Ohio, W.C. Beckjord Station | 757 US Route 52 | New Richmond | 45157 | 9709 | Clermont | B008 | No. 2 fuel oil-fired combustion turbine #2, having a nominal capacity of 766 MMBtu/hr (53 MW) | 2013-03-19 | NA | GRACE CONSULTING, INC. | 53 MW | NA | 56 MW | NA | 7E | Nitrogen Oxide | PASS | NA | Y | THIS TESTING WAS CONDUCTED IN ACCORDANCE WITH 40 CFR PART 75 APPENDIX E REQUIREMENTS. THREE RUNS WERE PERFORMED AT FOUR LOADS. TEST RESULTS FROM EACH LOAD ARE SHOWN BELOW. Report ID: 65450 LOAD MW NOX LB/MMBTU O2% LOW 5 0.203 18.27 MID-LOW 23 0.306 17.37 MID-HIGH 41 0.474 17.00 HIGH 56 0.591 15.97 | Yes
2013 | 1544 | 1413100008 | Duke Energy Ohio, W.C. Beckjord Station | 757 US Route 52 | New Richmond | 45157 | 9709 | Clermont | B008 | No. 2 fuel oil-fired combustion turbine #2, having a nominal capacity of 766 MMBtu/hr (53 MW) | 2013-03-19 | NA | GRACE CONSULTING, INC. | 53 MW | NA | 56 MW | 0.591 lb/mmBtu | 7E | Nitrogen Dioxide | PASS | NA | Y | THIS TESTING WAS CONDUCTED IN ACCORDANCE WITH 40 CFR PART 75 APPENDIX E REQUIREMENTS. THREE RUNS WERE PERFORMED AT FOUR LOADS. TEST RESULTS FROM EACH LOAD ARE SHOWN BELOW. Report ID: 65450 LOAD MW NOX LB/MMBTU O2% LOW 5 0.203 18.27 MID-LOW 23 0.306 17.37 MID-HIGH 41 0.474 17.00 HIGH 56 0.591 15.97 | Yes
2013 | 1545 | 1413100008 | Duke Energy Ohio, W.C. Beckjord Station | 757 US Route 52 | New Richmond | 45157 | 9709 | Clermont | B009 | No. 2 fuel oil-fired combustion turbine #3, having a nominal capacity of 766 MMBtu/hr (53 MW) | 2013-03-20 | NA | GRACE CONSULTING, INC. | 53 MW | See memo | 57 MW | 0.520 lb/mmbtu | 7E | Nitrogen Oxide | PASS | NA | Y | This testing was conducted in accordance with 40 CFR Part 45 Appendix E requirements. Three runs were performed at four load leves. Testing results from each load are shown below. MW NOX LB/MMBTU O2% LOW 5 0.244 15.70 MID-LOW 23 0.375 16.97 MID-HIGH 41 0.441 18.20 HIGH 57 0.520 18.73 Test report from the facility is located in STARS2 under report ID 65450 | Yes
2013 | 1546 | 1413100008 | Duke Energy Ohio, W.C. Beckjord Station | 757 US Route 52 | New Richmond | 45157 | 9709 | Clermont | B009 | No. 2 fuel oil-fired combustion turbine #3, having a nominal capacity of 766 MMBtu/hr (53 MW) | 2013-03-20 | NA | GRACE CONSULTING, INC. | 53 MW | See memo | 57 MW | 0.520 lb/mmbtu | 7E | Nitrogen Dioxide | PASS | NA | Y | This testing was conducted in accordance with 40 CFR Part 45 Appendix E requirements. Three runs were performed at four load leves. Testing results from each load are shown below. MW NOX LB/MMBTU O2% LOW 5 0.244 15.70 MID-LOW 23 0.375 16.97 MID-HIGH 41 0.441 18.20 HIGH 57 0.520 18.73 Test report from the facility is located in STARS2 under report ID 65450 | Yes
2013 | 1547 | 1413100008 | Duke Energy Ohio, W.C. Beckjord Station | 757 US Route 52 | New Richmond | 45157 | 9709 | Clermont | B010 | No. 2 fuel oil-fired combustion turbine #4, having a nominal capacity of 766 MMBtu/hr (53 MW) | 2013-03-20 | NA | GRACE CONSULTING, INC. | 53 MW | See memo | 55 MW | 0.533 lb/mmbtu | 7E | Nitrogen Oxide | PASS | NA | Y | This testing was conducted in accordance with 40 CFR Part 45 Appendix E requirements. Three runs were performed at four load leves. Testing results from each load are shown below. MW NOX LB/MMBTU O2% LOW 5 0.257 15.80 MID-LOW 23 0.413 17.00 MID-HIGH 41 0.455 18.17 HIGH 55 0.533 18.87 Test report from the facility is located in STARS2 under report ID 65450 | Yes
2013 | 1548 | 1413100008 | Duke Energy Ohio, W.C. Beckjord Station | 757 US Route 52 | New Richmond | 45157 | 9709 | Clermont | B010 | No. 2 fuel oil-fired combustion turbine #4, having a nominal capacity of 766 MMBtu/hr (53 MW) | 2013-03-20 | NA | GRACE CONSULTING, INC. | 53 MW | See memo | 55 MW | 0.533 lb/mmbtu | 7E | Nitrogen Dioxide | PASS | NA | Y | This testing was conducted in accordance with 40 CFR Part 45 Appendix E requirements. Three runs were performed at four load leves. Testing results from each load are shown below. MW NOX LB/MMBTU O2% LOW 5 0.257 15.80 MID-LOW 23 0.413 17.00 MID-HIGH 41 0.455 18.17 HIGH 55 0.533 18.87 Test report from the facility is located in STARS2 under report ID 65450 | Yes
2011 | 672 | 0448010737 | City of Toledo, Division of Water Reclamation | 3900 North Summit St. | Toledo | 43611 |  | Lucas | P109 | Natural Gas/Digester Gas/Landfill Gas powered combustion turbine for combined cycle cogeneration system | 2011-07-06 | none | Bureau Veritas Co |  |  |  |  | 7E | Nitrogen Dioxide | PASS | NA | Y | Tested pollutants: NO2, NO; Permitted Allowable Emission Rate = 74 ppmv@15%O2; Permitted Maximum Operating Rate = 10 MW; Average Tested Emission Rate = 38.8 ppmv@15%O2; Average Tested Operating Rate = 8.5 MW; Results = Passed; AFS Date = 2011-09-28 00:00:00.0; AFS ID = legacy) test 1 (Turbine & HRSG fired with biogas & Natural gas
2011 | 673 | 0448010737 | City of Toledo, Division of Water Reclamation | 3900 North Summit St. | Toledo | 43611 |  | Lucas | P109 | Natural Gas/Digester Gas/Landfill Gas powered combustion turbine for combined cycle cogeneration system | 2011-07-06 | none | Bureau Veritas Co |  |  |  |  | 7E | Nitrogen Oxide | PASS | NA | Y | Tested pollutants: NO2, NO; Permitted Allowable Emission Rate = 74 ppmv@15%O2; Permitted Maximum Operating Rate = 10 MW; Average Tested Emission Rate = 38.8 ppmv@15%O2; Average Tested Operating Rate = 8.5 MW; Results = Passed; AFS Date = 2011-09-28 00:00:00.0; AFS ID = legacy) test 1 (Turbine & HRSG fired with biogas & Natural gas
2011 | 674 | 0448010737 | City of Toledo, Division of Water Reclamation | 3900 North Summit St. | Toledo | 43611 |  | Lucas | P109 | Natural Gas/Digester Gas/Landfill Gas powered combustion turbine for combined cycle cogeneration system | 2011-07-07 | none | Bureau Veritas Co |  |  |  |  | 7E | Nitrogen Dioxide | PASS | NA | Y | Tested pollutants: NO2, NO; Permitted Allowable Emission Rate = 74 ppmv@15%O2; Permitted Maximum Operating Rate = 5 MW; Average Tested Emission Rate = 51 ppmv@15%O2; Average Tested Operating Rate = 5.5 MW; Results = Passed; AFS Date = 2011-09-28 00:00:00.0; AFS ID = legacy) test 1 (Turbine fired with biogas & Natural gas
2011 | 676 | 0448010737 | City of Toledo, Division of Water Reclamation | 3900 North Summit St. | Toledo | 43611 |  | Lucas | P109 | Natural Gas/Digester Gas/Landfill Gas powered combustion turbine for combined cycle cogeneration system | 2011-07-07 | none | Bureau Veritas Co |  |  |  |  | 7E | Nitrogen Oxide | PASS | NA | Y | Tested pollutants: NO2, NO; Permitted Allowable Emission Rate = 74 ppmv@15%O2; Permitted Maximum Operating Rate = 5 MW; Average Tested Emission Rate = 51 ppmv@15%O2; Average Tested Operating Rate = 5.5 MW; Results = Passed; AFS Date = 2011-09-28 00:00:00.0; AFS ID = legacy) test 1 (Turbine fired with biogas & Natural gas
2011 | 678 | 0448010737 | City of Toledo, Division of Water Reclamation | 3900 North Summit St. | Toledo | 43611 |  | Lucas | P109 | Natural Gas/Digester Gas/Landfill Gas powered combustion turbine for combined cycle cogeneration system | 2011-07-08 | none | Bureau Veritas Co |  |  |  |  | 7E | Nitrogen Oxide | PASS | NA | Y | Tested pollutants: NO2, NO; Permitted Allowable Emission Rate = 74 ppmv@15%O2; Permitted Maximum Operating Rate = 5 MW; Average Tested Emission Rate = 30.5 ppmv@15%O2; Average Tested Operating Rate = 1.8 MW; Results = Passed; AFS Date = 2011-09-28 00:00:00.0; AFS ID = legacy) test 3(Turbine fired with biogas vented to HRSG)
2011 | 679 | 0448010737 | City of Toledo, Division of Water Reclamation | 3900 North Summit St. | Toledo | 43611 |  | Lucas | P109 | Natural Gas/Digester Gas/Landfill Gas powered combustion turbine for combined cycle cogeneration system | 2011-07-08 | none | Bureau Veritas Co |  |  |  |  | 7E | Nitrogen Dioxide | PASS | NA | Y | Tested pollutants: NO2, NO; Permitted Allowable Emission Rate = 74 ppmv@15%O2; Permitted Maximum Operating Rate = 5 MW; Average Tested Emission Rate = 30.5 ppmv@15%O2; Average Tested Operating Rate = 1.8 MW; Results = Passed; AFS Date = 2011-09-28 00:00:00.0; AFS ID = legacy) test 3(Turbine fired with biogas vented to HRSG)
2011 | 681 | 0448010737 | City of Toledo, Division of Water Reclamation | 3900 North Summit St. | Toledo | 43611 |  | Lucas | P109 | Natural Gas/Digester Gas/Landfill Gas powered combustion turbine for combined cycle cogeneration system | 2011-07-09 | none | Bureau Veritas Co |  |  |  |  | 7E | Nitrogen Oxide | PASS | NA | Y | Tested pollutants: NO2, NO; Permitted Allowable Emission Rate = 74 ppmv@15%O2; Permitted Maximum Operating Rate = 5 MW; Average Tested Emission Rate = 25.2 ppmv@15%O2; Average Tested Operating Rate = 4 MW; Results = Passed; AFS Date = 2011-09-28 00:00:00.0; AFS ID = legacy) test 4 (HRSG fired with biogas and natural gas)
2011 | 682 | 0448010737 | City of Toledo, Division of Water Reclamation | 3900 North Summit St. | Toledo | 43611 |  | Lucas | P109 | Natural Gas/Digester Gas/Landfill Gas powered combustion turbine for combined cycle cogeneration system | 2011-07-09 | none | Bureau Veritas Co |  |  |  |  | 7E | Nitrogen Dioxide | PASS | NA | Y | Tested pollutants: NO2, NO; Permitted Allowable Emission Rate = 74 ppmv@15%O2; Permitted Maximum Operating Rate = 5 MW; Average Tested Emission Rate = 25.2 ppmv@15%O2; Average Tested Operating Rate = 4 MW; Results = Passed; AFS Date = 2011-09-28 00:00:00.0; AFS ID = legacy) test 4 (HRSG fired with biogas and natural gas)
2013 | 1111 | 0448010737 | City of Toledo, Division of Water Reclamation | 3900 North Summit St. | Toledo | 43611 |  | Lucas | P109 | Natural Gas/Digester Gas/Landfill Gas powered combustion turbine for combined cycle cogeneration system | 2013-09-19 | NONE | Bureau Veritas | 5 MW | 75 ppmv at 15% O2 | 3.2 MW | 41 ppmv at 15% O2 | 7E | Nitrogen Dioxide | PASS | NA | Y | Per TES/Central Office request, this test was to be conducted with:2 runs at the maximum firing rate of the turbine/HRSG at the maximum biogas flow rate (landfill gas + digester gas) and the maximum natural gas flow rate; and 1 run conducted at the maximum biogas flow rate (normal operation) since biogas is considered by NSPS KK to have a higher lb/mmBtu emission rate than that of natural gas. On a monthly average, the fuel burned at this emissions unit is greater than 50% biogas, so the applicable NOx emission limitation under NSPS KK is 74 ppmv at 15% O2. Run 1 was conducted while operating the turbine only at the maximum flow rate of biogas (2 MW) and run 2 was conducted while operating the turbine at maximum load (biogas + natural gas at 4.3 MW). Additional runs were not conducted since a bearing failed in the lube oil pump. Testing was re-scheduled for 10/10/2013 to complete the required test runs. | Yes
2013 | 1115 | 0448010737 | City of Toledo, Division of Water Reclamation | 3900 North Summit St. | Toledo | 43611 |  | Lucas | P109 | Natural Gas/Digester Gas/Landfill Gas powered combustion turbine for combined cycle cogeneration system | 2013-10-10 | NONE | Bureau Veritas | 10 MW | 74 ppmv at 15% O2 | 6.5 MW | 45 ppmv at 15% O2 | 7E | Nitrogen Dioxide | PASS | NA | Y | Per TES/Central Office request, this test was conducted with:2 runs at the maximum firing rate of the turbine/HRSG at the maximum biogas flow rate (landfill gas + digester gas) and the maximum natural gas flow rate; and 1 run conducted at the maximum biogas flow rate (normal operation) since biogas is considered by NSPS KK to have a higher lb/mmBtu emission rate than that of natural gas. On a monthly average, the fuel burned at this emissions unit is greater than 50% biogas, so the applicable NOx emission limitation under NSPS KK is 74 ppmv at 15% O2. Runs 1 and 2 were conducted at 8.8 megawatts with the maximum capacity of the turbine/HRSG being 10 MW. Run 3 was conducted at 2 MW with the maximum capacity of the turbine being 5 MW. | Yes

## Turbine CO
REPORTING YEAR | RECORD_NUMBER | FACILITY ID | FACILITY NAME | ADDRESS | CITY | ZIP5 | ZIP4 | COUNTY | EUID | EUID DESCRIPTION | EVALUATION DATE | CONTROL EQUPMENT | COMPANY PERFORMING TEST | MAX RATE | ALLOWABLE RATE | TESTED OPERATING RATE | TESTED EMISSION RATE | METHOD NUMBER | POLLUTANTS | RESULTS | CONFORM | AUDIT | NOTES | COULD_BE_GENERATOR
2004 | 800 | 0664000100 | Texas Eastern Transmission LP - Somerset | 1895 Big Inch Road | Somerset | 43783 | 0000 | Perry | B009 | Mars Solar Turbine, 10,600 HP, Natural gas-fired turbine used for natural gas compression. ser# 0260M | 2004-03-09 | none | CUBIX CORP. | 85.6 mmbh | 13 lb/hr | 106 mmbh | 3.12 lb/hr | 10 | CO - Carbon Monoxide | PASS | NA | Y
2004 | 1178 | 1483060328 | Texas Eastern Transmission - Lebanon | 1157 State Road 122 West | Lebanon | 45036 |  | Warren | P001 | 67.98 MMBtu natural gas fired turbine used for natural gas compression | 2004-07-09 | control equipment? | CUBIX |  |  |  |  | 7 | CO - Carbon Monoxide | PASS | NA | Y
2007 | 1299 | 1483060328 | Texas Eastern Transmission - Lebanon | 1157 State Road 122 West | Lebanon | 45036 |  | Warren | P001 | 67.98 MMBtu natural gas fired turbine used for natural gas compression | 2007-03-21 | LOW NOX LEAN AIR COMBUSTOR | CUBIX CORPORATION (GE) | 45.69 MMBTU/HR | 6.0 LB/HR | 44.7 MMBTU/HR (LOAD 98%) | 1.48 LB/HR | 10 | CO - Carbon Monoxide | PASS | NA | Y
2007 | 1328 | 0819780231 | TEXAS EASTERN TRANS, LP - GLEN KARN | 180 MIKESELL RD | Hollansburg | 45332 |  | Darke | B001 | 79.1 mmBtu/hr Natural Gas Turbine | 2007-07-11 | DRY LOW NOX BURNER | GE ENERGY MANAGEMENT SERVICES, INC. | 71.19 MMBTU/HR HEAT INPUT | 8.69 LB CO/HR | 52 MMBTU/HR HEAT INPUT;92% OF TURBINE CAPACITY | 1.05 LB CO/HR | 10 | CO - Carbon Monoxide | PASS | NA | Y | LOW CAPACITY DEMONSTRATION. NUMEROUS TEST DELAYS PUSHED THE DATE REPEATEDLY. THE UNIT WAS DELAYED FOR LACK OF DEMAND FOR NATURAL GAS BUT MORE IMPORTANTLY MAINTENANCE PROBLEMS RELATING TO FRACTURES IN THE BODY OF THE HOUSING. UPON REPAIR - THE TEST WAS COMPLETED. THE TEST WAS COMPOSED OF 12 RUNS TOTAL = 3 TEST RUNS PER OPERATING CAPACITY. FOUR OPERATING CAPACITIES SPANNING 92%, 95%, 98%, AND 100% OF THE NORMAL OPERATING RANGE AS ALLOWED BY SUBPART GG. NOX AND CO WERE TESTED IN EACH RANGE AND THE VALUES ARE GIVEN IN SEPARATE APPENDIX K FILES. TESTS AT THE DIFFERENT CAPACITIES CONDUCTED ON SAME DATE BUT ENTERED AS SUCCESSIVE DATES FOR CETA ENTRY PURPOSES.
2007 | 1330 | 0819780231 | TEXAS EASTERN TRANS, LP - GLEN KARN | 180 MIKESELL RD | Hollansburg | 45332 |  | Darke | B001 | 79.1 mmBtu/hr Natural Gas Turbine | 2007-07-12 | DRY LOW NOX BURNER | GE ENERGY MANAGEMENT SERVICES, INC. | 71.19 MMBTU/HR HEAT INPUT | 8.69 LB CO/HR | 59 MMBTU/HR HEAT INPUT;95% OF TURBINE CAPACITY | 0.85 LB CO/HR | 10 | CO - Carbon Monoxide | PASS | NA | Y | LOW/MID CAPACITY DEMONSTRATION. NUMEROUS TEST DELAYS PUSHED THE DATE REPEATEDLY. THE UNIT WAS DELAYED FOR LACK OF DEMAND FOR NATURAL GAS BUT MORE IMPORTANTLY MAINTENANCE PROBLEMS RELATING TO FRACTURES IN THE BODY OF THE HOUSING. UPON REPAIR - THE TEST WAS COMPLETED. THE TEST WAS COMPOSED OF 12 RUNS TOTAL = 3 TEST RUNS PER OPERATING CAPACITY. FOUR OPERATING CAPACITIES SPANNING 92%, 95%, 98%, AND 100% OF THE NORMAL OPERATING RANGE AS ALLOWED BY SUBPART GG. NOX AND CO WERE TESTED IN EACH RANGE AND THE VALUES ARE GIVEN IN SEPARATE APPENDIX K FILES. TESTS AT THE DIFFERENT CAPACITIES CONDUCTED ON SAME DATE BUT ENTERED AS SUCCESSIVE DATES FOR CETA ENTRY PURPOSES.
2007 | 1334 | 0819780231 | TEXAS EASTERN TRANS, LP - GLEN KARN | 180 MIKESELL RD | Hollansburg | 45332 |  | Darke | B001 | 79.1 mmBtu/hr Natural Gas Turbine | 2007-07-13 | DRY LOW NOX BURNER | GE ENERGY MANAGEMENT SERVICES, INC. | 71.19 MMBTU/HR HEAT INPUT | 8.69 LB CO/HR | 66 MMBTU/HR HEAT INPUT;98% OF TURBINE CAPACITY | 0.57 LB CO/HR | 10 | CO - Carbon Monoxide | PASS | NA | Y | MID/HIGH CAPACITY DEMONSTRATION. NUMEROUS TEST DELAYS PUSHED THE DATE REPEATEDLY. THE UNIT WAS DELAYED FOR LACK OF DEMAND FOR NATURAL GAS BUT MORE IMPORTANTLY MAINTENANCE PROBLEMS RELATING TO FRACTURES IN THE BODY OF THE HOUSING. UPON REPAIR - THE TEST WAS COMPLETED. THE TEST WAS COMPOSED OF 12 RUNS TOTAL = 3 TEST RUNS PER OPERATING CAPACITY. FOUR OPERATING CAPACITIES SPANNING 92%, 95%, 98%, AND 100% OF THE NORMAL OPERATING RANGE AS ALLOWED BY SUBPART GG. NOX AND CO WERE TESTED IN EACH RANGE AND THE VALUES ARE GIVEN IN SEPARATE APPENDIX K FILES. TESTS AT THE DIFFERENT CAPACITIES CONDUCTED ON SAME DATE BUT ENTERED AS SUCCESSIVE DATES FOR CETA ENTRY PURPOSES.
2007 | 1336 | 0819780231 | TEXAS EASTERN TRANS, LP - GLEN KARN | 180 MIKESELL RD | Hollansburg | 45332 |  | Darke | B001 | 79.1 mmBtu/hr Natural Gas Turbine | 2007-07-14 | DRY LOW NOX BURNER | GE ENERGY MANAGEMENT SERVICES, INC. | 71.19 MMBTU/HR HEAT INPUT | 8.69 LB CO/HR | 71 MMBTU/HR HEAT INPUT;100% OF TURBINE CAPACITY | 0.65 LB CO/HR | 10 | CO - Carbon Monoxide | PASS | NA | Y | HIGH CAPACITY DEMONSTRATION. NUMEROUS TEST DELAYS PUSHED THE DATE REPEATEDLY. THE UNIT WAS DELAYED FOR LACK OF DEMAND FOR NATURAL GAS BUT MORE IMPORTANTLY MAINTENANCE PROBLEMS RELATING TO FRACTURES IN THE BODY OF THE HOUSING. UPON REPAIR - THE TEST WAS COMPLETED. THE TEST WAS COMPOSED OF 12 RUNS TOTAL = 3 TEST RUNS PER OPERATING CAPACITY. FOUR OPERATING CAPACITIES SPANNING 92%, 95%, 98%, AND 100% OF THE NORMAL OPERATING RANGE AS ALLOWED BY SUBPART GG. NOX AND CO WERE TESTED IN EACH RANGE AND THE VALUES ARE GIVEN IN SEPARATE APPENDIX K FILES. TESTS AT THE DIFFERENT CAPACITIES CONDUCTED ON SAME DATE BUT ENTERED AS SUCCESSIVE DATES FOR CETA ENTRY PURPOSES.
2011 | 1166 | 1483060328 | Texas Eastern Transmission - Lebanon | 1157 State Road 122 West | Lebanon | 45036 |  | Warren | P001 | 67.98 MMBtu natural gas fired turbine used for natural gas compression | 2011-11-04 | LOW NOX LEAN AIR COMBUSTOR | Nordon Corporation | 45.69 MMBTU/HR | 6.0 LB/HR | 45.2 MMBTU/HR (LOAD 99%) | 0.1 LB/HR | 10 | CO - Carbon Monoxide | PASS | NA | Y
2011 | 1201 | 1667040085 | Kent State University Heating Plant | P.O. Box 5190 | Kent | 44242 | 0001 | Portage | B010 | Combustion Turbine CT 2 | 2011-12-01 | None | Air Compliance Testing Inc. | 76 MMBtu/hr | 0.13 lb/MMBtu 43.3 TPY | MMBtu/hr | 0.03 lb/MMBtu 10.12 TPY | 10 | CO - Carbon Monoxide | PASS | NA | Y | EPA Method 10 passed
2012 | 37 | 0124010117 | Dominion Transmission - Washington Compressor Station | 708 Parrott Road, N.W. | Washington Court House | 43160 |  | Fayette | B001 | Solar Centaur Combustion Turbine No. 1, 5500 HP | 2012-04-10 | None | Dominion Transmission | 100% | 14.3 lbs/hr | 100% torque | 0.26 lbs/hr | 10 | CO - Carbon Monoxide | PASS | NA | Y | Additional test run at 93% torque resulted in 0.32 lbs/hr CO.
2012 | 54 | 0124010117 | Dominion Transmission - Washington Compressor Station | 708 Parrott Road, N.W. | Washington Court House | 43160 |  | Fayette | B002 | Solar Centaur Combustion Turbine No. 2, 5500 HP | 2012-04-10 | None | Dominion Transmission | 100% | 14.3 lbs/hr | 100% torque | 1.18 lbs/hr | 10 | CO - Carbon Monoxide | PASS | NA | Y | Additional test run at 94% torque resulted in 4.48 lbs/hr CO.
2012 | 55 | 0124010117 | Dominion Transmission - Washington Compressor Station | 708 Parrott Road, N.W. | Washington Court House | 43160 |  | Fayette | B003 | Solar Centaur Combustion Turbine No. 3, 5500 HP | 2012-04-11 | None | Dominion Transmission | 100% | 14.3 lbs/hr | 100% torque | 0.51 lbs/hr | 10 | CO - Carbon Monoxide | PASS | NA | Y | Additional test run at 93% torque resulted in 2.67 lbs/hr CO.
2012 | 144 | 0145000307 | Dominion - Newark Compressor Station | 19042 Nashport Road | Nashport | 43830 |  | Licking | B002 | Solar Centaur Combustion Turbine No. 2, 5500 HP | 2012-04-03 | none | DOMINION TRANSMISSION | 5500 hp | 14.3 lbs/hr | 99% ngp | 1.31 lbs/hr | 10 | CO - Carbon Monoxide | PASS | NA | Y | Witnessed=No, but it says Witnessed By Adam Novak)
2012 | 145 | 0145000307 | Dominion - Newark Compressor Station | 19042 Nashport Road | Nashport | 43830 |  | Licking | B003 | Solar Centaur Combustion Turbine No. 3, 5500 HP | 2012-04-03 | none | DOMINION TRANSMISSION | 5500 hp | 14.3 lbs/hr | 99% ngp | 0.58 lbs/hr | 10 | CO - Carbon Monoxide | PASS | NA | Y | Witnessed=No, but it says Witnessed By Adam Novak)
2012 | 152 | 0145000307 | Dominion - Newark Compressor Station | 19042 Nashport Road | Nashport | 43830 |  | Licking | B001 | Solar Centaur Combustion Turbine No. 1, 5500 HP | 2012-04-04 | none | DOMINION TRANSMISSION | 5500 hp | 0.23 lbs/hr | 99% ngp | 14.3 lbs/hr | 10 | CO - Carbon Monoxide | PASS | NA | Y | Witnessed=No, but it says Witnessed By Adam Novak)
2013 | 974 | 0387020374 | OMEGA JV2 Bowling Green Peaking Station | 811 East Poe Road | Bowling Green | 43402 |  | Wood | P001 | 422.57 mmBtu/hour natural gas-fired turbine: modification to correct the emission limitations | 2013-08-08 | Water injection | Grace Consulting, Inc. | 422.57 MMBtu/hr | 263.8 lbs/hr | 305.6 MMBtu/hr | 11.21 lbs/hr | 10 | CO - Carbon Monoxide | PASS | NA | N | Low process weight rate determination made by Mohammad Smidi.
2014 | 627 | 0661005010 | E2 Appalachian Compression LLC - Upper Hill | Opossum Run Rd and Town Hwy 120 | Sarahsville | 43779 |  | Noble | P007 | 1,680 Hp. Waukesha (L7044GSI) natural gas-fired, rich burn, turbocharged, with oxidation catalyst, compressor engine. | 2014-11-06 | C-7(Catalytic Converter): Engine Catalyst; C-8(Catalytic Converter): Engine Catalyst; C-9(Catalytic Converter): Engine Catalyst | E2 Energy Services | 1680 Hp | 0.94 lb/hr | 1528 Hp | 0.26 lb/hr | 10 | CO - Carbon Monoxide | PASS | NA | Y | Method 10 not used. Method 3A and ASTM 6348-03 used
2014 | 772 | 0661005010 | E2 Appalachian Compression LLC - Upper Hill | Opossum Run Rd and Town Hwy 120 | Sarahsville | 43779 |  | Noble | P009 | 1,680 Hp. Waukesha (L7044GSI) natural gas-fired, rich burn, turbocharged, with oxidation catalyst, compressor engine. | 2014-11-06 | C-7(Catalytic Converter): Engine Catalyst; C-8(Catalytic Converter): Engine Catalyst; C-9(Catalytic Converter): Engine Catalyst | E2 Energy Services | 1680 Hp | 0.94 lb/hr | 1585 Hp | 0.52 lb/hr | 10 | CO - Carbon Monoxide | PASS | NA | Y | Method 10 not used. Method 3A and ASTM 6348-03 used
2014 | 778 | 0661005010 | E2 Appalachian Compression LLC - Upper Hill | Opossum Run Rd and Town Hwy 120 | Sarahsville | 43779 |  | Noble | P008 | 1,680 Hp. Waukesha (L7044GSI) natural gas-fired, rich burn, turbocharged, with oxidation catalyst, compressor engine. | 2014-11-06 | C-7(Catalytic Converter): Engine Catalyst; C-8(Catalytic Converter): Engine Catalyst; C-9(Catalytic Converter): Engine Catalyst | E2 Energy Services | 1680 Hp | 0.94 lb/hr | 1221 Hp | 0.62 lb/hr | 10 | CO - Carbon Monoxide | PASS | NA | Y | Method 10 not used. Method 3A and ASTM 6348-03 used
2014 | 782 | 0661005010 | E2 Appalachian Compression LLC - Upper Hill | Opossum Run Rd and Town Hwy 120 | Sarahsville | 43779 |  | Noble | P004 | 1,680 Hp. Waukesha (L7044GSI) natural gas-fired, rich burn, turbocharged, with oxidation catalyst, compressor engine. | 2014-11-10 | C-4(Catalytic Converter): Engine Catalyst | E2 Energy Services | 1680 Hp | 0.94 lb/hr | 1547 Hp | 0.63 lb/hr | 10 | CO - Carbon Monoxide | PASS | NA | Y | Method 10 not used. Method 3a and ASTM 6348-03 used
2014 | 860 | 0661005010 | E2 Appalachian Compression LLC - Upper Hill | Opossum Run Rd and Town Hwy 120 | Sarahsville | 43779 |  | Noble | P002 | 1,680 Hp. Waukesha (L7044GSI) natural gas-fired, rich burn, turbocharged, with oxidation catalyst, compressor engine. | 2014-11-12 | C-2(Catalytic Converter): Engine Catalyst; C-3(Catalytic Converter): Engine Catalyst | E2 Energy Services | 1680 Hp | 0.94 lb/hr | 1575 Hp | 0.87 lb/hr | 10 | CO - Carbon Monoxide | PASS | NA | Y | Method 10 not used. Method 3a and ASTM 6348-03
2014 | 864 | 0661005010 | E2 Appalachian Compression LLC - Upper Hill | Opossum Run Rd and Town Hwy 120 | Sarahsville | 43779 |  | Noble | P002 | 1,680 Hp. Waukesha (L7044GSI) natural gas-fired, rich burn, turbocharged, with oxidation catalyst, compressor engine. | 2014-11-13 | C-2(Catalytic Converter): Engine Catalyst; C-3(Catalytic Converter): Engine Catalyst | E2 Energy Services | 1680 Hp | 0.94 lb/hr | 1575 Hp | 0.87 lb/hr | 10 | CO - Carbon Monoxide | PASS | NA | Y | Method 10 not used. Method 3a and ASTM 6348-03
2014 | 866 | 0661005010 | E2 Appalachian Compression LLC - Upper Hill | Opossum Run Rd and Town Hwy 120 | Sarahsville | 43779 |  | Noble | P003 | 1,680 Hp. Waukesha (L7044GSI) natural gas-fired, rich burn, turbocharged, with oxidation catalyst, compressor engine. | 2014-11-12 | C-2(Catalytic Converter): Engine Catalyst; C-3(Catalytic Converter): Engine Catalyst | E2 Energy Services | 1680 Hp | 0.94 lb/hr | 1512 Hp | 0.89 lb/hr | 10 | CO - Carbon Monoxide | PASS | NA | Y | Method 10 not used. Method 3a and ASTM 6348-03
2014 | 870 | 0661005010 | E2 Appalachian Compression LLC - Upper Hill | Opossum Run Rd and Town Hwy 120 | Sarahsville | 43779 |  | Noble | P003 | 1,680 Hp. Waukesha (L7044GSI) natural gas-fired, rich burn, turbocharged, with oxidation catalyst, compressor engine. | 2014-11-13 | C-2(Catalytic Converter): Engine Catalyst; C-3(Catalytic Converter): Engine Catalyst | E2 Energy Services | 1680 Hp | 0.94 lb/hr | 1512 Hp | 0.89 lb/hr | 10 | CO - Carbon Monoxide | PASS | NA | Y | Method 10 not used. Method 3a and ASTM 6348-03
2014 | 908 | 0661005010 | E2 Appalachian Compression LLC - Upper Hill | Opossum Run Rd and Town Hwy 120 | Sarahsville | 43779 |  | Noble | P009 | 1,680 Hp. Waukesha (L7044GSI) natural gas-fired, rich burn, turbocharged, with oxidation catalyst, compressor engine. | 2014-07-15 | C-9(Catalytic Converter): Engine Catalyst | E2 Energy Services | 1,680 Hp | 0.94 lb/hr | 1,545 Hp | 1.96 lbs/hr | 10 | CO - Carbon Monoxide | FAIL | NA | Y
2015 | 255 | 0661005027 | E2 Appalachian LLC - Batesville | 58380 St John Rd | Quaker City | 43773 |  | Noble | P003 | 1,680 Hp. Waukesha (L7044GSI) natural gas-fired, rich burn, turbocharged, with oxidation catalyst, compressor engine | 2015-01-27 | C2701C(Catalytic Converter): Engine Catalyst | E2 Energy Services | 1680 hp | 2.0 g/hp-hr | 1277 hp | 0.04 g/hp-hr | 6348 03 | CO - Carbon Monoxide | PP | NA | Y
2015 | 278 | 0661005027 | E2 Appalachian LLC - Batesville | 58380 St John Rd | Quaker City | 43773 |  | Noble | P001 | 1,680 Hp. Waukesha (L7044GSI) natural gas-fired, rich burn, turbocharged, with oxidation catalyst, compressor engine | 2015-01-26 | C2701C(Catalytic Converter): Engine Catalyst | E2 Energy Services | 1680 hp | 2.0 g/hp-hr | 1400 hp | 0.07 g/hp-hr | 6348 03 | CO - Carbon Monoxide | PP | NA | Y
2015 | 476 | 0661005027 | E2 Appalachian LLC - Batesville | 58380 St John Rd | Quaker City | 43773 |  | Noble | P004 | 1,680 Hp. Waukesha (L7044GSI) natural gas-fired, rich burn, turbocharged, with oxidation catalyst, compressor engine | 2015-02-20 | C2704C(Catalytic Converter): Engine Catalyst | E2 Energy Services | 1,680 hp | 2.0 g/hp-hr | 1,510 hp | 0.11 g/hp-hr | 6348 03 | CO - Carbon Monoxide | PP | NA | Y
2015 | 531 | 0661005027 | E2 Appalachian LLC - Batesville | 58380 St John Rd | Quaker City | 43773 |  | Noble | P002 | 1,680 Hp. Waukesha (L7044GSI) natural gas-fired, rich burn, turbocharged, with oxidation catalyst, compressor engine | 2015-01-26 | C2701C(Catalytic Converter): Engine Catalyst | E2 Energy Services | 1680 hp | 2.0 g/hp-hr | 1361 hp | 0.16 g/hp-hr | 6348 03 | CO - Carbon Monoxide | PP | NA | Y
2015 | 534 | 0661005027 | E2 Appalachian LLC - Batesville | 58380 St John Rd | Quaker City | 43773 |  | Noble | P007 | 1,680 Hp. Waukesha (L7044GSI) natural gas-fired, rich burn, turbocharged, with oxidation catalyst, compressor engine | 2015-02-19 | C2707C(Catalytic Converter): Engine Catalyst | E2 Energy Services | 1,680 hp | 2.0 g/hp-hr | 1,512 hp | 0.18 g/hp-hr | 6348 03 | CO - Carbon Monoxide | PP | NA | Y
2015 | 697 | 0661005027 | E2 Appalachian LLC - Batesville | 58380 St John Rd | Quaker City | 43773 |  | Noble | P008 | 1,680 Hp. Waukesha (L7044GSI) natural gas-fired, rich burn, turbocharged, with oxidation catalyst, compressor engine | 2015-02-19 | C2708C(Catalytic Converter): Engine Catalyst | E2 Energy Services | 1,680 hp | 2.0 g/hp-hr | 1,512 hp | 0.24 g/hp-hr | 6348 03 | CO - Carbon Monoxide | PP | NA | Y
2015 | 698 | 0661005027 | E2 Appalachian LLC - Batesville | 58380 St John Rd | Quaker City | 43773 |  | Noble | P005 | 1,680 Hp. Waukesha (L7044GSI) natural gas-fired, rich burn, turbocharged, with oxidation catalyst, compressor engine | 2015-02-27 | C2705C(Catalytic Converter): Engine Catalyst | E2 Energy Services | 1,680 hp | 2.0 g/hp-hr | 1,295 hp | 0.30 g/hp-hr | 6348 03 | CO - Carbon Monoxide | PP | NA | Y
2016 | 719 | 0661005027 | E2 Appalachian LLC - Batesville | 58380 St John Rd | Quaker City | 43773 |  | Noble | P007 | 1,680 Hp. Waukesha (L7044GSI) natural gas-fired, rich burn, turbocharged, with oxidation catalyst, compressor engine | 2016-07-11 | C2701C(Catalytic Converter): Engine Catalyst; C2707C(Catalytic Converter): Engine Catalyst; C2708C(Catalytic Converter): Engine Catalyst | Alliance Source Testing | 1,680 hp | 2.0 g/hp-hr | 1,607 hp | 0.098 g/hp-hr | 10 | CO - Carbon Monoxide | PP | Y | NA
2016 | 1159 | 0661005027 | E2 Appalachian LLC - Batesville | 58380 St John Rd | Quaker City | 43773 |  | Noble | P008 | 1,680 Hp. Waukesha (L7044GSI) natural gas-fired, rich burn, turbocharged, with oxidation catalyst, compressor engine | 2016-07-11 | C2701C(Catalytic Converter): Engine Catalyst; C2707C(Catalytic Converter): Engine Catalyst; C2708C(Catalytic Converter): Engine Catalyst | Alliance Source Testing | 1,680 hp | 2.0 g/hp-hr | 1,568 hp | 0.105 g/hp-hr | 10 | CO - Carbon Monoxide | PP | Y | NA
2016 | 1186 | 0661005027 | E2 Appalachian LLC - Batesville | 58380 St John Rd | Quaker City | 43773 |  | Noble | P006 | 1,680 Hp. Waukesha (L7044GSI) natural gas-fired, rich burn, turbocharged, with oxidation catalyst, compressor engine | 2016-07-12 | C2706C(Catalytic Converter): Engine Catalyst | Alliance Source Testing | 1,680 hp | 0.254 g/hp-hr | 1,490 hp | 0.116 g/hp-hr | 10 | CO - Carbon Monoxide | PP | Y | NA
2016 | 1187 | 0630005041 | E2 Energy Services - Borton | 65483 Lydick Rd | Quaker City | 43773 |  | Guernsey | P002 | 1,680 Hp. Waukesha (L7044GSI) natural gas-fired, rich burn, turbocharged, with oxidation catalyst, compressor engine (Model Year 2014) | 2016-03-02 | C-2701C(Catalytic Converter): Engine Catalyst | E2 Energy Services | 1680 hp | 0.174 g/hp-hr | 1519 hp | 0.12 g/hp-hr | 6348 03 | CO - Carbon Monoxide | PP | N | NA
2016 | 1287 | 0661005027 | E2 Appalachian LLC - Batesville | 58380 St John Rd | Quaker City | 43773 |  | Noble | P001 | 1,680 Hp. Waukesha (L7044GSI) natural gas-fired, rich burn, turbocharged, with oxidation catalyst, compressor engine | 2016-07-11 | C2701C(Catalytic Converter): Engine Catalyst; C2707C(Catalytic Converter): Engine Catalyst; C2708C(Catalytic Converter): Engine Catalyst | Alliance Source Testing | 1,680 hp | 2.0 g/hp-hr | 1,529 hp | 0.131 g/hp-hr | 10 | CO - Carbon Monoxide | PP | Y | NA
2016 | 1294 | 0661005027 | E2 Appalachian LLC - Batesville | 58380 St John Rd | Quaker City | 43773 |  | Noble | P003 | 1,680 Hp. Waukesha (L7044GSI) natural gas-fired, rich burn, turbocharged, with oxidation catalyst, compressor engine | 2016-03-23 | C2703C(Catalytic Converter): Engine Catalyst | E2 Appalachian | 1680 hp | 2.0 g/hp-hr | 1348 hp | 0.1407 g/hp-hr | 6348 03 | CO - Carbon Monoxide | PP | Y | NA
2016 | 1295 | 0661005010 | E2 Appalachian Compression LLC - Upper Hill | Opossum Run Rd and Town Hwy 120 | Sarahsville | 43779 |  | Noble | P007 | 1,680 Hp. Waukesha (L7044GSI) natural gas-fired, rich burn, turbocharged, with oxidation catalyst, compressor engine. | 2016-03-17 | C-7(Catalytic Converter): Engine Catalyst; C-8(Catalytic Converter): Engine Catalyst | Alliance Source Testing | 1680 hp | 4.0 g/hp-hr | 1464 hp | 0.14g/hp-hr | 10 | CO - Carbon Monoxide | PP | Y | NA
2016 | 1305 | 0630005041 | E2 Energy Services - Borton | 65483 Lydick Rd | Quaker City | 43773 |  | Guernsey | P004 | 1,680 Hp. Waukesha (L7044GSI) natural gas-fired, rich burn, turbocharged, with oxidation catalyst, compressor engine (Model Year 2014) | 2016-05-12 | C-2703C(Catalytic Converter): Engine Catalyst | E2 Energy Services | 1680 hp | 0.174 g/hp-hr | 1348 hp | 0.156 g/hp-hr | 6348 03 | CO - Carbon Monoxide | PP | Y | NA
2016 | 1311 | 0661005027 | E2 Appalachian LLC - Batesville | 58380 St John Rd | Quaker City | 43773 |  | Noble | P005 | 1,680 Hp. Waukesha (L7044GSI) natural gas-fired, rich burn, turbocharged, with oxidation catalyst, compressor engine | 2016-03-31 | C2705C(Catalytic Converter): Engine Catalyst | E2 Appalachian | 1680 hp | 2.0 g/hp-hr | 1425 hp | 0.1597 g/hp-hr | 6348 03 | CO - Carbon Monoxide | PP | Y | NA
2016 | 1364 | 0661005027 | E2 Appalachian LLC - Batesville | 58380 St John Rd | Quaker City | 43773 |  | Noble | P001 | 1,680 Hp. Waukesha (L7044GSI) natural gas-fired, rich burn, turbocharged, with oxidation catalyst, compressor engine | 2016-04-13 | C2701C(Catalytic Converter): Engine Catalyst | E2 Appalachian | 1680 hp | 2.0 g/hp-hr | 1539 hp | 0.199 g/hp-hr | 6348 03 | CO - Carbon Monoxide | PP | Y | NA
2016 | 1372 | 0661005010 | E2 Appalachian Compression LLC - Upper Hill | Opossum Run Rd and Town Hwy 120 | Sarahsville | 43779 |  | Noble | P009 | 1,680 Hp. Waukesha (L7044GSI) natural gas-fired, rich burn, turbocharged, with oxidation catalyst, compressor engine. | 2016-04-29 | C-3(Catalytic Converter): Engine Catalyst; C-9(Catalytic Converter): Engine Catalyst | Alliance Source Testing | 1680 hp | 4.0 g/hp-hr | 1646 hp | 0.21 g/hp-hr | 10 | CO - Carbon Monoxide | PP | Y | NA
2016 | 1375 | 0661005010 | E2 Appalachian Compression LLC - Upper Hill | Opossum Run Rd and Town Hwy 120 | Sarahsville | 43779 |  | Noble | P009 | 1,680 Hp. Waukesha (L7044GSI) natural gas-fired, rich burn, turbocharged, with oxidation catalyst, compressor engine. | 2016-04-29 | C-3(Catalytic Converter): Engine Catalyst; C-9(Catalytic Converter): Engine Catalyst | Ecotest Energy Services | 1680 hp | 4.0 g/hp-hr | 1646 hp | 0.21 g/hp-hr | 6348 03 | CO - Carbon Monoxide | PP | Y | NA
2016 | 1444 | 0661005010 | E2 Appalachian Compression LLC - Upper Hill | Opossum Run Rd and Town Hwy 120 | Sarahsville | 43779 |  | Noble | P008 | 1,680 Hp. Waukesha (L7044GSI) natural gas-fired, rich burn, turbocharged, with oxidation catalyst, compressor engine. | 2016-03-17 | C-7(Catalytic Converter): Engine Catalyst; C-8(Catalytic Converter): Engine Catalyst | Alliance Source Testing | 1680 hp | 4.0 g/hp-hr | 1406 hp | 0.24 g/hp-hr | 10 | CO - Carbon Monoxide | PP | Y | NA
2016 | 1451 | 0661005027 | E2 Appalachian LLC - Batesville | 58380 St John Rd | Quaker City | 43773 |  | Noble | P002 | 1,680 Hp. Waukesha (L7044GSI) natural gas-fired, rich burn, turbocharged, with oxidation catalyst, compressor engine | 2016-04-28 | C2702C(Catalytic Converter): Engine Catalyst | Alliance Source Testing | 1680 hp | 2.0 g/hp-hr | 1529 hp | 0.242 g/hp-hr | 10 | CO - Carbon Monoxide | PP | N | NA
2016 | 1459 | 0661005027 | E2 Appalachian LLC - Batesville | 58380 St John Rd | Quaker City | 43773 |  | Noble | P006 | 1,680 Hp. Waukesha (L7044GSI) natural gas-fired, rich burn, turbocharged, with oxidation catalyst, compressor engine | 2016-04-01 | C2705C(Catalytic Converter): Engine Catalyst | E2 Appalachian | 1680 hp | 0.254 g/hp-hr | 1551 hp | 0.2585 g/hp-hr | 6348 03 | CO - Carbon Monoxide | FF | Y | NA
2016 | 1468 | 0661005027 | E2 Appalachian LLC - Batesville | 58380 St John Rd | Quaker City | 43773 |  | Noble | P004 | 1,680 Hp. Waukesha (L7044GSI) natural gas-fired, rich burn, turbocharged, with oxidation catalyst, compressor engine | 2016-03-30 | C2704C(Catalytic Converter): Engine Catalyst | E2 Appalachian | 1680 hp | 2.0 g/hp-hr | 1470 hp | 0.2795 g/hp-hr | 6348 03 | CO - Carbon Monoxide | PP | Y | NA
2016 | 1501 | 0661005027 | E2 Appalachian LLC - Batesville | 58380 St John Rd | Quaker City | 43773 |  | Noble | P002 | 1,680 Hp. Waukesha (L7044GSI) natural gas-fired, rich burn, turbocharged, with oxidation catalyst, compressor engine | 2016-03-24 | C2702C(Catalytic Converter): Engine Catalyst | E2 Appalachian | 1680 hp | 2.0 g/hp-hr | 1473 hp | 0.384 g/hp-hr | 6348 03 | CO - Carbon Monoxide | PP | Y | NA
2016 | 1502 | 0661005027 | E2 Appalachian LLC - Batesville | 58380 St John Rd | Quaker City | 43773 |  | Noble | P002 | 1,680 Hp. Waukesha (L7044GSI) natural gas-fired, rich burn, turbocharged, with oxidation catalyst, compressor engine | 2016-04-14 | C2702C(Catalytic Converter): Engine Catalyst | E2 Energy Services | 1680 hp | 2.0 g/hp-hr | 1473 hp | 0.384 g/hp-hr | 6348 03 | CO - Carbon Monoxide | PP | N | NA
2016 | 1504 | 0661005027 | E2 Appalachian LLC - Batesville | 58380 St John Rd | Quaker City | 43773 |  | Noble | P008 | 1,680 Hp. Waukesha (L7044GSI) natural gas-fired, rich burn, turbocharged, with oxidation catalyst, compressor engine | 2016-04-14 | C2708C(Catalytic Converter): Engine Catalyst | E2 Appalachian | 1680 hp | 2.0 g/hp-hr | 1475 hp | 0.4356 g/hp-hr | 6348 03 | CO - Carbon Monoxide | PP | Y | NA
2016 | 1520 | 0661005010 | E2 Appalachian Compression LLC - Upper Hill | Opossum Run Rd and Town Hwy 120 | Sarahsville | 43779 |  | Noble | P003 | 1,680 Hp. Waukesha (L7044GSI) natural gas-fired, rich burn, turbocharged, with oxidation catalyst, compressor engine. | 2016-04-29 | C-3(Catalytic Converter): Engine Catalyst; C-9(Catalytic Converter): Engine Catalyst | Alliance Source Testing | 1680 hp | 4.0 g/hp-hr | 1658 hp | 0.57 g/hp-hr | 10 | CO - Carbon Monoxide | PP | Y | NA
2016 | 1523 | 0661005010 | E2 Appalachian Compression LLC - Upper Hill | Opossum Run Rd and Town Hwy 120 | Sarahsville | 43779 |  | Noble | P003 | 1,680 Hp. Waukesha (L7044GSI) natural gas-fired, rich burn, turbocharged, with oxidation catalyst, compressor engine. | 2016-04-29 | C-3(Catalytic Converter): Engine Catalyst; C-9(Catalytic Converter): Engine Catalyst | Ecotest Energy Services | 1680 hp | 4.0 g/hp-hr | 1658 hp | 0.57 g/hp-hr | 6348 03 | CO - Carbon Monoxide | PP | Y | NA
2016 | 1659 | 0661005010 | E2 Appalachian Compression LLC - Upper Hill | Opossum Run Rd and Town Hwy 120 | Sarahsville | 43779 |  | Noble | P008 | 1,680 Hp. Waukesha (L7044GSI) natural gas-fired, rich burn, turbocharged, with oxidation catalyst, compressor engine. | 2016-07-13 | C-2(Catalytic Converter): Engine Catalyst; C-8(Catalytic Converter): Engine Catalyst | Alliance Source Testing | 1,680 hp | 540 hp | 1,518 hp | 23.3 ppm | 10 | CO - Carbon Monoxide | PP | Y | NA
2016 | 1695 | 0661005010 | E2 Appalachian Compression LLC - Upper Hill | Opossum Run Rd and Town Hwy 120 | Sarahsville | 43779 |  | Noble | P002 | 1,680 Hp. Waukesha (L7044GSI) natural gas-fired, rich burn, turbocharged, with oxidation catalyst, compressor engine. | 2016-07-13 | C-2(Catalytic Converter): Engine Catalyst; C-8(Catalytic Converter): Engine Catalyst | Alliance Source Testing | 1,680 hp | 540 ppm | 1,529 hp | 36.7 ppm | 10 | CO - Carbon Monoxide | PP | Y | NA
2016 | 1803 | 0744000150 | Hanging Rock Energy Facility | 1395 County Rd 1A | Ironton | 45638 |  | Lawrence | P001 | GE 7FA natural gas fired dry low NOx (DLN) combustion turbine No. 1, nominally rated at 2,045 MMBtu/hr, with duct burner nominally rated at 587MMBtu/hr operating in combined cycle mode controlled by Selective Calalytic Reduction (SCR) | 2016-04-05 | SCR - 1GT1(Other): Min temp - 525 F; SCR - 1GT2(Other): Min temp - 525 F | Mostardi Platt | 2,632 MMbtu/hr | duct burners operating 47.9 lb/hr/8 ppmvd at 15% | 2,436 MMbtu/hr avg | 1.19 lb/hr 0.2 ppmvd at 15% O2 | 10 | CO - Carbon Monoxide | PP | Y | NA | Tests were conducted with DUCT BURNERS OPERATING
2016 | 1804 | 0744000150 | Hanging Rock Energy Facility | 1395 County Rd 1A | Ironton | 45638 |  | Lawrence | P001 | GE 7FA natural gas fired dry low NOx (DLN) combustion turbine No. 1, nominally rated at 2,045 MMBtu/hr, with duct burner nominally rated at 587MMBtu/hr operating in combined cycle mode controlled by Selective Calalytic Reduction (SCR) | 2016-04-07 | SCR - 1GT1(Other): Min temp - 525 F; SCR - 1GT2(Other): Min temp - 525 F | Mostardi Platt | 2,632 MMbtu/hr | duct burners operating 47.9 lb/hr/8 ppmvd at 15% | 2,436 MMbtu/hr avg | 1.19 lb/hr 0.2 ppmvd at 15% O2 | 10 | CO - Carbon Monoxide | PP | Y | NA | Tests were conducted with DUCT BURNERS OPERATING
2016 | 1805 | 0744000150 | Hanging Rock Energy Facility | 1395 County Rd 1A | Ironton | 45638 |  | Lawrence | P002 | GE 7FA natural gas fired dry low NOx (DLN) combustion turbine No. 2, nominally rated at 2,045 MMBtu/hr, with duct burner nominally rated at 587 MMBtu/hr operating in combined cycle mode controlled by Selective Calalytic Reduction (SCR) | 2016-04-07 | SCR - 1GT1(Other): Min temp - 525 F; SCR - 1GT2(Other): Min temp - 525 F | Mostardi Platt | 2,632 MMbtu/hr | duct burners operating 47.9 lb/hr/8 ppmvd at 15% | 2,370.1 MMBtu/hr avg | 1.09 lb/hr 0.2 ppmvd at 15% O2 | 10 | CO - Carbon Monoxide | PP | Y | NA | Tests were conducted with DUCT BURNERS OPERATING
2016 | 1806 | 0744000150 | Hanging Rock Energy Facility | 1395 County Rd 1A | Ironton | 45638 |  | Lawrence | P003 | GE 7FA natural gas fired dry low NOx (DLN) combustion turbine No. 3, nominally rated at 2,045 MMBtu/hr, with duct burner nominally rated at 587 MMBtu/hr operating in combined cycle mode controlled by Selective Calalytic Reduction (SCR) | 2016-04-07 | SCR - 1GT1(Other): Min temp - 525 F; SCR - 1GT2(Other): Min temp - 525 F | Mostardi Platt | 2,632 MMbtu/hr | duct burners operating 47.9 lb/hr/8 ppmvd at 15% | 2,375.8 MMBtu/hr avg | 1.07 lb/hr 0.2 ppmvd at 15% O2 | 10 | CO - Carbon Monoxide | PP | Y | NA | Tests were conducted with DUCT BURNERS OPERATING
2016 | 1807 | 0744000150 | Hanging Rock Energy Facility | 1395 County Rd 1A | Ironton | 45638 |  | Lawrence | P004 | GE 7FA natural gas fired dry low NOx (DLN) combustion turbine No. 4, nominally rated at 2,045 MMBtu/hr, with duct burner nominally rated at 587 MMBtu/hr operating in combined cycle mode controlled by Selective Calalytic Reduction (SCR) | 2016-04-07 | SCR - 1GT1(Other): Min temp - 525 F; SCR - 1GT2(Other): Min temp - 525 F | Mostardi Platt | 2,632 MMbtu/hr | duct burners operating 47.9 lb/hr/8 ppmvd at 15% | 2,342.7 MMBtu/hr avg | 0.92 lb/hr 0.2 ppmvd at 15% O2 | 10 | CO - Carbon Monoxide | PP | Y | NA | Tests were conducted with DUCT BURNERS OPERATING
2016 | 1824 | 0744000150 | Hanging Rock Energy Facility | 1395 County Rd 1A | Ironton | 45638 |  | Lawrence | P001 | GE 7FA natural gas fired dry low NOx (DLN) combustion turbine No. 1, nominally rated at 2,045 MMBtu/hr, with duct burner nominally rated at 587MMBtu/hr operating in combined cycle mode controlled by Selective Calalytic Reduction (SCR) | 2016-04-08 | SCR - 1GT1(Other): Min temp - 525 F; SCR - 1GT2(Other): Min temp - 525 F | Mostardi Platt | 2,045 MMbtu/hr | without duct burners 28.0 lb/hr/6 ppmvd at 15% | 1,967.2 MMbtu/hr avg | 2.02 lb/hr 0.5 ppmvd at 15% O2 | 10 | CO - Carbon Monoxide | PP | Y | NA | Tests were conducted WITHOUT duct burners operating.
2016 | 1825 | 0744000150 | Hanging Rock Energy Facility | 1395 County Rd 1A | Ironton | 45638 |  | Lawrence | P002 | GE 7FA natural gas fired dry low NOx (DLN) combustion turbine No. 2, nominally rated at 2,045 MMBtu/hr, with duct burner nominally rated at 587 MMBtu/hr operating in combined cycle mode controlled by Selective Calalytic Reduction (SCR) | 2016-04-08 | SCR - 1GT1(Other): Min temp - 525 F; SCR - 1GT2(Other): Min temp - 525 F | Mostardi Platt | 2,045 MMbtu/hr | without duct burners 28.0 lb/hr/6 ppmvd at 15% | 1,967.2 MMBtu/hr avg | 1.90 lb/hr 0.4 ppmvd at 15% O2 | 10 | CO - Carbon Monoxide | PP | Y | NA | Tests were conducted WITHOUT duct burners operating.
2016 | 1826 | 0744000150 | Hanging Rock Energy Facility | 1395 County Rd 1A | Ironton | 45638 |  | Lawrence | P003 | GE 7FA natural gas fired dry low NOx (DLN) combustion turbine No. 3, nominally rated at 2,045 MMBtu/hr, with duct burner nominally rated at 587 MMBtu/hr operating in combined cycle mode controlled by Selective Calalytic Reduction (SCR) | 2016-04-08 | SCR - 1GT1(Other): Min temp - 525 F; SCR - 1GT2(Other): Min temp - 525 F | Mostardi Platt | 2,045 MMbtu/hr | without duct burners 28.0 lb/hr/6 ppmvd at 15% | 1,945.2 MMBtu/hr avg | 2.13 lb/hr 0.5 ppmvd at 15% O2 | 10 | CO - Carbon Monoxide | PP | Y | NA | Tests were conducted WITHOUT duct burners operating.
2016 | 1827 | 0744000150 | Hanging Rock Energy Facility | 1395 County Rd 1A | Ironton | 45638 |  | Lawrence | P004 | GE 7FA natural gas fired dry low NOx (DLN) combustion turbine No. 4, nominally rated at 2,045 MMBtu/hr, with duct burner nominally rated at 587 MMBtu/hr operating in combined cycle mode controlled by Selective Calalytic Reduction (SCR) | 2016-04-08 | SCR - 1GT1(Other): Min temp - 525 F; SCR - 1GT2(Other): Min temp - 525 F | Mostardi Platt | 2,045 MMbtu/hr | without duct burners 28.0 lb/hr/6 ppmvd at 15% | 1908.2 MMBtu/hr avg | 2.36 lb/hr 0.6 ppmvd at 15% O2 | 10 | CO - Carbon Monoxide | PP | Y | NA | Tests were conducted WITHOUT duct burners operating.
2016 | 2342 | 1483060328 | Texas Eastern Transmission - Lebanon | 1157 State Road 122 West | Lebanon | 45036 |  | Warren | P006 | Solar Taurus, 68.34 MMBtu/hr (ISO conditions), natural gas-fired turbine used for natural gas compression | 2016-11-09 | P006 Ox Cat(Other): oxidation catalyst | Nordon Corporation | 68.34 MMBtu/hr | < 10 TPY | 61.345 MMBtu/hr | 0.38 TPY | 10 | CO - Carbon Monoxide | PP | Y | NA | Stack Test Report - Compliance Report ID#130459 ITT - Compliance Report ID#129355 Permit - PTI P120361 1. An example calculation of EPA Method 4- moisture was not originally included in the emission compliance test report. The test report stated that EPA
2004 | 119 | 0165000132 | AEP Generation Resources Inc., - Darby Plant | 12509 Adkins Road | Mt. Sterling | 43143 | 9061 | Pickaway | P001 | Natural Gas or number two fuel oil-fired, simple cycle, combustion turbine having a nominal capacity of 1,115.2 MMBTU/hr (80 MW, nominal), controlled with a dry low NOx combustor; CT1 - Combustion Turbine No.1; *Modified | 2004-08-03 | n/a | SHAW ENVIRONMENTAL, INC. |  |  |  |  | 10 | CO - Carbon Monoxide | PASS | NA | Y |  | Yes
2004 | 121 | 0165000132 | AEP Generation Resources Inc., - Darby Plant | 12509 Adkins Road | Mt. Sterling | 43143 | 9061 | Pickaway | P002 | Natural Gas or number two fuel oil-fired, simple cycle, combustion turbine having a nominal capacity of 1,115.2 MMBTU/hr (80 MW, nominal), controlled with a dry low NOx combustor; CT2 - Combustion Turbine No.2; *Modified | 2004-08-31 | n/a | GE ENERGY MANAGEMENT SYSTEMS |  |  |  |  | 10 | CO - Carbon Monoxide | PASS | NA | Y |  | Yes
2004 | 124 | 0165000132 | AEP Generation Resources Inc., - Darby Plant | 12509 Adkins Road | Mt. Sterling | 43143 | 9061 | Pickaway | P003 | Natural Gas or number two fuel oil-fired, simple cycle, combustion turbine having a nominal capacity of 1,115.2 MMBTU/hr (80 MW, nominal), controlled with a dry low NOx combustor; CT3 - Combustion Turbine No.3; *Modified | 2004-09-01 | n/a | GE ENERGY MANAGEMENT SYSTEMS |  |  |  |  | 10 | CO - Carbon Monoxide | PASS | NA | Y |  | Yes
2004 | 126 | 0165000132 | AEP Generation Resources Inc., - Darby Plant | 12509 Adkins Road | Mt. Sterling | 43143 | 9061 | Pickaway | P004 | Natural Gas or number two fuel oil-fired, simple cycle, combustion turbine having a nominal capacity of 1,115.2 MMBTU/hr (80 MW, nominal), controlled with a dry low NOx combustor; CT4 - Combustion Turbine No.4; *Modified | 2004-09-01 | n/a | GE ENERGY MANAGEMENT SYSTEMS |  |  |  |  | 10 | CO - Carbon Monoxide | PASS | NA | Y |  | Yes
2004 | 128 | 0165000132 | AEP Generation Resources Inc., - Darby Plant | 12509 Adkins Road | Mt. Sterling | 43143 | 9061 | Pickaway | P005 | Natural Gas or number two fuel oil-fired, simple cycle, combustion turbine having a nominal capacity of 1,115.2 MMBTU/hr (80 MW, nominal), controlled with a dry low NOx combustor; CT5 - Combustion Turbine No.5; *Modified | 2004-09-02 | n/a | GE ENERGY MANAGEMENT SYSTEMS |  |  |  |  | 10 | CO - Carbon Monoxide | PASS | NA | Y |  | Yes
2004 | 129 | 0165000132 | AEP Generation Resources Inc., - Darby Plant | 12509 Adkins Road | Mt. Sterling | 43143 | 9061 | Pickaway | P006 | Natural Gas or number two fuel oil-fired, simple cycle, combustion turbine having a nominal capacity of 1,115.2 MMBTU/hr (80 MW, nominal), controlled with a dry low NOx combustor; CT6 - Combustion Turbine No.6; *Modified | 2004-09-02 | n/a | GE ENERGY MANAGEMENT SYSTEMS |  |  |  |  | 10 | CO - Carbon Monoxide | PASS | NA | Y |  | Yes
2005 | 164 | 0165000132 | AEP Generation Resources Inc., - Darby Plant | 12509 Adkins Road | Mt. Sterling | 43143 | 9061 | Pickaway | P002 | Natural Gas or number two fuel oil-fired, simple cycle, combustion turbine having a nominal capacity of 1,115.2 MMBTU/hr (80 MW, nominal), controlled with a dry low NOx combustor; CT2 - Combustion Turbine No.2; *Modified | 2005-08-17 | n/a | GE Energy Management Services, Inc. | n/a | n/a | normal operations | n/a | 10 | CO - Carbon Monoxide | PASS | NA | Y | RATA test passed per 40CFR60 and 40CFR75. | Yes
2005 | 167 | 0165000132 | AEP Generation Resources Inc., - Darby Plant | 12509 Adkins Road | Mt. Sterling | 43143 | 9061 | Pickaway | P004 | Natural Gas or number two fuel oil-fired, simple cycle, combustion turbine having a nominal capacity of 1,115.2 MMBTU/hr (80 MW, nominal), controlled with a dry low NOx combustor; CT4 - Combustion Turbine No.4; *Modified | 2005-08-18 | n/a | GE Energy Management Services, Inc. | n/a | n/a | normal operations | n/a | 10 | CO - Carbon Monoxide | PASS | NA | Y | RATA test passed per 40CFR60 and 40CFR75. | Yes
2005 | 168 | 0165000132 | AEP Generation Resources Inc., - Darby Plant | 12509 Adkins Road | Mt. Sterling | 43143 | 9061 | Pickaway | P005 | Natural Gas or number two fuel oil-fired, simple cycle, combustion turbine having a nominal capacity of 1,115.2 MMBTU/hr (80 MW, nominal), controlled with a dry low NOx combustor; CT5 - Combustion Turbine No.5; *Modified | 2005-08-19 | n/a | GE Energy Management Services, Inc. | n/a | n/a | normal operations | n/a | 10 | CO - Carbon Monoxide | PASS | NA | Y | RATA test passed per 40CFR60 and 40CFR75. | Yes
2005 | 994 | 1409000896 | Duke Energy Indiana, Madison Generating Station | 5657 Kennel Road | Trenton | 45067 |  | Butler | P002 | 84.65 Megawatt (Nominal) Simple-Cycle Combustion Turbine No 2 | 2005-06-14 | control equipment? | GRACE CONSULTING | 80 mw | 10% ra or 5 ppm mean difference | 75 mw | 5.53% ra | other | CO - Carbon Monoxide | PASS | NA | Y | TEST WAS A RATA | Yes
2005 | 995 | 1409000896 | Duke Energy Indiana, Madison Generating Station | 5657 Kennel Road | Trenton | 45067 |  | Butler | P003 | 84.65 Megawatt (Nominal) simple-cycle combustion turbine No. 3 | 2005-06-15 | control equipment? | GRACE CONSULTING | 80 mw | 10% ra co ppm | 76 mw | 6.52% ra co ppm | 10 | CO - Carbon Monoxide | PASS | NA | Y |  | Yes
2005 | 999 | 1409000896 | Duke Energy Indiana, Madison Generating Station | 5657 Kennel Road | Trenton | 45067 |  | Butler | P004 | 84.65 Megawatt (Nominal) simple-cycle combustion turbine No. 4 | 2005-06-15 | control equipment? | GRACE CONSULTING | 80 mw | 10% ra co ppm | 76 mw | 3.08% ra co ppm | 10 | CO - Carbon Monoxide | PASS | NA | Y |  | Yes
2005 | 1088 | 1409000896 | Duke Energy Indiana, Madison Generating Station | 5657 Kennel Road | Trenton | 45067 |  | Butler | P001 | 84.65 Megawatt (Nominal) Simple-Cycle Combustion Turbine No.1 | 2005-06-14 | control equipment? | GRACE CONSULTING | 80 mw | 10% ra or 5 ppm mean difference | 75 mw | 4.17% ra | other | CO - Carbon Monoxide | PASS | NA | Y | TEST WAS A RATA | Yes
2005 | 1091 | 1409000896 | Duke Energy Indiana, Madison Generating Station | 5657 Kennel Road | Trenton | 45067 |  | Butler | P005 | 84.65 Megawatt (Nominal) simple-cycle combustion turbine No. 5 | 2005-06-16 | control equipment? | GRACE CONSULTING | 80 mw | 10% ra co ppm | 79 mw | 4.57% ra co ppm | 10 | CO - Carbon Monoxide | PASS | NA | Y |  | Yes
2005 | 1093 | 1409000896 | Duke Energy Indiana, Madison Generating Station | 5657 Kennel Road | Trenton | 45067 |  | Butler | P006 | 84.65 Megawatt (Nominal) simple-cycle combustion turbine No. 6 | 2005-06-16 | control equipment? | GRACE CONSULTING | 80 mw | 10% ra co ppm | 78 mw | 0.395% ra co ppm | 10 | CO - Carbon Monoxide | PASS | NA | Y |  | Yes
2005 | 1096 | 1409000896 | Duke Energy Indiana, Madison Generating Station | 5657 Kennel Road | Trenton | 45067 |  | Butler | P001 | 84.65 Megawatt (Nominal) Simple-Cycle Combustion Turbine No.1 | 2005-06-17 | control equipment? | GRACE CONSULTING | 80 mw | 10% ra or 5 ppm mean difference | 79 mw | 3.85% | other | CO - Carbon Monoxide | PASS | NA | Y | TEST WAS A RATA | Yes
2005 | 1098 | 1409000896 | Duke Energy Indiana, Madison Generating Station | 5657 Kennel Road | Trenton | 45067 |  | Butler | P007 | 84.65 Megawatt (Nominal) simple-cycle combustion turbine No. 7 | 2005-06-17 | control equipment? | GRACE CONSULTING | 80 mw | 10% ra or 5 ppm mean difference | 79 mw | 6.57% ra | 10 | CO - Carbon Monoxide | PASS | NA | Y | TEST WAS A RATA | Yes
2005 | 1100 | 1409000896 | Duke Energy Indiana, Madison Generating Station | 5657 Kennel Road | Trenton | 45067 |  | Butler | P008 | 84.65 Megawatt (Nominal) simple-cycle combustion turbine No. 8 | 2005-06-17 | control equipment? | GRACE CONSULTING | 80 mw | see memo field | 79 mw | see memo field | other | CO - Carbon Monoxide | PASS | NA | Y | TEST WAS A RATAALLOWABLESNOX (PPM) - RA LESS THAN OR EQUAL TO 20% OR 12 PPM MEAN DIFFERENCENOX (PPM @ 15% O2) - RA LESS THAN OR EQUAL TO 20%NOX (LB/MMBTU) - RA LESS THAN OR EQUAL TO 7.5% OR 0.015 LB/MMBTU MEAN DIFFERENCEACTUAL NOX(PPM) - 4.82% RA NOX (PPM @ 15% O2) - 5.81% RA NOX (LB/MMBTU) - 5.44% RA | Yes
2006 | 197 | 0165000132 | AEP Generation Resources Inc., - Darby Plant | 12509 Adkins Road | Mt. Sterling | 43143 | 9061 | Pickaway | P001 | Natural Gas or number two fuel oil-fired, simple cycle, combustion turbine having a nominal capacity of 1,115.2 MMBTU/hr (80 MW, nominal), controlled with a dry low NOx combustor; CT1 - Combustion Turbine No.1; *Modified | 2006-08-21 | None | Platt Environmental Services, Inc. | 80 MW | 301 lb/hr CO | 76.25 MW | 13 lb/hr CO | 10 | CO - Carbon Monoxide | PASS | NA | Y |  | Yes
2006 | 199 | 0165000132 | AEP Generation Resources Inc., - Darby Plant | 12509 Adkins Road | Mt. Sterling | 43143 | 9061 | Pickaway | P002 | Natural Gas or number two fuel oil-fired, simple cycle, combustion turbine having a nominal capacity of 1,115.2 MMBTU/hr (80 MW, nominal), controlled with a dry low NOx combustor; CT2 - Combustion Turbine No.2; *Modified | 2006-08-21 | None | Platt Environmental Services, Inc. | 80 MW | 301 lb/hr CO | 76.75 MW | 6.2 lb/hr CO | 10 | CO - Carbon Monoxide | PASS | NA | Y |  | Yes
2006 | 204 | 0165000132 | AEP Generation Resources Inc., - Darby Plant | 12509 Adkins Road | Mt. Sterling | 43143 | 9061 | Pickaway | P003 | Natural Gas or number two fuel oil-fired, simple cycle, combustion turbine having a nominal capacity of 1,115.2 MMBTU/hr (80 MW, nominal), controlled with a dry low NOx combustor; CT3 - Combustion Turbine No.3; *Modified | 2006-08-21 | None | Platt Environmental Services, Inc. | 80 MW | 301 lb/hr CO | 76.74 MW | 5.82 lb/hr CO | 10 | CO - Carbon Monoxide | PASS | NA | Y |  | Yes
2006 | 207 | 0165000132 | AEP Generation Resources Inc., - Darby Plant | 12509 Adkins Road | Mt. Sterling | 43143 | 9061 | Pickaway | P004 | Natural Gas or number two fuel oil-fired, simple cycle, combustion turbine having a nominal capacity of 1,115.2 MMBTU/hr (80 MW, nominal), controlled with a dry low NOx combustor; CT4 - Combustion Turbine No.4; *Modified | 2006-08-21 | None | Platt Environmental Services, Inc. | 80 MW | 301 lb/hr CO | 75.5 MW | 3.5 lb/hr CO | 10 | CO - Carbon Monoxide | PASS | NA | Y |  | Yes
2006 | 210 | 0165000132 | AEP Generation Resources Inc., - Darby Plant | 12509 Adkins Road | Mt. Sterling | 43143 | 9061 | Pickaway | P005 | Natural Gas or number two fuel oil-fired, simple cycle, combustion turbine having a nominal capacity of 1,115.2 MMBTU/hr (80 MW, nominal), controlled with a dry low NOx combustor; CT5 - Combustion Turbine No.5; *Modified | 2006-08-21 | None | Platt Environmental Services, Inc. | 80 MW | 301 lb/hr CO | 75.58 MW | 0.7 lb/hr CO | 10 | CO - Carbon Monoxide | PASS | NA | Y |  | Yes
2006 | 213 | 0165000132 | AEP Generation Resources Inc., - Darby Plant | 12509 Adkins Road | Mt. Sterling | 43143 | 9061 | Pickaway | P006 | Natural Gas or number two fuel oil-fired, simple cycle, combustion turbine having a nominal capacity of 1,115.2 MMBTU/hr (80 MW, nominal), controlled with a dry low NOx combustor; CT6 - Combustion Turbine No.6; *Modified | 2006-08-21 | None | Platt Environmental Services, Inc. | 80 MW | 301 lb/hr CO | 73.24 MW | 3.21 lb/hr CO | 10 | CO - Carbon Monoxide | PASS | NA | Y |  | Yes
2011 | 470 | 0335010056 | AMP Napoleon Peaking Plant | 775 Interchange Drive | Napoleon | 43545 |  | Henry | P001 | 16.5 MW NG fired turbine W/SCR | 2011-06-07 | Selective Catalytic Reduction | Grace Consulting, Inc. | 14.4 MW | 0.112 lb CO/MMBtu heat input | 12.2 MW | 0.010 lb CO/MMBtu heat input | 10 | CO - Carbon Monoxide | PASS | NA | N | This was an informal test that was peformed for informational purposes only. The stack did not meet the Method 1 criteria. | Yes
2011 | 471 | 0335010056 | AMP Napoleon Peaking Plant | 775 Interchange Drive | Napoleon | 43545 |  | Henry | P002 | 33 MW NG fired turbine W/SCR | 2011-06-10 | Selective Catalytic Reduction | Grace Consulting, Inc. | 29.9 MW | 0.112 lb CO/MMBtu heat input | 26.3 MW | 0.042 lb CO/MMBtu heat input | 10 | CO - Carbon Monoxide | PASS | NA | N | This was an informal test that was peformed for informational purposes only. The stack did not meet the Method 1 criteria. | Yes
2012 | 162 | 0165000132 | AEP Generation Resources Inc., - Darby Plant | 12509 Adkins Road | Mt. Sterling | 43143 | 9061 | Pickaway | P002 | Natural Gas or number two fuel oil-fired, simple cycle, combustion turbine having a nominal capacity of 1,115.2 MMBTU/hr (80 MW, nominal), controlled with a dry low NOx combustor; CT2 - Combustion Turbine No.2; *Modified | 2012-06-28 | n/a | Mostardi Platt | 80 MW | 301.0 lbs/hour | 58.1 MW | 8.4 lbs/hr | 10 | CO - Carbon Monoxide | PASS | NA | Y |  | Yes
2012 | 165 | 0165000132 | AEP Generation Resources Inc., - Darby Plant | 12509 Adkins Road | Mt. Sterling | 43143 | 9061 | Pickaway | P003 | Natural Gas or number two fuel oil-fired, simple cycle, combustion turbine having a nominal capacity of 1,115.2 MMBTU/hr (80 MW, nominal), controlled with a dry low NOx combustor; CT3 - Combustion Turbine No.3; *Modified | 2012-06-28 | n/a | Mostardi Platt | 80 MW | 301.0 lbs/hour | 58.1 MW | 9.2 lbs/hr | 10 | CO - Carbon Monoxide | PASS | NA | Y |  | Yes
2012 | 168 | 0165000132 | AEP Generation Resources Inc., - Darby Plant | 12509 Adkins Road | Mt. Sterling | 43143 | 9061 | Pickaway | P006 | Natural Gas or number two fuel oil-fired, simple cycle, combustion turbine having a nominal capacity of 1,115.2 MMBTU/hr (80 MW, nominal), controlled with a dry low NOx combustor; CT6 - Combustion Turbine No.6; *Modified | 2012-06-28 | n/a | Mostardi Platt | 80 MW | 301.0 lbs/hour | 58.1 MW | 3.6 lbs/hr | 10 | CO - Carbon Monoxide | PASS | NA | Y |  | Yes
2012 | 210 | 0204010193 | Cristal USA Inc., Ashtabula Complex Plant 2 | 2426 Middle Road | Ashtabula | 44004 |  | Ashtabula | B013 | 65.1 mmBtu/hr (4.92 MW) natural gas-fired combustion turbine with NOx emissions control technology, and a 55.0 mmBtu/hr natural gas-fired duct heater/heat recovery boiler no. 2 | 2012-04-25 | none | Contastoga-Rovers & Associates | 5500 kW | 12.70 #/hr | 2767 kW (50.3% load) | 2.4 #/hr; 15.5 ppmvd | 10 | CO - Carbon Monoxide | PASS | NA | Y |  | Yes
2012 | 213 | 0204010193 | Cristal USA Inc., Ashtabula Complex Plant 2 | 2426 Middle Road | Ashtabula | 44004 |  | Ashtabula | B014 | 65.1 mmBtu/hr (4.92 MW) natural gas-fired combustion turbine with NOx emissions control technology and a 55.0 mmBtu/hr natural gas-fired duct heater/heat recovery boiler no. 3 | 2012-04-25 | none | Contastoga-Rovers & Associates | 5500 kW | 12.70 #/hr | 5301 kW (96% load) | 5.7 #/hr; 37.1 ppmvd | 10 | CO - Carbon Monoxide | PASS | NA | Y |  | Yes
2012 | 218 | 0204010193 | Cristal USA Inc., Ashtabula Complex Plant 2 | 2426 Middle Road | Ashtabula | 44004 |  | Ashtabula | B016 | 65.1 mmBtu/hr natural gas-fired combustion turbine with NOx emissions contorl technology and a 55.0 mmBtu/hr natural gas-fired duct heater/heat recovery boiler no. 5 | 2012-04-25 | none | Contastoga-Rovers & Associates | 5500 kW | 12.70 #/hr | 5304 kW (96.4% load) | 7.3 #/hr; 47.9 ppmvd | 10 | CO - Carbon Monoxide | PASS | NA | Y |  | Yes
2012 | 225 | 0204010193 | Cristal USA Inc., Ashtabula Complex Plant 2 | 2426 Middle Road | Ashtabula | 44004 |  | Ashtabula | B017 | 65.1 mmBtu/hr natural gas-fired turbine with NOx emissions control technology and a heat recovery steam generator no. 1 | 2012-04-25 | Chen low NOx steam injection system | Contastoga-Rovers & Associates | 5500 kW | 8.57 #/hr | 2985 kW (54.3% load) | 2.6 #/hr | 10 | CO - Carbon Monoxide | PASS | NA | Y |  | Yes
2012 | 229 | 0204010193 | Cristal USA Inc., Ashtabula Complex Plant 2 | 2426 Middle Road | Ashtabula | 44004 |  | Ashtabula | B014 | 65.1 mmBtu/hr (4.92 MW) natural gas-fired combustion turbine with NOx emissions control technology and a 55.0 mmBtu/hr natural gas-fired duct heater/heat recovery boiler no. 3 | 2012-04-26 | none | Contastoga-Rovers & Associates | 5500 kW | 12.70 #/hr | 5301 kW (96% load) | 0.7 #/hr; 4.4 ppmvd | 10 | CO - Carbon Monoxide | PASS | NA | Y |  | Yes
2012 | 233 | 0204010193 | Cristal USA Inc., Ashtabula Complex Plant 2 | 2426 Middle Road | Ashtabula | 44004 |  | Ashtabula | B015 | 65.1 mmBtu/hr (4.92 MW) natural gas-fired combustion turbine with NOx emissions control technology and a 55.0 mmBtu/hr natural gas-fired duct heater/heat recovery boiler no. 4 | 2012-04-26 | none | Contastoga-Rovers & Associates | 5500 kW | 12.70 #/hr | 5286 kW (96.1% load) | 4.5 #/hr; 27.5 ppmvd | 10 | CO - Carbon Monoxide | PASS | NA | Y |  | Yes
2012 | 248 | 0204010193 | Cristal USA Inc., Ashtabula Complex Plant 2 | 2426 Middle Road | Ashtabula | 44004 |  | Ashtabula | B013 | 65.1 mmBtu/hr (4.92 MW) natural gas-fired combustion turbine with NOx emissions control technology, and a 55.0 mmBtu/hr natural gas-fired duct heater/heat recovery boiler no. 2 | 2012-04-28 | none | Contastoga-Rovers & Associates | 5500 kW | 12.70 #/hr | 5367 kW (97.6% load) | 4.9 #/hr; 31.7 ppmvd | 10 | CO - Carbon Monoxide | PASS | NA | Y |  | Yes
2012 | 255 | 0204010193 | Cristal USA Inc., Ashtabula Complex Plant 2 | 2426 Middle Road | Ashtabula | 44004 |  | Ashtabula | B015 | 65.1 mmBtu/hr (4.92 MW) natural gas-fired combustion turbine with NOx emissions control technology and a 55.0 mmBtu/hr natural gas-fired duct heater/heat recovery boiler no. 4 | 2012-04-28 | none | Contastoga-Rovers & Associates | 5500 kW | 12.53 #/hr | 2767 kW (50.3% load) | 1.2 #/hr; 7.8 ppmvd | 10 | CO - Carbon Monoxide | PASS | NA | Y |  | Yes
2012 | 259 | 0204010193 | Cristal USA Inc., Ashtabula Complex Plant 2 | 2426 Middle Road | Ashtabula | 44004 |  | Ashtabula | B016 | 65.1 mmBtu/hr natural gas-fired combustion turbine with NOx emissions contorl technology and a 55.0 mmBtu/hr natural gas-fired duct heater/heat recovery boiler no. 5 | 2012-04-28 | none | Contastoga-Rovers & Associates | 5500 kW | 12.70 #/hr | 2930 kW (53.2% load) | 1.0 #/hr; 6.7 ppmvd | 10 | CO - Carbon Monoxide | PASS | NA | Y |  | Yes
2012 | 261 | 0204010193 | Cristal USA Inc., Ashtabula Complex Plant 2 | 2426 Middle Road | Ashtabula | 44004 |  | Ashtabula | B017 | 65.1 mmBtu/hr natural gas-fired turbine with NOx emissions control technology and a heat recovery steam generator no. 1 | 2012-04-28 | Chen low NOx steam injection system | Contastoga-Rovers & Associates | 5500 kW | 8.57 #/hr | 5485 kW (99.7% load) | 0.53 #/hr | 10 | CO - Carbon Monoxide | PASS | NA | Y |  | Yes
2012 | 703 | 0660000247 | Appalachian Power Co, Dresden Plant | 9595 McGlade School Rd | Dresden | 43821 |  | Muskingum | P001 | Turbine No 1 to generate electrical power. | 2012-04-03 | SCR | Mostardi Platt | 171 MW | 49.0 lbs/hr Duct burners on | 170 MW | 2.57 lbs/hr | 10 | CO - Carbon Monoxide | PASS | NA | Y | Emissions limit 13.5 ppmvd @ 15% O2 -- Results 0.5 ppmvd @ 15% O2 | Yes
2012 | 710 | 0660000247 | Appalachian Power Co, Dresden Plant | 9595 McGlade School Rd | Dresden | 43821 |  | Muskingum | P001 | Turbine No 1 to generate electrical power. | 2012-04-04 | SCR | Mostardi Platt | 171 MW | 22.0 lbs/hr Duct burners off | 170 MW | 2.38 lbs/hr | 10 | CO - Carbon Monoxide | PASS | NA | Y | Emissions limit 6 ppmvd @ 15% O2 -- Results 0.6 ppmvd @ 15% O2 | Yes
2012 | 720 | 0660000247 | Appalachian Power Co, Dresden Plant | 9595 McGlade School Rd | Dresden | 43821 |  | Muskingum | P002 | Turbine No 2 to generate electrical power. | 2012-04-05 | SCR | Mostardi Platt | 171 MW | 49.0 lbs/hr Duct burners on | 170 MW | 2.71 lbs/hr | 10 | CO - Carbon Monoxide | PASS | NA | Y | emissions limit 13.5 ppmvd @ 15% O2, - results - 0.6 ppmvd @ 15% O2 | Yes
2012 | 722 | 0660000247 | Appalachian Power Co, Dresden Plant | 9595 McGlade School Rd | Dresden | 43821 |  | Muskingum | P002 | Turbine No 2 to generate electrical power. | 2012-04-06 | SCR | Mostardi Platt | 171 MW | 22.0 lbs/hr Duct burners off | 170 MW | 4.03 lbs/hr | 10 | CO - Carbon Monoxide | PASS | NA | Y | emissions limit 6.0 ppmvd @ 15% O2, - results - 1.1 ppmvd @ 15% O2 | Yes
2012 | 863 | 0744000150 | Hanging Rock Energy Facility | 1395 County Rd 1A | Ironton | 45638 |  | Lawrence | P003 | 172 MW GE 7FA natural gas fired dry low NOx (DLN) combustion turbine No. 3 with duct firing operating in combined cycle mode controlled by Selective Catalytic Reduction (SCR) | 2012-08-22 | scr | Environmental Quality Management, Inc. | 175 MW | 50.3 lbs/hr, 9 ppm(turbine + duct burners) | 229 mw | 0.37 lbs/hr, 0.07 ppm(turbine + duct burner | 10 | CO - Carbon Monoxide | PASS | NA | Y |  | Yes
2012 | 866 | 0744000150 | Hanging Rock Energy Facility | 1395 County Rd 1A | Ironton | 45638 |  | Lawrence | P004 | 172 MW GE 7FA natural gas fired dry low NOx (DLN) combustion turbine No. 4 with duct firing operating in combined cycle mode controlled by Selective Catalytic Reduction (SCR) | 2012-08-22 | scr | Environmental Quality Management, Inc. | 175 MW | 50.3 lbs/hr, 9 ppm(turbine + duct burners) | 232 mw | 0.0 lbs/hr, 0.0 ppm(turbine + duct burner | 10 | CO - Carbon Monoxide | PASS | NA | Y |  | Yes
2012 | 873 | 0744000150 | Hanging Rock Energy Facility | 1395 County Rd 1A | Ironton | 45638 |  | Lawrence | P001 | 172 MW GE 7FA natural gas fired dry low NOx (DLN) combustion turbine No. 1 with duct firing operating in combined cycle mode controlled by Selective Calalytic Reduction (SCR) | 2012-08-23 | scr | Environmental Quality Management, Inc. | 175 MW | 50.3 lbs/hr, 9 ppm(turbine + duct burners) | 228 mw | 0.7 lbs/hr, 0.13 ppm(turbine + duct burner | 10 | CO - Carbon Monoxide | PASS | NA | Y |  | Yes
2012 | 874 | 0744000150 | Hanging Rock Energy Facility | 1395 County Rd 1A | Ironton | 45638 |  | Lawrence | P002 | 172 MW GE 7FA natural gas fired dry low NOx (DLN) combustion turbine No. 2 with duct firing operating in combined cycle mode controlled by Selective Catalytic Reduction (SCR) | 2012-08-23 | scr | Environmental Quality Management, Inc. | 175 MW | 50.3 lbs/hr, 9 ppm(turbine + duct burners) | 231 mw | 5.52 lbs/hr, 1.03 ppm(turbine + duct burner | 10 | CO - Carbon Monoxide | PASS | NA | Y |  | Yes
2012 | 987 | 0857043333 | DP&L Tait Generating Station | 2101 Arbor Boulevard | Moraine | 45439 | 1762 | Montgomery | P005 | 80 MW (1115 mmBtu/hr nominal heat input) natural gas or fuel oil fired simple cycle turbine with water injection controls, CT-1 | 2012-11-13 | CT-1(Other): Max. controlled emission rate = permit limit; CT-2(Other): Max. controlled emission rate = permit limit; CT-3(gas)(Other): Max. controlled emission rate = permit limit | Grace Consulting, Inc. | 80MW; 1115 mmBtu/hr | 1700 lb/hr | 86MW | 41.8 | 10 | CO - Carbon Monoxide | PASS | NA | Y |  | Yes
2012 | 989 | 0857043333 | DP&L Tait Generating Station | 2101 Arbor Boulevard | Moraine | 45439 | 1762 | Montgomery | P006 | 80 MW (1115 mmBtu/hr nominal heat input) natural gas or fuel oil fired simple cycle turbine with water injection controls, CT-2 | 2012-11-13 | CT-1(Other): Max. controlled emission rate = permit limit; CT-2(Other): Max. controlled emission rate = permit limit; CT-3(gas)(Other): Max. controlled emission rate = permit limit | Grace Consulting, Inc. | 80MW; 1115 mmBtu/hr | 1700 lb/hr | 86MW | 58.6 | 10 | CO - Carbon Monoxide | PASS | NA | Y |  | Yes
2012 | 993 | 0857043333 | DP&L Tait Generating Station | 2101 Arbor Boulevard | Moraine | 45439 | 1762 | Montgomery | P007 | 80 MW (1115 mmBtu/hr nominal heat input) natural gas or fuel oil fired simple cycle turbine with water injection and dry low NOx (DLN) combustor controls, CT-3 | 2012-11-13 | CT-1(Other): Max. controlled emission rate = permit limit; CT-2(Other): Max. controlled emission rate = permit limit; CT-3(gas)(Other): Max. controlled emission rate = permit limit | Grace Consulting, Inc. | 80MW; 1115 mmBtu/hr | 301 lb/hr | 85MW | 8.2 | 10 | CO - Carbon Monoxide | PASS | NA | Y |  | Yes
2013 | 976 | 0387020378 | AMP Bowling Green Peaking Plant | 1225 College Drive | Bowling Green | 43402 |  | Wood | P001 | 16.5 WM NG fired turbine W/SCR | 2013-06-18 | SCR-P001(Other): 14 ppmvd @ 15% O2 | Grace Consulting, Inc. | 16.5 MW | 0.112 lb/MMBtu | 16.2 MW | 0.0156 lb/MMBtu | 10 | CO - Carbon Monoxide | PASS | NA | N | The test did not conform to the proper testing methodology because the stack did not meet the Method 1 criteria. This was informal testing performed for informational purposes only. | Yes
2013 | 1349 | 0857043334 | DPL Energy LLC | 2101 Arbor Boulevard | Dayton | 45439 | 1511 | Montgomery | P001 | Natural gas and No. 2 fuel oil fired simple cycle stationary combustion turbine No. 4 - Tait CT4, with a nominal production rating of 80 MW and a nominal heat input of 1115.2 mmBtu/hour, with dry low NOx combustion and water injection controls | 2013-12-03 | Control is within the combustion zone as dry low NOx combustion | Grace Consulting, Inc. | 80 MW | 20 ppmv CO @ 15% O2; 301 lb CO/ hr | 82 MW | 7ppm & 15 lb/hr | 10 | CO - Carbon Monoxide | PASS | NA | N | This was a subpart GG test to determine low mass emission rates. The test was conducted a all 4 loads. The following CO emissions were measured at the load stated: P001 @ 70MW = 5.2 & 10lb/hr, P001 @ 58MW = 4.6 ppm & 8 lb/hr, P001 @ 45MW = 4.5 ppm & 7 lb/hr. P003 @ 70MW = 5.5 ppm & 10 lb/hr, P003 @ 57MW = 3 ppm & 5 lb/hr, P003 @ 45MW = 3 ppm & 4.2 lb/hr. P004 @ 69MW = 2.1 ppm & 4 lb/hr, P004 @ 57MW = 1.5 ppm & 3 lb/hr, P004 @ 45MW = 1.5ppm & 2 lb/hr. | Yes
2013 | 1351 | 0857043334 | DPL Energy LLC | 2101 Arbor Boulevard | Dayton | 45439 | 1511 | Montgomery | P002 | Natural gas and No. 2 fuel oil fired simple cycle stationary combustion turbine No. 5 - Tait CT5, with a nominal production rating of 80 MW and a nominal heat input of 1115.2 mmBtu/hour, with dry low NOx combustion and water injection controls | 2013-12-03 | Control is within the combustion zone as dry low NOx combustion | Grace Consulting, Inc. | 80 MW | 20 ppmv CO @ 15% O2; 301 lb CO/ hr | 81 MW | 12.7 ppm & 27 lb/hr | 10 | CO - Carbon Monoxide | PASS | NA | N | This was a subpart GG test to determine low mass emission rates. The test was conducted a all 4 loads. The following CO emissions were measured at the load stated: P001 @ 70MW = 5.2 & 10lb/hr, P001 @ 58MW = 4.6 ppm & 8 lb/hr, P001 @ 45MW = 4.5 ppm & 7 lb/hr. P003 @ 70MW = 5.5 ppm & 10 lb/hr, P003 @ 57MW = 3 ppm & 5 lb/hr, P003 @ 45MW = 3 ppm & 4.2 lb/hr. P004 @ 69MW = 2.1 ppm & 4 lb/hr, P004 @ 57MW = 1.5 ppm & 3 lb/hr, P004 @ 45MW = 1.5ppm & 2 lb/hr. | Yes
2013 | 1353 | 0857043334 | DPL Energy LLC | 2101 Arbor Boulevard | Dayton | 45439 | 1511 | Montgomery | P003 | Natural gas and No. 2 fuel oil fired simple cycle stationary combustion turbine No. 6 - Tait CT6, with a nominal production rating of 80 MW and a nominal heat input of 1115.2 mmBtu/hour, with dry low NOx combustion and water injection controls | 2013-12-03 | Control is within the combustion zone as dry low NOx combustion | Grace Consulting, Inc. | 80 MW | 20 ppmv CO @ 15% O2; 301 lb CO/ hr | 82 MW | 7ppm & 15 lb/hr | 10 | CO - Carbon Monoxide | PASS | NA | N | This was a subpart GG test to determine low mass emission rates. The test was conducted a all 4 loads. The following CO emissions were measured at the load stated: P001 @ 70MW = 5.2 & 10lb/hr, P001 @ 58MW = 4.6 ppm & 8 lb/hr, P001 @ 45MW = 4.5 ppm & 7 lb/hr. P003 @ 70MW = 5.5 ppm & 10 lb/hr, P003 @ 57MW = 3 ppm & 5 lb/hr, P003 @ 45MW = 3 ppm & 4.2 lb/hr. P004 @ 69MW = 2.1 ppm & 4 lb/hr, P004 @ 57MW = 1.5 ppm & 3 lb/hr, P004 @ 45MW = 1.5ppm & 2 lb/hr. | Yes
2013 | 1357 | 0857043334 | DPL Energy LLC | 2101 Arbor Boulevard | Dayton | 45439 | 1511 | Montgomery | P004 | Natural gas and No. 2 fuel oil fired simple cycle stationary combustion turbine No. 7 - Tait CT7, with a nominal production rating of 80 MW and a nominal heat input of 1115.2 mmBtu/hour, with dry low NOx combustion and water injection controls | 2013-12-03 | Control is within the combustion zone as dry low NOx combustion | Grace Consulting, Inc. | 80 MW | 20 ppmv CO @ 15% O2; 301 lb CO/ hr | 81 MW | 1.5 ppm & 3.2 lb/hr | 10 | CO - Carbon Monoxide | PASS | NA | N | This was a subpart GG test to determine low mass emission rates. The test was conducted a all 4 loads. The following CO emissions were measured at the load stated: P001 @ 70MW = 5.2 & 10lb/hr, P001 @ 58MW = 4.6 ppm & 8 lb/hr, P001 @ 45MW = 4.5 ppm & 7 lb/hr. P003 @ 70MW = 5.5 ppm & 10 lb/hr, P003 @ 57MW = 3 ppm & 5 lb/hr, P003 @ 45MW = 3 ppm & 4.2 lb/hr. P004 @ 69MW = 2.1 ppm & 4 lb/hr, P004 @ 57MW = 1.5 ppm & 3 lb/hr, P004 @ 45MW = 1.5ppm & 2 lb/hr. | Yes
2014 | 84 | 0165000132 | AEP Generation Resources Inc., - Darby Plant | 12509 Adkins Road | Mt. Sterling | 43143 | 9061 | Pickaway | P004 | Natural Gas or number two fuel oil-fired, simple cycle, combustion turbine having a nominal capacity of 1,115.2 MMBTU/hr (80 MW, nominal), controlled with a dry low NOx combustor; CT4 - Combustion Turbine No.4; *Modified | 2014-08-19 | dry low NOx combustor | Mostardi Platt | 80 MW | 301 lb/hr | 41.3, 55.7, 68, &81 MW | 12.86 lb/hr (low) | 10 | CO - Carbon Monoxide | PASS | NA | Y |  | Yes
2014 | 86 | 0165000132 | AEP Generation Resources Inc., - Darby Plant | 12509 Adkins Road | Mt. Sterling | 43143 | 9061 | Pickaway | P005 | Natural Gas or number two fuel oil-fired, simple cycle, combustion turbine having a nominal capacity of 1,115.2 MMBTU/hr (80 MW, nominal), controlled with a dry low NOx combustor; CT5 - Combustion Turbine No.5; *Modified | 2014-08-19 | dry low NOx combustor | Mostardi Platt | 80 MW | 301 lb/hr | 41.3, 55.3, 69, & 80.7 MW | 4.27 lb/hr (low) | 10 | CO - Carbon Monoxide | PASS | NA | Y |  | Yes
2014 | 88 | 0165000132 | AEP Generation Resources Inc., - Darby Plant | 12509 Adkins Road | Mt. Sterling | 43143 | 9061 | Pickaway | P004 | Natural Gas or number two fuel oil-fired, simple cycle, combustion turbine having a nominal capacity of 1,115.2 MMBTU/hr (80 MW, nominal), controlled with a dry low NOx combustor; CT4 - Combustion Turbine No.4; *Modified | 2014-08-20 | dry low NOx combustor | Mostardi Platt | 80 MW | 301 lb/hr | 41.3, 55.7, 68, &81 MW | 12.86 lb/hr (low) | 10 | CO - Carbon Monoxide | PASS | NA | Y |  | Yes
2014 | 89 | 0165000132 | AEP Generation Resources Inc., - Darby Plant | 12509 Adkins Road | Mt. Sterling | 43143 | 9061 | Pickaway | P005 | Natural Gas or number two fuel oil-fired, simple cycle, combustion turbine having a nominal capacity of 1,115.2 MMBTU/hr (80 MW, nominal), controlled with a dry low NOx combustor; CT5 - Combustion Turbine No.5; *Modified | 2014-08-20 | dry low NOx combustor | Mostardi Platt | 80 MW | 301 lb/hr | 41.3, 55.3, 69, & 80.7 MW | 4.27 lb/hr (low) | 10 | CO - Carbon Monoxide | PASS | NA | Y |  | Yes
2014 | 92 | 0165000132 | AEP Generation Resources Inc., - Darby Plant | 12509 Adkins Road | Mt. Sterling | 43143 | 9061 | Pickaway | P001 | Natural Gas or number two fuel oil-fired, simple cycle, combustion turbine having a nominal capacity of 1,115.2 MMBTU/hr (80 MW, nominal), controlled with a dry low NOx combustor; CT1 - Combustion Turbine No.1; *Modified | 2014-08-21 | dry low NOx combustor | Mostardi Platt | 80 MW | 301 lb/hr | 41, 55.3, 68, & 83.3 MW | 21.93 lb/hr (low) | 10 | CO - Carbon Monoxide | PASS | NA | Y |  | Yes
2014 | 94 | 0165000132 | AEP Generation Resources Inc., - Darby Plant | 12509 Adkins Road | Mt. Sterling | 43143 | 9061 | Pickaway | P001 | Natural Gas or number two fuel oil-fired, simple cycle, combustion turbine having a nominal capacity of 1,115.2 MMBTU/hr (80 MW, nominal), controlled with a dry low NOx combustor; CT1 - Combustion Turbine No.1; *Modified | 2014-08-22 | dry low NOx combustor | Mostardi Platt | 80 MW | 301 lb/hr | 41, 55.3, 68, & 83.3 MW | 21.93 lb/hr (low) | 10 | CO - Carbon Monoxide | PASS | NA | Y |  | Yes
2014 | 2176 | 0684000212 | Washington Energy Facility | 859 Ohio 83 | Beverly | 45715 | 1329 | Washington | P001 | 170 MW GE 7FA natural gas fired dry low NOx (DLN) combustion turbine with duct firing operating in combined cycle mode controlled by Selective Catalytic Reduction (SCR)- Modified | 2014-12-02 | SCR #1(Other): 32.3 lb/hr with duct burner firing(24.7 lb/hr w/o) | Mostardi Platt | 170 MW | 45.9 lbs/hr | 181 MW | 4.52 lbs/hr | 6348 03 | CO - Carbon Monoxide | PASS | NA | Y | duct burners on Ammonia allowable- 28.1 lbs/hr emission rate-0.81 lb/hr formaldehyde allowable-0.82 lb/hr emission rate-<0.41 lb/hr | Yes
2014 | 2180 | 0684000212 | Washington Energy Facility | 859 Ohio 83 | Beverly | 45715 | 1329 | Washington | P001 | 170 MW GE 7FA natural gas fired dry low NOx (DLN) combustion turbine with duct firing operating in combined cycle mode controlled by Selective Catalytic Reduction (SCR)- Modified | 2014-12-03 | SCR #1(Other): 32.3 lb/hr with duct burner firing(24.7 lb/hr w/o) | Mostardi Platt | 170 MW | 43.0 lbs/hr | 180 MW | 4.68 lbs/hr | 6348 03 | CO - Carbon Monoxide | PASS | NA | Y | duct burners off ammonia allowable-26.6 lbs/hr emission rate-0.61 lbs/hr formaldehyde allowable-0.8 lb/hr emission rate-<0.41 lb/hr | Yes
2014 | 2181 | 0684000212 | Washington Energy Facility | 859 Ohio 83 | Beverly | 45715 | 1329 | Washington | P002 | 170 MW GE 7FA natural gas fired dry low NOx (DLN) combustion turbine with duct firing operating in combined cycle mode controlled with Selective Catalytic Reduction (SCR)- Modified | 2014-12-04 | SCR #2(Other): 32.3 lb/hr with duct burner firing(24.7 lb/hr w/o) | Mostardi Platt | 170 MW | 45.9 lbs/hr | 186 MW | 3.75 lbs/hr | 6348 03 | CO - Carbon Monoxide | PASS | NA | Y | ammonia allowable-28.1 lbs/hr emission rate-1.39 lbs/hr formaldehyde allowable-0.82 lb/hr emission rate-<0.43 lb/hr duct burners on | Yes
2014 | 2187 | 0684000212 | Washington Energy Facility | 859 Ohio 83 | Beverly | 45715 | 1329 | Washington | P002 | 170 MW GE 7FA natural gas fired dry low NOx (DLN) combustion turbine with duct firing operating in combined cycle mode controlled with Selective Catalytic Reduction (SCR)- Modified | 2014-12-05 | SCR #2(Other): 32.3 lb/hr with duct burner firing(24.7 lb/hr w/o) | Mostardi Platt | 170 MW | 43.0 lbs/hr | 181 MW | 5.14 lbs/hr | 6348 03 | CO - Carbon Monoxide | PASS | NA | Y | duct burners off ammonia allowable-26.6 lbs/hr emission rate-0.73 lb/hr formaldehyde allowable 0.8 lb/hr emission rate-<0.41 lb/hr | Yes
2014 | 2252 | 0819070237 | Buckeye Power Greenville Station | 5119 Sebring Warner Road | Greenville | 45331 |  | Darke | B001 | 269.71 mmBtu/hr natural gas/No. 2 oil, simple cycle combustion turbine with water injection nitrogen oxides reduction system; G1CT1 | 2014-06-09 | WATER INJECTION | Mostardi Platt | 25 MW | 73.5 lb CO/hr | 26 MW | 155 lb CO/hr | 10 | CO - Carbon Monoxide | FAIL | NA | Y | Unit G1CT1Low Mass Emission Test HIGH Load Demonstration: Facility tested to provide data to support it as a Low Mass Emitter per 40 CFR 75.19 and to establish emission rates for NOx and Carbon Monoxide. The water to fuel ratio submitted at 1.14. Heat Input measured 271 mmBtu/hr. Natural gas usage approx. 263730 cf. Actual test date 06/10/2014. This HIGH Load demonstration exceeded the permit allowable. The facility performed another LME late July and August to re-establish the water to fuel ratio while showing passing results. | Yes
2014 | 2253 | 0819070237 | Buckeye Power Greenville Station | 5119 Sebring Warner Road | Greenville | 45331 |  | Darke | B002 | 269.71 mmBtu/hr natural gas/No. 2 oil, simple cycle combustion turbine with water injection nitrogen oxides reduction system; G1CT2 | 2014-06-09 | WATER INJECTION | Mostardi Platt | 25 MW | 73.5 lb CO/hr | 27 MW | 82.9 lb CO/hr | 10 | CO - Carbon Monoxide | FAIL | NA | Y | Unit G1CT2Low Mass Emission Test HIGH Load Demonstration: Facility tested to provide data to support it as a Low Mass Emitter per 40 CFR 75.19 and to establish emission rates for NOx and Carbon Monoxide. The water to fuel ratio submitted at 1.14. Heat Input measured 282 mmBtu/hr. Natural gas usage approx. 274323 cf. Actual test date 06/10/2014. Due to the exceedance of this permit allowable at this operating level, facility repeated LME demonstration to establish new water to fuel operating ration in late July/ early August. | Yes
2014 | 2257 | 0819070237 | Buckeye Power Greenville Station | 5119 Sebring Warner Road | Greenville | 45331 |  | Darke | B001 | 269.71 mmBtu/hr natural gas/No. 2 oil, simple cycle combustion turbine with water injection nitrogen oxides reduction system; G1CT1 | 2014-06-10 | WATER INJECTION | Mostardi Platt | 25 MW | 73.5 lb CO/hr | 11 MW | 44.5 lb CO/hr | 10 | CO - Carbon Monoxide | PASS | NA | Y | Unit G1CT1Low Mass Emission Test LOW Load Demonstration: Facility tested to provide data to support it as a Low Mass Emitter per 40 CFR 75.19 and to establish emission rates for NOx and Carbon Monoxide. The water to fuel ratio submitted at 0.78. Heat Input measured 142 mmBtu/hr. Natural gas usage approx. 137817 cf. | Yes
2014 | 2259 | 0819070237 | Buckeye Power Greenville Station | 5119 Sebring Warner Road | Greenville | 45331 |  | Darke | B002 | 269.71 mmBtu/hr natural gas/No. 2 oil, simple cycle combustion turbine with water injection nitrogen oxides reduction system; G1CT2 | 2014-06-10 | WATER INJECTION | Mostardi Platt | 25 MW | 73.5 lb CO/hr | 13 MW | 37.4 lb CO/hr | 10 | CO - Carbon Monoxide | PASS | NA | Y | Unit G1CT2Low Mass Emission Test LOW Load Demonstration: Facility tested to provide data to support it as a Low Mass Emitter per 40 CFR 75.19 and to establish emission rates for NOx and Carbon Monoxide. The water to fuel ratio submitted at 0.82. Heat Input measured 162 mmBtu/hr. Natural gas usage approx. 157690 cf. | Yes
2014 | 2262 | 0819070237 | Buckeye Power Greenville Station | 5119 Sebring Warner Road | Greenville | 45331 |  | Darke | B001 | 269.71 mmBtu/hr natural gas/No. 2 oil, simple cycle combustion turbine with water injection nitrogen oxides reduction system; G1CT1 | 2014-06-11 | WATER INJECTION | Mostardi Platt | 25 MW | 73.5 lb CO/hr | 17 MW | 53.6 lb CO/hr | 10 | CO - Carbon Monoxide | PASS | NA | Y | Unit G1CT1Low Mass Emission Test LOW/MID Load Demonstration: Facility tested to provide data to support it as a Low Mass Emitter per 40 CFR 75.19 and to establish emission rates for NOx and Carbon Monoxide. The water to fuel ratio submitted at 0.88. Heat Input measured 187 mmBtu/hr. Natural gas usage approx. 182163 cf. Actual test date 06/10/2014. | Yes
2014 | 2265 | 0819070237 | Buckeye Power Greenville Station | 5119 Sebring Warner Road | Greenville | 45331 |  | Darke | B002 | 269.71 mmBtu/hr natural gas/No. 2 oil, simple cycle combustion turbine with water injection nitrogen oxides reduction system; G1CT2 | 2014-06-11 | WATER INJECTION | Mostardi Platt | 25 MW | 73.5 lb CO/hr | 17 MW | 34.5 lb CO/hr | 10 | CO - Carbon Monoxide | PASS | NA | Y | Unit G1CT2Low Mass Emission Test LOW/MID Load Demonstration: Facility tested to provide data to support it as a Low Mass Emitter per 40 CFR 75.19 and to establish emission rates for NOx and Carbon Monoxide. The water to fuel ratio submitted at 0.88. Heat Input measured 200 mmBtu/hr. Natural gas usage approx. 194107 cf. | Yes
2014 | 2268 | 0819070237 | Buckeye Power Greenville Station | 5119 Sebring Warner Road | Greenville | 45331 |  | Darke | B001 | 269.71 mmBtu/hr natural gas/No. 2 oil, simple cycle combustion turbine with water injection nitrogen oxides reduction system; G1CT1 | 2014-06-12 | WATER INJECTION | Mostardi Platt | 25 MW | 73.5 lb CO/hr | 21 MW | 51.8 lb CO/hr | 10 | CO - Carbon Monoxide | PASS | NA | Y | Unit G1CT1Low Mass Emission Test MID/HIGH Load Demonstration: Facility tested to provide data to support it as a Low Mass Emitter per 40 CFR 75.19 and to establish emission rates for NOx and Carbon Monoxide. The water to fuel ratio submitted at 0.92. Heat Input measured 224 mmBtu/hr. Natural gas usage approx. 217363 cf. Actual test date 06/11/2014. | Yes
2014 | 2271 | 0819070237 | Buckeye Power Greenville Station | 5119 Sebring Warner Road | Greenville | 45331 |  | Darke | B002 | 269.71 mmBtu/hr natural gas/No. 2 oil, simple cycle combustion turbine with water injection nitrogen oxides reduction system; G1CT2 | 2014-06-12 | WATER INJECTION | Mostardi Platt | 25 MW | 73.5 lb CO/hr | 17 MW | 34.5 lb CO/hr | 10 | CO - Carbon Monoxide | PASS | NA | Y | Unit G1CT2Low Mass Emission Test MID/HIGH Load Demonstration: Facility tested to provide data to support it as a Low Mass Emitter per 40 CFR 75.19 and to establish emission rates for NOx and Carbon Monoxide. The water to fuel ratio submitted at 0.93. Heat Input measured 240 mmBtu/hr. Natural gas usage approx. 233750 cf. Actual test date 06/11/2014. | Yes
2014 | 2275 | 0819070237 | Buckeye Power Greenville Station | 5119 Sebring Warner Road | Greenville | 45331 |  | Darke | B005 | 269.71 mmBtu/hr natural gas/No. 2 oil, simple cycle combustion turbine with water injection nitrogen oxides reduction system; G3CT1 | 2014-06-12 | WATER INJECTION | Mostardi Platt | 25 MW | 73.5 lb CO/hr | 12 MW | 35.1 lb CO/hr | 10 | CO - Carbon Monoxide | PASS | NA | Y | Unit G3CT1 Low Mass Emission Test LOW Load Demonstration: Facility tested to provide data to support it as a Low Mass Emitter per 40 CFR 75.19 and to establish emission rates for NOx and Carbon Monoxide. The water to fuel ratio submitted at 0.80. Heat Input measured 164 mmBtu/hr. Natural gas usage approx. 159150 cf. | Yes
2014 | 2279 | 0819070237 | Buckeye Power Greenville Station | 5119 Sebring Warner Road | Greenville | 45331 |  | Darke | B005 | 269.71 mmBtu/hr natural gas/No. 2 oil, simple cycle combustion turbine with water injection nitrogen oxides reduction system; G3CT1 | 2014-06-13 | WATER INJECTION | Mostardi Platt | 25 MW | 73.5 lb CO/hr | 17 MW | 73.6 lb CO/hr | 10 | CO - Carbon Monoxide | FAIL | NA | Y | Unit G3CT1 Low Mass Emission Test LOW/MID Load Demonstration: Facility tested to provide data to support it as a Low Mass Emitter per 40 CFR 75.19 and to establish emission rates for NOx and Carbon Monoxide. The water to fuel ratio submitted at 0.97. Heat Input measured 207 mmBtu/hr. Natural gas usage approx. 205217 cf. Due to the exceedance of this permit allowable at this operating level, facility repeated LME demonstration to establish new water to fuel operating ration in late July/ early August. | Yes
2014 | 2281 | 0819070237 | Buckeye Power Greenville Station | 5119 Sebring Warner Road | Greenville | 45331 |  | Darke | B005 | 269.71 mmBtu/hr natural gas/No. 2 oil, simple cycle combustion turbine with water injection nitrogen oxides reduction system; G3CT1 | 2014-06-14 | WATER INJECTION | Mostardi Platt | 25 MW | 73.5 lb CO/hr | 22 MW | 67.4 lb CO/hr | 10 | CO - Carbon Monoxide | PASS | NA | Y | Unit G3CT1 Low Mass Emission Test MID/HIGH Load Demonstration: Facility tested to provide data to support it as a Low Mass Emitter per 40 CFR 75.19 and to establish emission rates for NOx and Carbon Monoxide. The water to fuel ratio submitted at 1.07. Heat Input measured 249 mmBtu/hr. Natural gas usage approx. 242490 cf. Actual test date 06/13/2014. | Yes
2014 | 2284 | 0819070237 | Buckeye Power Greenville Station | 5119 Sebring Warner Road | Greenville | 45331 |  | Darke | B005 | 269.71 mmBtu/hr natural gas/No. 2 oil, simple cycle combustion turbine with water injection nitrogen oxides reduction system; G3CT1 | 2014-06-15 | WATER INJECTION | Mostardi Platt | 25 MW | 73.5 lb CO/hr | 25 MW | 111 lb CO/hr | 10 | CO - Carbon Monoxide | FAIL | NA | Y | Unit G3CT1 Low Mass Emission Test HIGH Load Demonstration: Facility tested to provide data to support it as a Low Mass Emitter per 40 CFR 75.19 and to establish emission rates for NOx and Carbon Monoxide. The water to fuel ratio submitted at 1.14. Heat Input measured 278 mmBtu/hr. Natural gas usage approx. 206709 cf. Actual test date 06/12/2014. Due to the CO exceedance at this operating level, the facility repeated the LME demonstration late July/ early August to establish a new water to fuel operating scenario. | Yes
2014 | 2286 | 0819070237 | Buckeye Power Greenville Station | 5119 Sebring Warner Road | Greenville | 45331 |  | Darke | B001 | 269.71 mmBtu/hr natural gas/No. 2 oil, simple cycle combustion turbine with water injection nitrogen oxides reduction system; G1CT1 | 2014-07-28 | WATER INJECTION | Mostardi Platt | 25 MW | 73.5 lb CO/ hr | 25 MW | 43.5 lb CO/hr | 10 | CO - Carbon Monoxide | PASS | NA | Y | Unit G1CT1 Mass Emission Test High Load Demonstration: Facility tested to provide data to support it as a Low Mass Emitter per 40 CFR 75.19 and to establish emission rates for NOx and Carbon Monoxide. This was a repeated testing effort as first attempt in June showed exceedances of CO emission rates at higher operating levels apparently due to facility calculation error and establishment of wrong water to fuel ratio. The water to fuel ratio submitted at 0.98. Heat Input measured 268 lb/MMbtu. Natural Gas usage approx. 254987 cf. This test was conducted on 07/29/14 but labled 07/28 to allow file savings. | Yes
2014 | 2289 | 0819070237 | Buckeye Power Greenville Station | 5119 Sebring Warner Road | Greenville | 45331 |  | Darke | B002 | 269.71 mmBtu/hr natural gas/No. 2 oil, simple cycle combustion turbine with water injection nitrogen oxides reduction system; G1CT2 | 2014-07-28 | WATER INJECTION | Mostardi Platt | 25 MW | 73.5 lb CO/hr | 22 MW | 29.1 lb CO/hr | 10 | CO - Carbon Monoxide | PASS | NA | Y | Unit G1CT2 Mass Emission Test MID/HIGH Load Demonstration: Facility tested to provide data to support it as a Low Mass Emitter per 40 CFR 75.19 and to establish emission rates for NOx and Carbon Monoxide. This was a repeated testing effort as first attempt in June showed exceedances of CO emission rates at higher operating levels apparently due to facility calculation error and establishment of wrong water to fuel ratio. The water to fuel ratio submitted at 0.97. Heat Input measured 242 lb/MMbtu. Natural Gas usage approx. 230653 cf. Actual test date 07/30/14. | Yes
2014 | 2292 | 0819070237 | Buckeye Power Greenville Station | 5119 Sebring Warner Road | Greenville | 45331 |  | Darke | B001 | 269.71 mmBtu/hr natural gas/No. 2 oil, simple cycle combustion turbine with water injection nitrogen oxides reduction system; G1CT1 | 2014-07-29 | WATER INJECTION | Mostardi Platt | 25 MW | 73.5 lb CO/hr | 11 MW | 45.8 lb CO/hr | 10 | CO - Carbon Monoxide | PASS | NA | Y | Unit G1CT1Low Mass Emission Test Low Load Demonstration: Facility tested to provide data to support it as a Low Mass Emitter per 40 CFR 75.19 and to establish emission rates for NOx and Carbon Monoxide. This was a repeated testing effort as first attempt in June showed exceedances of CO emission rates at higher operating levels apparently due to facility calculation error and establishment of wrong water to fuel ratio. The water to fuel ratio submitted at 0.84. Heat Input measured 146 mmBtu/hr. Natural gas usage approx. 138633 cf. | Yes
2014 | 2295 | 0819070237 | Buckeye Power Greenville Station | 5119 Sebring Warner Road | Greenville | 45331 |  | Darke | B002 | 269.71 mmBtu/hr natural gas/No. 2 oil, simple cycle combustion turbine with water injection nitrogen oxides reduction system; G1CT2 | 2014-07-29 | WATER INJECTION | Mostardi Platt | 25 MW | 75 lb CO/ hr | 13 MW | 38 lb CO/hr | 10 | CO - Carbon Monoxide | PASS | NA | Y | Unit G1CT2 Mass Emission Test LOW Load Demonstration: Facility tested to provide data to support it as a Low Mass Emitter per 40 CFR 75.19 and to establish emission rates for NOx and Carbon Monoxide. This was a repeated testing effort as first attempt in June showed exceedances of CO emission rates at higher operating levels apparently due to facility calculation error and establishment of wrong water to fuel ratio. The water to fuel ratio submitted at 0.88. Heat Input measured 166 lb/MMbtu. Natural Gas usage approx. 158307 cf. | Yes
2014 | 2299 | 0819070237 | Buckeye Power Greenville Station | 5119 Sebring Warner Road | Greenville | 45331 |  | Darke | B001 | 269.71 mmBtu/hr natural gas/No. 2 oil, simple cycle combustion turbine with water injection nitrogen oxides reduction system; G1CT1 | 2014-07-30 | WATER INJECTION | Mostardi Platt | 25 MW | 73.5 lb CO/ hr | 16 MW | 47.0 lb CO/hr | 10 | CO - Carbon Monoxide | PASS | NA | Y | Unit G1CT1 Mass Emission Test LOW/MID Load Demonstration: Facility tested to provide data to support it as a Low Mass Emitter per 40 CFR 75.19 and to establish emission rates for NOx and Carbon Monoxide. This was a repeated testing effort as first attempt in June showed exceedances of CO emission rates at higher operating levels apparently due to facility calculation error and establishment of wrong water to fuel ratio. The water to fuel ratio submitted at 0.91. Heat Input measured 190 lb/MMbtu. Natural Gas usage approx. 180800 cf. | Yes
2014 | 2301 | 0819070237 | Buckeye Power Greenville Station | 5119 Sebring Warner Road | Greenville | 45331 |  | Darke | B002 | 269.71 mmBtu/hr natural gas/No. 2 oil, simple cycle combustion turbine with water injection nitrogen oxides reduction system; G1CT2 | 2014-07-30 | WATER INJECTION | Mostardi Platt | 25 MW | 73.5 lb CO/hr | 18 MW | 34.8 CO/hr | 10 | CO - Carbon Monoxide | PASS | NA | Y | Unit G1CT2 Mass Emission Test LOW/MID Load Demonstration: Facility tested to provide data to support it as a Low Mass Emitter per 40 CFR 75.19 and to establish emission rates for NOx and Carbon Monoxide. This was a repeated testing effort as first attempt in June showed exceedances of CO emission rates at higher operating levels apparently due to facility calculation error and establishment of wrong water to fuel ratio. The water to fuel ratio submitted at 0.90. Heat Input measured 205 lb/MMbtu. Natural Gas usage approx. 195240 cf. | Yes
2014 | 2306 | 0819070237 | Buckeye Power Greenville Station | 5119 Sebring Warner Road | Greenville | 45331 |  | Darke | B005 | 269.71 mmBtu/hr natural gas/No. 2 oil, simple cycle combustion turbine with water injection nitrogen oxides reduction system; G3CT1 | 2014-07-30 | WATER INJECTION | Mostardi Platt | 25 MW | 73.5 lb CO/ hr | 25 MW | 44.4 lb CO/hr | 10 | CO - Carbon Monoxide | PASS | NA | Y | Unit G3CT1 Mass Emission Test HIGH Load Demonstration: Facility tested to provide data to support it as a Low Mass Emitter per 40 CFR 75.19 and to establish emission rates for NOx and Carbon Monoxide. This was a repeated testing effort as first attempt in June showed exceedances of CO emission rates at higher operating levels apparently due to facility calculation error and establishment of wrong water to fuel ratio. The water to fuel ratio submitted at 1.01. Heat Input measured 277 lb/MMbtu. Natural Gas usage approx. 263970 cf. Actual test date 07/31/2014. | Yes
2014 | 2309 | 0819070237 | Buckeye Power Greenville Station | 5119 Sebring Warner Road | Greenville | 45331 |  | Darke | B001 | 269.71 mmBtu/hr natural gas/No. 2 oil, simple cycle combustion turbine with water injection nitrogen oxides reduction system; G1CT1 | 2014-07-31 | WATER INJECTION | Mostardi Platt | 25 MW | 73.5 lb CO/hr | 20 MW | 44.8 lb CO/hr | 10 | CO - Carbon Monoxide | PASS | NA | Y | Unit G1CT1 Mass Emission Test MID/HIGH Load Demonstration: Facility tested to provide data to support it as a Low Mass Emitter per 40 CFR 75.19 and to establish emission rates for NOx and Carbon Monoxide. This was a repeated testing effort as first attempt in June showed exceedances of CO emission rates at higher operating levels apparently due to facility calculation error and establishment of wrong water to fuel ratio. The water to fuel ratio submitted at 0.95. Heat Input measured 222 lb/MMbtu. Natural Gas usage approx. 211117 cf. Actual test date 07/30/2014. | Yes
2014 | 2311 | 0819070237 | Buckeye Power Greenville Station | 5119 Sebring Warner Road | Greenville | 45331 |  | Darke | B002 | 269.71 mmBtu/hr natural gas/No. 2 oil, simple cycle combustion turbine with water injection nitrogen oxides reduction system; G1CT2 | 2014-07-31 | WATER INJECTION | Mostardi Platt | 25 MW | 73.5 lb CO/hr | 27 MW | 30.6 lb CO/hr | 10 | CO - Carbon Monoxide | PASS | NA | Y | Unit G1CT2 Mass Emission Test HIGH Load Demonstration: Facility tested to provide data to support it as a Low Mass Emitter per 40 CFR 75.19 and to establish emission rates for NOx and Carbon Monoxide. This was a repeated testing effort as first attempt in June showed exceedances of CO emission rates at higher operating levels apparently due to facility calculation error and establishment of wrong water to fuel ratio. The water to fuel ratio submitted at 0.99. Heat Input measured 286 lb/MMbtu. Natural Gas usage approx. 272474 cf. Actual test date 07/29/14. | Yes
2014 | 2315 | 0819070237 | Buckeye Power Greenville Station | 5119 Sebring Warner Road | Greenville | 45331 |  | Darke | B005 | 269.71 mmBtu/hr natural gas/No. 2 oil, simple cycle combustion turbine with water injection nitrogen oxides reduction system; G3CT1 | 2014-07-31 | WATER INJECTION | Mostardi Platt | 25 MW | 73.5 lb CO/ hr | 12 MW | 47.4 lb CO/hr | 10 | CO - Carbon Monoxide | PASS | NA | Y | Unit G3CT1 Mass Emission Test LOW Load Demonstration: Facility tested to provide data to support it as a Low Mass Emitter per 40 CFR 75.19 and to establish emission rates for NOx and Carbon Monoxide. This was a repeated testing effort as first attempt in June showed exceedances of CO emission rates at higher operating levels apparently due to facility calculation error and establishment of wrong water to fuel ratio. The water to fuel ratio submitted at 0.90. Heat Input measured 168 lb/MMbtu. Natural Gas usage approx. 159980 cf. | Yes
2014 | 2318 | 0819070237 | Buckeye Power Greenville Station | 5119 Sebring Warner Road | Greenville | 45331 |  | Darke | B005 | 269.71 mmBtu/hr natural gas/No. 2 oil, simple cycle combustion turbine with water injection nitrogen oxides reduction system; G3CT1 | 2014-08-01 | WATER INJECTION | Mostardi Platt | 25 MW | 73.5 lb CO/hr | 16 MW | 54.4 lb CO/hr | 10 | CO - Carbon Monoxide | PASS | NA | Y | Unit G3CT1 Mass Emission Test LOW/MID Load Demonstration: Facility tested to provide data to support it as a Low Mass Emitter per 40 CFR 75.19 and to establish emission rates for NOx and Carbon Monoxide. This was a repeated testing effort as first attempt in June showed exceedances of CO emission rates at higher operating levels apparently due to facility calculation error and establishment of wrong water to fuel ratio. The water to fuel ratio submitted at 0.96. Heat Input measured 203 lb/MMbtu. Natural Gas usage approx. 193097 cf. | Yes
2014 | 2321 | 0819070237 | Buckeye Power Greenville Station | 5119 Sebring Warner Road | Greenville | 45331 |  | Darke | B005 | 269.71 mmBtu/hr natural gas/No. 2 oil, simple cycle combustion turbine with water injection nitrogen oxides reduction system; G3CT1 | 2014-08-02 | WATER INJECTION | Mostardi Platt | 25 MW | 73.5 lb CO/hr | 21 MW | 54.0 lb CO/hr | 10 | CO - Carbon Monoxide | PASS | NA | Y | Unit G3CT1 Mass Emission Test MID/HIGH Load Demonstration: Facility tested to provide data to support it as a Low Mass Emitter per 40 CFR 75.19 and to establish emission rates for NOx and Carbon Monoxide. This was a repeated testing effort as first attempt in June showed exceedances of CO emission rates at higher operating levels apparently due to facility calculation error and establishment of wrong water to fuel ratio. The water to fuel ratio submitted at 1.05. Heat Input measured 246 lb/MMbtu. Natural Gas usage approx. 234293 cf. Actual test date 08/01/2014 | Yes
2014 | 2412 | 0857043333 | DP&L Tait Generating Station | 2101 Arbor Boulevard | Moraine | 45439 | 1762 | Montgomery | P007 | 80 MW (1115 mmBtu/hr nominal heat input) natural gas or fuel oil fired simple cycle turbine with water injection and dry low NOx (DLN) combustor controls, CT-3 | 2014-05-22 | CT-1(Other): Max. controlled emission rate = permit limit; CT-2(Other): Max. controlled emission rate = permit limit; CT-3(gas)(Other): Max. controlled emission rate = permit limit; CT-3(gas)(Other): Max. controlled emission rate = permit limit | Grace Consulting, Inc. | 80MW; 1500 mmbtu/hr | 301 lb CO/hr | 72MW | 1.4lb/hr; 0.93ppmvd | 10 | CO - Carbon Monoxide | PASS | NA | Y | Retest due to maintenance on unit. Facility supplied support to operate this retest at one operating load based on capacity factor. Based on the 0.93ppmvd and calculated using the F-factor, the lb/hr calculates to1.4 lb/hr CO. The Reference temperature averaged at 2032 degrees Fahrenheit. | Yes
2014 | 2417 | 0857043333 | DP&L Tait Generating Station | 2101 Arbor Boulevard | Moraine | 45439 | 1762 | Montgomery | P005 | 80 MW (1115 mmBtu/hr nominal heat input) natural gas or fuel oil fired simple cycle turbine with water injection controls, CT-1 | 2014-12-18 | CT-1(Other): Max. controlled emission rate = permit limit; CT-2(Other): Max. controlled emission rate = permit limit; CT-3(gas)(Other): Max. controlled emission rate = permit limit; CT-3(gas)(Other): Max. controlled emission rate = permit limit | Grace Consulting, Inc. | 80MW; 1115mmBtu/hr | 1700 lb/hr | 86MW | 42lb/hr | 10 | CO - Carbon Monoxide | PASS | NA | Y | Another LME retest due to the installation of a new water injection system. The requirement then being to re-establish the water to fuel ratio. This test was run at the same load as the initial December 2012 tests. | Yes
2015 | 975 | 0684015015 | DTE Marietta | 17005 State Route 7 | Marietta | 45750 |  | Washington | P001 | 8 MW Turbine and heat recovery steam generator (HRSG) - Natural Gas | 2015-03-02 | SCR(NOx Reduction Technology): Selective Catalytic Reduction (SCR) | Montrose Environmental Group | 83.3 mm btu/hr | 25.0 ppm | 75 mm btu/hr 91% steam load | 0.8 ppm | 10 | CO - Carbon Monoxide | PP | NA | Y | turbine and HRSG combined | Yes
2015 | 976 | 0684015015 | DTE Marietta | 17005 State Route 7 | Marietta | 45750 |  | Washington | P001 | 8 MW Turbine and heat recovery steam generator (HRSG) - Natural Gas | 2015-03-03 | SCR(NOx Reduction Technology): Selective Catalytic Reduction (SCR) | MontroseEnvironmental Group | 83.3 lb/mm btu | 25.0 ppm | 80 mm btu/hr | 1.79 ppm | 10 | CO - Carbon Monoxide | PP | NA | Y |  | Yes
2015 | 978 | 0684015015 | DTE Marietta | 17005 State Route 7 | Marietta | 45750 |  | Washington | P001 | 8 MW Turbine and heat recovery steam generator (HRSG) - Natural Gas | 2015-05-05 | SCR(NOx Reduction Technology): Selective Catalytic Reduction (SCR) | Montrose Environmental Group | 130 mm btu/hr | none | 112 mm btu/hr | 312.8 lb/mm scf | 10 | CO - Carbon Monoxide | PP | NA | Y | HRSG only | Yes
2015 | 1390 | 1667040085 | Kent State University Heating Plant | P.O. Box 5190 | Kent | 44242 | 0001 | Portage | B010 | Combustion Turbine CT 2 | 2015-01-15 | none | Air Compliance Testing, Inc. | 7 MW | 0.13 lb/mmBtu | 7 MW | 0.0059 lb/mmBtu | 10 | CO - Carbon Monoxide | PP | NA | Y |  | Yes
2016 | 990 | 0381000043 | Robert P. Mone Plant | 4406 Mentzer Road | Convoy | 45832 |  | Van Wert | P001 | GE-7FA simple cycle combustion turbine | 2016-02-02 | Low NOx burners/water injection system | Mostardi Platt | 180 MW | 72.0 lbs/hr | 188.7 MW | 3.33 lbs/jhr | 10 | CO - Carbon Monoxide | PP | Y | NA | Fuel was no. 2 oil/distillate oil | Yes
2016 | 993 | 0381000043 | Robert P. Mone Plant | 4406 Mentzer Road | Convoy | 45832 |  | Van Wert | P002 | GE-7FA simple cycle combustion turbine | 2016-02-03 | Low NOx burners/water injection system | Mostardi Platt | 178 MW | 72.0 lbs/hr | 185 MW | 1.81 lb/hr | 10 | CO - Carbon Monoxide | PP | Y | NA | Fuel was No. 2 oil/distillate oil | Yes
2016 | 996 | 0381000043 | Robert P. Mone Plant | 4406 Mentzer Road | Convoy | 45832 |  | Van Wert | P003 | GE-7FA simple cycle combustion turbine | 2016-02-04 | Low NOx burners/water injection system | Mostardi Platt | 189 MW | 72.0 lbs/hr | 196 MW | 2.03 lbs/hr | 10 | CO - Carbon Monoxide | PP | Y | NA | Fuel was No. 2 oil/distillate oil. | Yes
2016 | 1769 | 0684000212 | Washington Energy Facility | 859 Ohio 83 | Beverly | 45715 | 1329 | Washington | P001 | Nominally Rated 207 MW GE 7FA - Natural-Gas Fired Dry Low NOx (DLN) Combustion Turbine with duct firing operating in combined cycle mode controlled by Selective Catalytic Reduction (SCR) | 2016-06-29 | SCR #1(Other): 32.3 lb/hr with duct burner firing(24.7 lb/hr w/o); SCR #2(Other): 32.3 lb/hr with duct burner firing(24.7 lb/hr w/o) | Mostardi Platt | 207 MW | 45.9 lbs/hr burners on 43.0 lbs/hr burners off | 187 MW | 1.32 lbs/hr 0.8 lb/hr | 10 | CO - Carbon Monoxide | PP | Y | NA |  | Yes
2016 | 1770 | 0684000212 | Washington Energy Facility | 859 Ohio 83 | Beverly | 45715 | 1329 | Washington | P002 | Nominally Rated 207 MW GE 7FA - Natural-Gas Fired Dry Low NOx (DLN) Combustion Turbine with duct firing operating in combined cycle mode controlled by Selective Catalytic Reduction (SCR) | 2016-06-29 | SCR #1(Other): 32.3 lb/hr with duct burner firing(24.7 lb/hr w/o); SCR #2(Other): 32.3 lb/hr with duct burner firing(24.7 lb/hr w/o) | Mostardi Platt | 207 MW | 45.9 lbs/hr burners on 43.0 lbs/hr burners off | 185 MW 186 MW | 1.0 lb/hr 1.32 lbs/hr | 10 | CO - Carbon Monoxide | PP | Y | NA |  | Yes
2016 | 328 | 0165000132 | AEP Generation Resources Inc., - Darby Plant | 12509 Adkins Road | Mt. Sterling | 43143 | 9061 | Pickaway | P001 | Natural Gas or number two fuel oil-fired, simple cycle, combustion turbine having a nominal capacity of 1,115.2 MMBTU/hr (80 MW, nominal), controlled with a dry low NOx combustor; CT1 - Combustion Turbine No.1; *Modified | 2016-12-14 | PCT1(Other): Water Injection for NOx reduction during periods when distillate oil is used as fuel.; PCT2(Other): Water Injection for NOx reduction during periods when distillate oil is used as fuel; PCT3(Other): Water injection for NOx reduction during pe | Mostardi Platt | 80 MW, nominal | 1,093 lb/hr while burning No. 2 fuel oil | 92 MWe | 5.8 lb/hr | 10 | CO - Carbon Monoxide | PP | Y | NA | This test was conducted to establish fuel-and-unit specific CO emissions rates while burning No. 2 fuel oil in accordance with the low mass emissions unit provisions in 40 CFR 75.19. Emissions units P001, P002, P003, and P004 are identical units and qua | Yes
2016 | 329 | 0165000132 | AEP Generation Resources Inc., - Darby Plant | 12509 Adkins Road | Mt. Sterling | 43143 | 9061 | Pickaway | P002 | Natural Gas or number two fuel oil-fired, simple cycle, combustion turbine having a nominal capacity of 1,115.2 MMBTU/hr (80 MW, nominal), controlled with a dry low NOx combustor; CT2 - Combustion Turbine No.2; *Modified | 2016-12-14 | PCT1(Other): Water Injection for NOx reduction during periods when distillate oil is used as fuel.; PCT2(Other): Water Injection for NOx reduction during periods when distillate oil is used as fuel; PCT3(Other): Water injection for NOx reduction during pe | Mostardi Platt | 80 MW, nominal | 1,093 lb/hr while burning No. 2 fuel oil | 92 MWe | 6.7 lb/hr | 10 | CO - Carbon Monoxide | PP | Y | NA | This test was conducted to establish fuel-and-unit specific CO emissions rates while burning No. 2 fuel oil in accordance with the low mass emissions unit provisions in 40 CFR 75.19. Emissions units P001, P002, P003, and P004 are identical units and qua | Yes
2016 | 330 | 0165000132 | AEP Generation Resources Inc., - Darby Plant | 12509 Adkins Road | Mt. Sterling | 43143 | 9061 | Pickaway | P003 | Natural Gas or number two fuel oil-fired, simple cycle, combustion turbine having a nominal capacity of 1,115.2 MMBTU/hr (80 MW, nominal), controlled with a dry low NOx combustor; CT3 - Combustion Turbine No.3; *Modified | 2016-12-14 | PCT1(Other): Water Injection for NOx reduction during periods when distillate oil is used as fuel.; PCT2(Other): Water Injection for NOx reduction during periods when distillate oil is used as fuel; PCT3(Other): Water injection for NOx reduction during pe | Mostardi Platt | 80 MW, nominal | 1,093 lb/hr while burning No. 2 fuel oil | 98 MWe | 6.4 lb/hr | 10 | CO - Carbon Monoxide | PP | Y | NA | This test was conducted to establish fuel-and-unit specific CO emissions rates while burning No. 2 fuel oil in accordance with the low mass emissions unit provisions in 40 CFR 75.19. Emissions units P001, P002, P003, and P004 are identical units and qua | Yes
2016 | 331 | 0165000132 | AEP Generation Resources Inc., - Darby Plant | 12509 Adkins Road | Mt. Sterling | 43143 | 9061 | Pickaway | P004 | Natural Gas or number two fuel oil-fired, simple cycle, combustion turbine having a nominal capacity of 1,115.2 MMBTU/hr (80 MW, nominal), controlled with a dry low NOx combustor; CT4 - Combustion Turbine No.4; *Modified | 2016-12-14 | PCT1(Other): Water Injection for NOx reduction during periods when distillate oil is used as fuel.; PCT2(Other): Water Injection for NOx reduction during periods when distillate oil is used as fuel; PCT3(Other): Water injection for NOx reduction during pe | Mostardi Platt | 80 MW, nominal | 1,093 lb/hr while burning No. 2 fuel oil | 93 MWe | 6.3 lb/hr | 10 | CO - Carbon Monoxide | PP | Y | NA | This test was conducted to establish fuel-and-unit specific CO emissions rates while burning No. 2 fuel oil in accordance with the low mass emissions unit provisions in 40 CFR 75.19. Emissions units P001, P002, P003, and P004 are identical units and qua | Yes
2016 | 338 | 0165000132 | AEP Generation Resources Inc., - Darby Plant | 12509 Adkins Road | Mt. Sterling | 43143 | 9061 | Pickaway | P005 | Natural Gas or number two fuel oil-fired, simple cycle, combustion turbine having a nominal capacity of 1,115.2 MMBTU/hr (80 MW, nominal), controlled with a dry low NOx combustor; CT5 - Combustion Turbine No.5; *Modified | 2016-12-14 | PCT5(Other): Water injection for NOx reduction during periods when distillate oil is used as fuel.; PCT6(Other): Water injection for NOx reduction during periods when distillate oil is used for fuel. | Mostardi Platt | 80 MW, nominal | 1,093 lb/hr | 98 MWe | 2.0 lb/hr | 10 | CO - Carbon Monoxide | PP | Y | NA | This test was conducted to establish fuel-and-unit specific CO emissions rates while burning No. 2 fuel oil in accordance with the low mass emissions unit provisions in 40 CFR 75.19. Emissions units P005 and P006 are identical units and qualify for sing | Yes
2016 | 339 | 0165000132 | AEP Generation Resources Inc., - Darby Plant | 12509 Adkins Road | Mt. Sterling | 43143 | 9061 | Pickaway | P006 | Natural Gas or number two fuel oil-fired, simple cycle, combustion turbine having a nominal capacity of 1,115.2 MMBTU/hr (80 MW, nominal), controlled with a dry low NOx combustor; CT6 - Combustion Turbine No.6; *Modified | 2016-12-14 | PCT5(Other): Water injection for NOx reduction during periods when distillate oil is used as fuel.; PCT6(Other): Water injection for NOx reduction during periods when distillate oil is used for fuel. | Mostardi Platt | 80 MW, nominal | 1,093 lb/hr | 98 MWe | 3.9 lb/hr | 10 | CO - Carbon Monoxide | PP | Y | NA | This test was conducted to establish fuel-and-unit specific CO emissions rates while burning No. 2 fuel oil in accordance with the low mass emissions unit provisions in 40 CFR 75.19. Emissions units P005 and P006 are identical units and qualify for sing | Yes
2016 | 1926 | 0857043334 | AES Ohio Generation, LLC | 2101 Arbor Boulevard | Dayton | 45439 | 1511 | Montgomery | P003 | Natural gas and No. 2 fuel oil fired simple cycle stationary combustion turbine No. 6 - Tait CT6, with a nominal production rating of 80 MW and a nominal heat input of 1115.2 mmBtu/hour, with dry low NOx combustion and water injection controls | 2016-10-27 | Control is within the combustion zone as dry low NOx combustion | Mostardi Platt | 80 MW | 20 ppmv CO @ 15% O2; 800 lb CO/ hr | 85 MW | 1.5ppm & 3.47 lb/hr | 10 | CO - Carbon Monoxide | PP | Y | NA | This test was designed to show compliance with permit allowables using #2 fuel oil. | Yes
2016 | 1932 | 0857043334 | AES Ohio Generation, LLC | 2101 Arbor Boulevard | Dayton | 45439 | 1511 | Montgomery | P003 | Natural gas and No. 2 fuel oil fired simple cycle stationary combustion turbine No. 6 - Tait CT6, with a nominal production rating of 80 MW and a nominal heat input of 1115.2 mmBtu/hour, with dry low NOx combustion and water injection controls | 2016-10-31 | Control is within the combustion zone as dry low NOx combustion | Mostardi Platt | 80 MW | 20ppm@15%O2; 800 lb/hr | 84MW | 1ppm@15%O2; 3 lb/hr | 10 | CO - Carbon Monoxide | PP | Y | NA | This test was designed to show compliance with permit allowables using diesel fuel. This part of the water injection testing devised to determine water to fuel operating ratios at different operating loads. At 40 MW, 1ppm; 1.2 lb/hr. At 60 MW, 1 ppm@15 | Yes
2016 | 1937 | 0857043334 | AES Ohio Generation, LLC | 2101 Arbor Boulevard | Dayton | 45439 | 1511 | Montgomery | P001 | Natural gas and No. 2 fuel oil fired simple cycle stationary combustion turbine No. 4 - Tait CT4, with a nominal production rating of 80 MW and a nominal heat input of 1115.2 mmBtu/hour, with dry low NOx combustion and water injection controls | 2016-11-22 | Control is within the combustion zone as dry low NOx combustion | Mostardi Platt | 80 MW | 20 ppmvd @ 15%O2; 800 lb CO/hr | 76 MW | 1 ppmvd@15%O2; 1.2 lb/hr | 10 | CO - Carbon Monoxide | PP | Y | NA | This test was designed to show compliance with permit allowables using #2 fuel oil and at base load. | Yes
2016 | 1938 | 0857043334 | AES Ohio Generation, LLC | 2101 Arbor Boulevard | Dayton | 45439 | 1511 | Montgomery | P002 | Natural gas and No. 2 fuel oil fired simple cycle stationary combustion turbine No. 5 - Tait CT5, with a nominal production rating of 80 MW and a nominal heat input of 1115.2 mmBtu/hour, with dry low NOx combustion and water injection controls | 2016-11-22 | Control is within the combustion zone as dry low NOx combustion | Mostardi Platt | 80 MW | 20 ppmvd @ 15%O2; 800 lb CO/hr | 80 MW | 1 ppmvd@15%; 2.6 lb/hr | 10 | CO - Carbon Monoxide | PP | Y | NA | This test was designed to show compliance with permit allowables using #2 fuel oil and at base load. | Yes
2016 | 1939 | 0857043334 | AES Ohio Generation, LLC | 2101 Arbor Boulevard | Dayton | 45439 | 1511 | Montgomery | P004 | Natural gas and No. 2 fuel oil fired simple cycle stationary combustion turbine No. 7 - Tait CT7, with a nominal production rating of 80 MW and a nominal heat input of 1115.2 mmBtu/hour, with dry low NOx combustion and water injection controls | 2016-11-22 | Control is within the combustion zone as dry low NOx combustion | Mostardi Platt | 80 MW | 20 ppmvd @ 15%O2; 800 lb CO/hr | 83 MW | 1 ppmvd@15% O2; 1.7 lb/hr | 10 | CO - Carbon Monoxide | PP | Y | NA | This test was designed to show compliance with permit allowables using #2 fuel oil and at base load. | Yes
2016 | 1952 | 0857043334 | AES Ohio Generation, LLC | 2101 Arbor Boulevard | Dayton | 45439 | 1511 | Montgomery | P002 | Natural gas and No. 2 fuel oil fired simple cycle stationary combustion turbine No. 5 - Tait CT5, with a nominal production rating of 80 MW and a nominal heat input of 1115.2 mmBtu/hour, with dry low NOx combustion and water injection controls | 2016-11-03 | Control is within the combustion zone as dry low NOx combustion | Mostardi Platt | 80 MW | 20ppmvd@15%O2; 800lb/hr CO | 79 MW | 1.0PPMVD@15%o2; 1.8 lb/hr CO | 10 | CO - Carbon Monoxide | PP | Y | NA | This test was designed to show compliance with permit allowables using diesel fuel. This part of the WATER INJECTION testing devised to determine water to fuel operating ratios at different operating loads. At 40 MW, 1 ppm; 1.5 lb/hr. At 60 MW, 1 ppm@1 | Yes
2016 | 1955 | 0857043334 | AES Ohio Generation, LLC | 2101 Arbor Boulevard | Dayton | 45439 | 1511 | Montgomery | P001 | Natural gas and No. 2 fuel oil fired simple cycle stationary combustion turbine No. 4 - Tait CT4, with a nominal production rating of 80 MW and a nominal heat input of 1115.2 mmBtu/hour, with dry low NOx combustion and water injection controls | 2016-11-02 | Control is within the combustion zone as dry low NOx combustion | Mostardi Platt | 80 MW | 20ppmvd@15%O2; 800 lb/hr | 76 MW | 0.4ppmvd@15%O2; 1 lb/hr | 10 | CO - Carbon Monoxide | PP | Y | NA | This test was designed to show compliance with permit allowables using diesel fuel. This part of the WATER INJECTION testing devised to determine water to fuel operating ratios at different operating loads. At 40 MW, 1 ppm; 1.2 lb/hr. At 60 MW, 1 ppm@1 | Yes
2016 | 1956 | 0857043334 | AES Ohio Generation, LLC | 2101 Arbor Boulevard | Dayton | 45439 | 1511 | Montgomery | P004 | Natural gas and No. 2 fuel oil fired simple cycle stationary combustion turbine No. 7 - Tait CT7, with a nominal production rating of 80 MW and a nominal heat input of 1115.2 mmBtu/hour, with dry low NOx combustion and water injection controls | 2016-11-05 | Control is within the combustion zone as dry low NOx combustion | Mostardi Platt | 80 MW | 20ppmvd@15%O2; 800 lb/hr | 83 MW | 1ppmvd@15%O2;1.6lb/hr | 10 | CO - Carbon Monoxide | PP | Y | NA | This test was designed to show compliance with permit allowables using diesel fuel. This part of the WATER INJECTION testing devised to determine water to fuel operating ratios at different operating loads. At 40 MW, 1 ppm; 1.0 lb/hr. At 60 MW, 1 ppm@1 | Yes
2005 | 550 | 0387000377 | Troy Energy, LLC | 22379 Pemberville Road | Luckey | 43443 |  | Wood | P001 | 1,570 mmBTU/hr combustion turbine | 2005-07-13 | none | TRC ENVIRONMENTAL CORPORATION | 1749.5 mmbtu/hr | 32.0 lbs/hr; 0.018 lbs/mmbtu | 1617 mmbtu/hr | 2.2 lbs/hr; 0.001 lbs/mmbtu | 10 | CO - Carbon Monoxide | PASS | NA | Y | Generator fuel was natural gas.
2005 | 554 | 0387000377 | Troy Energy, LLC | 22379 Pemberville Road | Luckey | 43443 |  | Wood | P001 | 1,570 mmBTU/hr combustion turbine | 2005-07-14 | none | TRC ENVIRONMENTAL CORPORATION | 1988.7 mmbtu/hr | 72.0 lbs/hr; 0.036 lbs/mmbtu | 1749.21 mmbtu/hr | 2.90 lbs/hr; 0.002 lbs/mmbtu | 10 | CO - Carbon Monoxide | PASS | NA | Y | Generator fuel was fuel oil.
2005 | 556 | 0387000377 | Troy Energy, LLC | 22379 Pemberville Road | Luckey | 43443 |  | Wood | P002 | 1,570 mmBTU/hr combustion turbine | 2005-07-15 | none | TRC ENVIRONMENTAL CORPORATION | 1749.5 mmbtu/hr | 32.0 lbs/hr; 0.018 lbs/mmbtu | 1597 mmbtu/hr | 1.3 lbs/hr; 0.0008 lbs/mmbtu | 10 | CO - Carbon Monoxide | PASS | NA | Y | Generator fuel was natural gas.
2005 | 560 | 0387000377 | Troy Energy, LLC | 22379 Pemberville Road | Luckey | 43443 |  | Wood | P002 | 1,570 mmBTU/hr combustion turbine | 2005-07-18 | none | TRC ENVIRONMENTAL CORPORATION | 1988.7 mmbtu/hr | 72.0 lbs/hr; 0.036 lbs/mmbtu | 1929.4 mmbtu/hr | 2.5 lbs/hr; 0.001 lbs/mmbtu | 10 | CO - Carbon Monoxide | PASS | NA | Y | Generator fuel was fuel oil.
2005 | 564 | 0387000377 | Troy Energy, LLC | 22379 Pemberville Road | Luckey | 43443 |  | Wood | P003 | 1,570 mmBTU/hr combustion turbine | 2005-07-19 | none | TRC ENVIRONMENTAL CORPORATION | 1988.7 mmbtu/hr | 72.0 lbs/hr; 0.036 lbs/mmbtu | 1941.77 mmbtu/hr | 3.71 lbs/hr; 0.002 lbs/mmbtu | 10 | CO - Carbon Monoxide | PASS | NA | Y | Generator fuel was fuel oil.
2005 | 569 | 0387000377 | Troy Energy, LLC | 22379 Pemberville Road | Luckey | 43443 |  | Wood | P003 | 1,570 mmBTU/hr combustion turbine | 2005-07-20 | none | TRC ENVIRONMENTAL CORPORATION | 1749.5 mmbtu/hr | 32.0 lbs/hr; 0.018 lbs/mmbtu | 1633.7 mmbtu/hr | 3.5 lbs/hr; 0.002 lbs/mmbtu | 10 | CO - Carbon Monoxide | PASS | NA | Y | Generator fuel was natural gas.
2005 | 575 | 0387000377 | Troy Energy, LLC | 22379 Pemberville Road | Luckey | 43443 |  | Wood | P004 | 1,570 mmBTU/hr combustion turbine | 2005-07-21 | none | TRC ENVIRONMENTAL CORPORATION | 1749.5 mmbtu/hr | 32.0 lbs/hr; 0.018 lbs/mmbtu | 1625.1 mmbtu/hr | 1.1 lbs/hr; 0.001 lbs/mmbtu | 10 | CO - Carbon Monoxide | PASS | NA | Y | Generator fuel was natural gas.
2005 | 579 | 0387000377 | Troy Energy, LLC | 22379 Pemberville Road | Luckey | 43443 |  | Wood | P004 | 1,570 mmBTU/hr combustion turbine | 2005-07-22 | none | TRC ENVIRONMENTAL CORPORATION | 1988.7 mmbtu/hr | 72.0 lbs/hr; 0.036 lbs/mmbtu | 1790.1 mmbtu/hr | 1.94 lbs/hr; 0.0011 lbs/mmbtu | 10 | CO - Carbon Monoxide | PASS | NA | Y | Generator fuel was fuel oil.
2004 | 1157 | 1431070849 | University of Cincinnati | Clifton Campus | Cincinnati | 45221 |  | Hamilton | P003 | 13.5 MW Natural Gas/ No. 2 Fuel Oil-fired Turbines with 98.5 mmBtu/hr duct burner | 2004-05-28 | control equipment? | RMC | 14.5mw/hr | 1.97 lb/hr | 12 mw/hr | 0.0lb/hr | 10 | CO - Carbon Monoxide | PASS | Y | Y |  | Yes
2004 | 1158 | 1431070849 | University of Cincinnati | Clifton Campus | Cincinnati | 45221 |  | Hamilton | P004 | 13.5 MW Natural Gas/ No. 2 Fuel Oil-fired Turbines with 98.5 mmBtu/hr duct burner | 2004-05-28 | cat | RMC | 14.5mw/hr | 1.97 lb/hr | 12 mw/hr | .37 lb/hr | 10 | CO - Carbon Monoxide | PASS | Y | Y |  | Yes
2005 | 1204 | 1431070849 | University of Cincinnati | Clifton Campus | Cincinnati | 45221 |  | Hamilton | P004 | 13.5 MW Natural Gas/ No. 2 Fuel Oil-fired Turbines with 98.5 mmBtu/hr duct burner | 2005-05-18 | control equipment? | RMC |  |  |  |  | 7 | CO - Carbon Monoxide | PASS | Y | Y |  | Yes
2005 | 1209 | 1431070849 | University of Cincinnati | Clifton Campus | Cincinnati | 45221 |  | Hamilton | P003 | 13.5 MW Natural Gas/ No. 2 Fuel Oil-fired Turbines with 98.5 mmBtu/hr duct burner | 2005-11-30 | HRSG & DUCT BURNERS | RMC | 12 MW | <5 PPM MEAN DIFF | 11 MW | 0.73 PPM MEAN DIFF | 10 | CO - Carbon Monoxide | PASS | NA | Y |  | Yes
2005 | 1211 | 1431070849 | University of Cincinnati | Clifton Campus | Cincinnati | 45221 |  | Hamilton | P004 | 13.5 MW Natural Gas/ No. 2 Fuel Oil-fired Turbines with 98.5 mmBtu/hr duct burner | 2005-11-30 | HRSG & DUCT BURNERS | RMC | 12 MW | <5 PPM MEAN DIFF | 12 MW | 1.27 PPM MEAN DIFF | 10 | CO - Carbon Monoxide | PASS | NA | Y |  | Yes
2006 | 1409 | 1431070849 | University of Cincinnati | Clifton Campus | Cincinnati | 45221 |  | Hamilton | P003 | 13.5 MW Natural Gas/ No. 2 Fuel Oil-fired Turbines with 98.5 mmBtu/hr duct burner | 2006-11-15 | HRSG & DUCT BURNERS | RMC | 12 MW | <5 PPM MEAN DIFF | 12 MW | 1.21 PPM MEAN DIFF | 10 | CO - Carbon Monoxide | PASS | NA | Y |  | Yes
2006 | 1411 | 1431070849 | University of Cincinnati | Clifton Campus | Cincinnati | 45221 |  | Hamilton | P004 | 13.5 MW Natural Gas/ No. 2 Fuel Oil-fired Turbines with 98.5 mmBtu/hr duct burner | 2006-11-15 | HRSG & DUCT BURNERS | RMC | 12 MW | <5 PPM MEAN DIFF | 12 MW | 1.26 PPM MEAN DIFF | 10 | CO - Carbon Monoxide | PASS | NA | Y |  | Yes
2007 | 1617 | 1431070849 | University of Cincinnati | Clifton Campus | Cincinnati | 45221 |  | Hamilton | P004 | 13.5 MW Natural Gas/ No. 2 Fuel Oil-fired Turbines with 98.5 mmBtu/hr duct burner | 2007-07-20 | CO CATALYST | RMC ENVIRONMENTAL | 132.1 MMBTU/HR | 1.97 LB/HR W/O DUCT BURNER; 89% DE | 138.8 MMBTU/HR | 0.46 LB/HR; 89.8% DE | 10 | CO - Carbon Monoxide | PASS | NA | Y | CO CATALYST TEMPERATURE DURING TESTING WAS 490 DEG F. | Yes
2007 | 1618 | 1431070849 | University of Cincinnati | Clifton Campus | Cincinnati | 45221 |  | Hamilton | P003 | 13.5 MW Natural Gas/ No. 2 Fuel Oil-fired Turbines with 98.5 mmBtu/hr duct burner | 2007-08-22 | CO CATALYST | RMC ENVIRONMENTAL | 123.5 MMBTU/HR | 1.97 LB/HR W/O DUCT BURNER; 89% DE | 135.8 MMBTU/HR | 0.14 LB/HR; 98.4% DE | 10 | CO - Carbon Monoxide | PASS | NA | Y | THIS TEST WAS ACTUALLY PERFORMED ON 8/23/07. CO CATALYST TEMPERATURE DURING TESTING WAS 497 DEG F. | Yes
2007 | 1619 | 1431070849 | University of Cincinnati | Clifton Campus | Cincinnati | 45221 |  | Hamilton | P003 | 13.5 MW Natural Gas/ No. 2 Fuel Oil-fired Turbines with 98.5 mmBtu/hr duct burner | 2007-08-23 | CO CATALYST | RMC ENVIRONMENTAL | 122.2 MMBTU/HR; 98.5 MMBTU/HR DB | 2.84 LB/HR W DUCT BURNER; 89% DE | 136.1 MMBTU/HR; 99.2 MMBTU/HR DB | 0.76 LB/HR; 99.2% DE | 10 | CO - Carbon Monoxide | PASS | NA | Y | CO CATALYST TEMPERATURE DURING TESTING WAS 560 DEG F. | Yes
2007 | 1620 | 1431070849 | University of Cincinnati | Clifton Campus | Cincinnati | 45221 |  | Hamilton | P004 | 13.5 MW Natural Gas/ No. 2 Fuel Oil-fired Turbines with 98.5 mmBtu/hr duct burner | 2007-08-24 | CO CATALYST | RMC ENVIRONMENTAL | 128.7 MMBTU/HR; 98.5 MMBTU/HR DB | 2.84 LB/HR W DUCT BURNER; 89% DE | 139.5 MMBTU/HR; 99.3 MMBTU/HR DB | 0.14 LB/HR; 99.9% DE | 10 | CO - Carbon Monoxide | PASS | NA | Y | CO CATALYST TEMPERATURE DURING TESTING WAS 553 DEG F. | Yes
2005 | 476 | 0320010006 | Richland Substation Peaker Facility | Carpenter Rd. S/U.S. 24 | Defiance | 43512 |  | Defiance | P001 | 1673 mmBtu/hr natural gas-fired simple cycle turbine generator, with distillate oil backup, controlled with water injection NOx reduction system | 2005-08-09 | none | GRACE CONSULTING, INC. | 1673 mmbtu/hr | 40.0 lbs/hr | 1483.5 mmbtu/hr | 2.72 lbs/hr | 10 | CO - Carbon Monoxide | PASS | NA | Y | Operated at 88.7 % of maximum process weight rate, but met the definition of "peak load" for testing day.
2016 | 1918 | 0857043333 | DP&L Tait Generating Station | 2101 Arbor Boulevard | Moraine | 45439 | 1762 | Montgomery | P005 | 80 MW (1115 mmBtu/hr nominal heat input) natural gas or fuel oil fired simple cycle turbine with water injection controls, CT-1 | 2016-03-11 | CT-1(Other): Max. controlled emission rate = permit limit; CT-2(Other): Max. controlled emission rate = permit limit; CT-3(gas)(Other): Max. controlled emission rate = permit limit; CT-3(gas)(Other): Max. controlled emission rate = permit limit | Mostardi Platt, Inc. | 80 MW | 350 lb/hr CO | 81 MW | 2.2 lb/hr CO | 10 | CO - Carbon Monoxide | PP | Y | NA | Low Mass Emissions test to determine unit emissions while burning #2 fuel oil. Additional tests at differing loads where performed to establish water to fuel ratios. At standard operations, P005 water to fuel ration was 1.27 at 80MW. With additional wa | Yes
2016 | 1919 | 0857043333 | DP&L Tait Generating Station | 2101 Arbor Boulevard | Moraine | 45439 | 1762 | Montgomery | P006 | 80 MW (1115 mmBtu/hr nominal heat input) natural gas or fuel oil fired simple cycle turbine with water injection controls, CT-2 | 2016-03-11 | CT-1(Other): Max. controlled emission rate = permit limit; CT-2(Other): Max. controlled emission rate = permit limit; CT-3(gas)(Other): Max. controlled emission rate = permit limit; CT-3(gas)(Other): Max. controlled emission rate = permit limit | Mostardi Platt, Inc. | 80 MW | 350 lb/hr CO | 81 MW | 12.8 lb/hr CO | 10 | CO - Carbon Monoxide | PP | Y | NA | Low Mass Emissions test to determine unit emissions while burning #2 fuel oil. Additional tests at differing loads where performed to establish water to fuel ratios. At standard operations, P005 water to fuel ration was 1.27 at 80MW. With additional wa | Yes
2016 | 1920 | 0857043333 | DP&L Tait Generating Station | 2101 Arbor Boulevard | Moraine | 45439 | 1762 | Montgomery | P007 | 80 MW (1115 mmBtu/hr nominal heat input) natural gas or fuel oil fired simple cycle turbine with water injection and dry low NOx (DLN) combustor controls, CT-3 | 2016-03-11 | CT-1(Other): Max. controlled emission rate = permit limit; CT-2(Other): Max. controlled emission rate = permit limit; CT-3(gas)(Other): Max. controlled emission rate = permit limit; CT-3(gas)(Other): Max. controlled emission rate = permit limit | Mostardi Platt, Inc. | 80 MW | 800 lb/hr CO | 80 MW | <1.0 lb/hr CO | 10 | CO - Carbon Monoxide | PP | Y | NA | Low Mass Emissions test to determine unit emissions while burning #2 fuel oil. Additional tests at differing loads where performed to establish water to fuel ratios. At standard operations, P005 water to fuel ration was 1.27 at 80MW. With additional wa | Yes
2011 | 671 | 0448010737 | City of Toledo, Division of Water Reclamation | 3900 North Summit St. | Toledo | 43611 |  | Lucas | P109 | Natural Gas/Digester Gas/Landfill Gas powered combustion turbine for combined cycle cogeneration system | 2011-07-06 | none | Bureau Veritas Co | 10 MW | 36.51 lbs/hr | 8.5 MW | 0.4 lb/hr | 10 | CO - Carbon Monoxide | PASS | NA | Y |  | Yes
2011 | 675 | 0448010737 | City of Toledo, Division of Water Reclamation | 3900 North Summit St. | Toledo | 43611 |  | Lucas | P109 | Natural Gas/Digester Gas/Landfill Gas powered combustion turbine for combined cycle cogeneration system | 2011-07-07 | none | Bureau Veritas Co | 5 MW | 29.2 lbs/hr | 5.5 MW | 0.6 lb/hr | 10 | CO - Carbon Monoxide | PASS | NA | Y | test 1 (Turbine fired with biogas & Natural gas | Yes
2011 | 677 | 0448010737 | City of Toledo, Division of Water Reclamation | 3900 North Summit St. | Toledo | 43611 |  | Lucas | P109 | Natural Gas/Digester Gas/Landfill Gas powered combustion turbine for combined cycle cogeneration system | 2011-07-08 | none | Bureau Veritas Co | 5 MW | 29.2 lbs/hr | 1.8 MW | 9.5 lb/hr | 10 | CO - Carbon Monoxide | PASS | NA | Y | test 3 (Turbine fired with biogas vented to HRSG) | Yes
2011 | 680 | 0448010737 | City of Toledo, Division of Water Reclamation | 3900 North Summit St. | Toledo | 43611 |  | Lucas | P109 | Natural Gas/Digester Gas/Landfill Gas powered combustion turbine for combined cycle cogeneration system | 2011-07-09 | none | Bureau Veritas Co | 5 MW | 7.31 lbs/hr | 4 MW | 1.7 lb/hr | 10 | CO - Carbon Monoxide | PASS | NA | Y | test 4 (HRSG fired with biogas and Natural Gas) | Yes

## Turbine VOC
REPORTING YEAR | RECORD_NUMBER | FACILITY ID | FACILITY NAME | ADDRESS | CITY | ZIP5 | ZIP4 | COUNTY | EUID | EUID DESCRIPTION | EVALUATION DATE | CONTROL EQUPMENT | COMPANY PERFORMING TEST | MAX RATE | ALLOWABLE RATE | TESTED OPERATING RATE | TESTED EMISSION RATE | METHOD NUMBER | POLLUTANTS | RESULTS | CONFORM | AUDIT | NOTES | COULD_BE_GENERATOR
2004 | 799 | 0664000100 | Texas Eastern Transmission LP - Somerset | 1895 Big Inch Road | Somerset | 43783 | 0000 | Perry | B009 | Mars Solar Turbine, 10,600 HP, Natural gas-fired turbine used for natural gas compression. ser# 0260M | 2004-03-09 | none | CUBIX CORP. | 85.6 mmbh | 2.12 lb/hr | 106 mmbh | 0.23 lb/hr | 18 | VOC - Volatile Organic Compounds | PASS | NA | Y
2012 | 49 | 0124010117 | Dominion Transmission - Washington Compressor Station | 708 Parrott Road, N.W. | Washington Court House | 43160 |  | Fayette | B001 | Solar Centaur Combustion Turbine No. 1, 5500 HP | 2012-04-10 | None | Dominion Transmission | 100% | 1.70 lbs/hr | 100% torque | 0.28 lbs/hr | 25A | Total Hydrocarbons | PASS | NA | Y | Additional test run at 93% torque resulted in 0.16 lbs/hr VOC.
2012 | 53 | 0124010117 | Dominion Transmission - Washington Compressor Station | 708 Parrott Road, N.W. | Washington Court House | 43160 |  | Fayette | B002 | Solar Centaur Combustion Turbine No. 2, 5500 HP | 2012-04-10 | None | Dominion Transmission | 100% | 1.70 lbs/hr | 100% torque | 0.22 lbs/hr | 25A | Total Hydrocarbons | PASS | NA | Y | Additional test run at 94% torque resulted in 4.48 lbs/hr VOC.
2012 | 85 | 0124010117 | Dominion Transmission - Washington Compressor Station | 708 Parrott Road, N.W. | Washington Court House | 43160 |  | Fayette | B003 | Solar Centaur Combustion Turbine No. 3, 5500 HP | 2012-04-11 | None | Dominion Transmission | 100% | 1.70 lbs/hr | 100% torque | 0.30 lbs/hr | 25A | Total Hydrocarbons | PASS | NA | Y | Additional test run at 93% torque resulted in 0.22 lbs/hr VOC.
2012 | 143 | 0145000307 | Dominion - Newark Compressor Station | 19042 Nashport Road | Nashport | 43830 |  | Licking | B002 | Solar Centaur Combustion Turbine No. 2, 5500 HP | 2012-04-03 | none | DOMINION TRANSMISSION | 5500 hp | 1.7 lbs/hr | 99% ngp | 0.31 lbs/hr | 25A | Total Hydrocarbons | PASS | NA | Y | Witnessed=No, but it says Witnessed By Adam Novak)
2012 | 148 | 0145000307 | Dominion - Newark Compressor Station | 19042 Nashport Road | Nashport | 43830 |  | Licking | B003 | Solar Centaur Combustion Turbine No. 3, 5500 HP | 2012-04-03 | none | DOMINION TRANSMISSION | 5500 hp | 1.7 lbs/hr | 99% ngp | 1.21 lbs/hr | 25A | Total Hydrocarbons | PASS | NA | Y | Witnessed=No, but it says Witnessed By Adam Novak)
2014 | 2084 | 0661005010 | E2 Appalachian Compression LLC - Upper Hill | Opossum Run Rd and Town Hwy 120 | Sarahsville | 43779 |  | Noble | P009 | 1,680 Hp. Waukesha (L7044GSI) natural gas-fired, rich burn, turbocharged, with oxidation catalyst, compressor engine. | 2014-07-15 | C-9(Catalytic Converter): Engine Catalyst | E2 Energy Services | 1,680 Hp | 0.22 lb/hr | 1,545 Hp | 0.1 lb/hr | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y
2014 | 2087 | 0661005010 | E2 Appalachian Compression LLC - Upper Hill | Opossum Run Rd and Town Hwy 120 | Sarahsville | 43779 |  | Noble | P007 | 1,680 Hp. Waukesha (L7044GSI) natural gas-fired, rich burn, turbocharged, with oxidation catalyst, compressor engine. | 2014-11-06 | C-7(Catalytic Converter): Engine Catalyst; C-8(Catalytic Converter): Engine Catalyst; C-9(Catalytic Converter): Engine Catalyst | E2 Energy Services | 1680 Hp | 0.22 lb/hr | 1528 Hp | 0.02 lb/hr | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y | Method 25A not used. Method 3A and ASTM 6348-03 used
2014 | 2090 | 0661005010 | E2 Appalachian Compression LLC - Upper Hill | Opossum Run Rd and Town Hwy 120 | Sarahsville | 43779 |  | Noble | P008 | 1,680 Hp. Waukesha (L7044GSI) natural gas-fired, rich burn, turbocharged, with oxidation catalyst, compressor engine. | 2014-11-06 | C-7(Catalytic Converter): Engine Catalyst; C-8(Catalytic Converter): Engine Catalyst; C-9(Catalytic Converter): Engine Catalyst | E2 Energy Services | 1680 Hp | 0.22 lb/hr | 1221 Hp | 0.01 lb/hr | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y | Method 25A not used. Method 3A and ASTM 6348-03 used
2014 | 2092 | 0661005010 | E2 Appalachian Compression LLC - Upper Hill | Opossum Run Rd and Town Hwy 120 | Sarahsville | 43779 |  | Noble | P009 | 1,680 Hp. Waukesha (L7044GSI) natural gas-fired, rich burn, turbocharged, with oxidation catalyst, compressor engine. | 2014-11-06 | C-7(Catalytic Converter): Engine Catalyst; C-8(Catalytic Converter): Engine Catalyst; C-9(Catalytic Converter): Engine Catalyst | E2 Energy Services | 1680 Hp | 0.22 lb/hr | 1585 Hp | 0.02 lb/hr | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y | Method 25A not used. Method 3A and ASTM 6348-03 used
2014 | 2096 | 0661005010 | E2 Appalachian Compression LLC - Upper Hill | Opossum Run Rd and Town Hwy 120 | Sarahsville | 43779 |  | Noble | P004 | 1,680 Hp. Waukesha (L7044GSI) natural gas-fired, rich burn, turbocharged, with oxidation catalyst, compressor engine. | 2014-11-10 | C-4(Catalytic Converter): Engine Catalyst | E2 Energy Services | 1680 Hp | 0.22 lb/hr | 1547 Hp | 0.01 lb/hr | 25B | VOC - Volatile Organic Compounds | PASS | NA | Y | Method 25B not used. Method 3a and ASTM 6348-03 used
2014 | 2098 | 0661005010 | E2 Appalachian Compression LLC - Upper Hill | Opossum Run Rd and Town Hwy 120 | Sarahsville | 43779 |  | Noble | P002 | 1,680 Hp. Waukesha (L7044GSI) natural gas-fired, rich burn, turbocharged, with oxidation catalyst, compressor engine. | 2014-11-12 | C-2(Catalytic Converter): Engine Catalyst; C-3(Catalytic Converter): Engine Catalyst | E2 Energy Services | 1680 Hp | 0.22 lb/hr | 1575 Hp | 0.02 lb/hr | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y | Method 25 A not used. Method 3a and ASTM 6348-03 used
2014 | 2100 | 0661005010 | E2 Appalachian Compression LLC - Upper Hill | Opossum Run Rd and Town Hwy 120 | Sarahsville | 43779 |  | Noble | P003 | 1,680 Hp. Waukesha (L7044GSI) natural gas-fired, rich burn, turbocharged, with oxidation catalyst, compressor engine. | 2014-11-12 | C-2(Catalytic Converter): Engine Catalyst; C-3(Catalytic Converter): Engine Catalyst | E2 Energy Services | 1680 Hp | 0.22 lb/hr | 1512 Hp | 0.02 lb/hr | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y | Method 25 A not used. Method 3a and ASTM 6348-03 used
2014 | 2104 | 0661005010 | E2 Appalachian Compression LLC - Upper Hill | Opossum Run Rd and Town Hwy 120 | Sarahsville | 43779 |  | Noble | P002 | 1,680 Hp. Waukesha (L7044GSI) natural gas-fired, rich burn, turbocharged, with oxidation catalyst, compressor engine. | 2014-11-13 | C-2(Catalytic Converter): Engine Catalyst; C-3(Catalytic Converter): Engine Catalyst | E2 Energy Services | 1680 Hp | 0.22 lb/hr | 1575 Hp | 0.02 lb/hr | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y | Method 25 A not used. Method 3a and ASTM 6348-03 used
2014 | 2108 | 0661005010 | E2 Appalachian Compression LLC - Upper Hill | Opossum Run Rd and Town Hwy 120 | Sarahsville | 43779 |  | Noble | P003 | 1,680 Hp. Waukesha (L7044GSI) natural gas-fired, rich burn, turbocharged, with oxidation catalyst, compressor engine. | 2014-11-13 | C-2(Catalytic Converter): Engine Catalyst; C-3(Catalytic Converter): Engine Catalyst | E2 Energy Services | 1680 Hp | 0.22 lb/hr | 1512 Hp | 0.02 lb/hr | 25A | VOC - Volatile Organic Compounds | PASS | NA | Y | Method 25 A not used. Method 3a and ASTM 6348-03 used
2015 | 889 | 0661005027 | E2 Appalachian LLC - Batesville | 58380 St John Rd | Quaker City | 43773 |  | Noble | P001 | 1,680 Hp. Waukesha (L7044GSI) natural gas-fired, rich burn, turbocharged, with oxidation catalyst, compressor engine | 2015-01-26 | C2701C(Catalytic Converter): Engine Catalyst | E2 Energy Services | 1680 hp | 0.7 g/hp-hr | 1400 hp | 0.003 g/hp-hr | 6348 03 | VOC - Volatile Organic Compounds | PP | NA | Y
2015 | 892 | 0661005027 | E2 Appalachian LLC - Batesville | 58380 St John Rd | Quaker City | 43773 |  | Noble | P002 | 1,680 Hp. Waukesha (L7044GSI) natural gas-fired, rich burn, turbocharged, with oxidation catalyst, compressor engine | 2015-01-26 | C2701C(Catalytic Converter): Engine Catalyst | E2 Energy Services | 1680 hp | 0.70 g/hp-hr | 1361 hp | 0.006 g/hp-hr | 6348 03 | VOC - Volatile Organic Compounds | PP | NA | Y
2015 | 896 | 0661005027 | E2 Appalachian LLC - Batesville | 58380 St John Rd | Quaker City | 43773 |  | Noble | P003 | 1,680 Hp. Waukesha (L7044GSI) natural gas-fired, rich burn, turbocharged, with oxidation catalyst, compressor engine | 2015-01-27 | C2701C(Catalytic Converter): Engine Catalyst | E2 Energy Services | 1680 hp | 0.7 g/hp-hr | 1277 hp | 0.008 g/hp-hr | 6348 03 | VOC - Volatile Organic Compounds | PP | NA | Y
2015 | 898 | 0661005027 | E2 Appalachian LLC - Batesville | 58380 St John Rd | Quaker City | 43773 |  | Noble | P007 | 1,680 Hp. Waukesha (L7044GSI) natural gas-fired, rich burn, turbocharged, with oxidation catalyst, compressor engine | 2015-02-19 | C2707C(Catalytic Converter): Engine Catalyst | E2 Energy Services | 1,680 hp | 0.7 g/hp-hr | 1,512 hp | 0.004 g/hp-hr | 6348 03 | VOC - Volatile Organic Compounds | PP | NA | Y
2015 | 901 | 0661005027 | E2 Appalachian LLC - Batesville | 58380 St John Rd | Quaker City | 43773 |  | Noble | P008 | 1,680 Hp. Waukesha (L7044GSI) natural gas-fired, rich burn, turbocharged, with oxidation catalyst, compressor engine | 2015-02-19 | C2708C(Catalytic Converter): Engine Catalyst | E2 Energy Services | 1,680 hp | 0.7 g/hp-hr | 1,512 hp | 0.01 g/hp-hr | 6348 03 | VOC - Volatile Organic Compounds | PP | NA | Y
2015 | 906 | 0661005027 | E2 Appalachian LLC - Batesville | 58380 St John Rd | Quaker City | 43773 |  | Noble | P004 | 1,680 Hp. Waukesha (L7044GSI) natural gas-fired, rich burn, turbocharged, with oxidation catalyst, compressor engine | 2015-02-20 | C2704C(Catalytic Converter): Engine Catalyst | E2 Energy Services | 1,680 hp | 0.7 g/hp-hr | 1,510 hp | 0.004 g/hp-hr | 6348 03 | VOC - Volatile Organic Compounds | PP | NA | Y
2015 | 907 | 0661005027 | E2 Appalachian LLC - Batesville | 58380 St John Rd | Quaker City | 43773 |  | Noble | P005 | 1,680 Hp. Waukesha (L7044GSI) natural gas-fired, rich burn, turbocharged, with oxidation catalyst, compressor engine | 2015-02-27 | C2705C(Catalytic Converter): Engine Catalyst | E2 Energy Services | 1,680 hp | 0.7 g/hp-hr | 1,295 hp | 0.006 g/hp-hr | 6348 03 | VOC - Volatile Organic Compounds | PP | NA | Y
2016 | 912 | 0744000150 | Hanging Rock Energy Facility | 1395 County Rd 1A | Ironton | 45638 |  | Lawrence | P003 | GE 7FA natural gas fired dry low NOx (DLN) combustion turbine No. 3, nominally rated at 2,045 MMBtu/hr, with duct burner nominally rated at 587 MMBtu/hr operating in combined cycle mode controlled by Selective Calalytic Reduction (SCR) | 2016-04-08 | SCR - 1GT1(Other): Min temp - 525 F; SCR - 1GT2(Other): Min temp - 525 F; SCR - 2GT1(Other): Min temp - 525 F; SCR - 2GT2(Other): Min temp - 525 F | Mostardi Platt | 2,045 MMbtu/hr | without duct burners 3.1 lbs/hr | 1,945.2 MMbtu/hr avg | 0 lbs/hr | 25A | VOC - Volatile Organic Compounds | PP | Y | NA | Tests conducted WITHOUT duct burners operating
2016 | 913 | 0744000150 | Hanging Rock Energy Facility | 1395 County Rd 1A | Ironton | 45638 |  | Lawrence | P004 | GE 7FA natural gas fired dry low NOx (DLN) combustion turbine No. 4, nominally rated at 2,045 MMBtu/hr, with duct burner nominally rated at 587 MMBtu/hr operating in combined cycle mode controlled by Selective Calalytic Reduction (SCR) | 2016-04-08 | SCR - 1GT1(Other): Min temp - 525 F; SCR - 1GT2(Other): Min temp - 525 F; SCR - 2GT1(Other): Min temp - 525 F; SCR - 2GT2(Other): Min temp - 525 F | Mostardi Platt | 2,045 MMbtu/hr | without duct burners 3.1 lbs/hr | 1,908.2 MMbtu/hr avg | 0.37 lbs/hr | 25A | VOC - Volatile Organic Compounds | PP | Y | NA | Tests conducted WITHOUT duct burners operating
2016 | 1264 | 0630005041 | E2 Energy Services - Borton | 65483 Lydick Rd | Quaker City | 43773 |  | Guernsey | P002 | 1,680 Hp. Waukesha (L7044GSI) natural gas-fired, rich burn, turbocharged, with oxidation catalyst, compressor engine (Model Year 2014) | 2016-03-02 | C-2701C(Catalytic Converter): Engine Catalyst | E2 Energy Services | 1680 hp | 0.03 g/hp-hr | 1519 hp | 0.01 g/hp-hr | 6348 03 | VOC - Volatile Organic Compounds | PP | N | NA
2016 | 1265 | 0630005041 | E2 Energy Services - Borton | 65483 Lydick Rd | Quaker City | 43773 |  | Guernsey | P004 | 1,680 Hp. Waukesha (L7044GSI) natural gas-fired, rich burn, turbocharged, with oxidation catalyst, compressor engine (Model Year 2014) | 2016-05-12 | C-2703C(Catalytic Converter): Engine Catalyst | E2 Energy Services | 1680 hp | 0.03 g/hp-hr | 1348 hp | 0.015 g/hp-hr | 6348 03 | VOC - Volatile Organic Compounds | PP | Y | NA
2016 | 1607 | 0661005010 | E2 Appalachian Compression LLC - Upper Hill | Opossum Run Rd and Town Hwy 120 | Sarahsville | 43779 |  | Noble | P003 | 1,680 Hp. Waukesha (L7044GSI) natural gas-fired, rich burn, turbocharged, with oxidation catalyst, compressor engine. | 2016-04-29 | C-3(Catalytic Converter): Engine Catalyst; C-9(Catalytic Converter): Engine Catalyst | Alliance Source Testing | 1680 hp | 1.0 g/hp-hr | 1658 hp | 0.01 g/hp-hr | 25A | VOC - Volatile Organic Compounds | PP | Y | NA
2016 | 1608 | 0661005010 | E2 Appalachian Compression LLC - Upper Hill | Opossum Run Rd and Town Hwy 120 | Sarahsville | 43779 |  | Noble | P009 | 1,680 Hp. Waukesha (L7044GSI) natural gas-fired, rich burn, turbocharged, with oxidation catalyst, compressor engine. | 2016-04-29 | C-3(Catalytic Converter): Engine Catalyst; C-9(Catalytic Converter): Engine Catalyst | Alliance Source Testing | 1680 hp | 1.0 g/hp-hr | 1646 hp | 0.02 g/hp-hr | 25A | VOC - Volatile Organic Compounds | PP | Y | NA
2016 | 1613 | 0661005010 | E2 Appalachian Compression LLC - Upper Hill | Opossum Run Rd and Town Hwy 120 | Sarahsville | 43779 |  | Noble | P007 | 1,680 Hp. Waukesha (L7044GSI) natural gas-fired, rich burn, turbocharged, with oxidation catalyst, compressor engine. | 2016-03-17 | C-7(Catalytic Converter): Engine Catalyst; C-8(Catalytic Converter): Engine Catalyst | Alliance Source Testing | 1680 hp | 1.0 g/hp-hr | 1464 hp | 0.02 g/hp-hr | 25A | VOC - Volatile Organic Compounds | PP | Y | NA
2016 | 1614 | 0661005010 | E2 Appalachian Compression LLC - Upper Hill | Opossum Run Rd and Town Hwy 120 | Sarahsville | 43779 |  | Noble | P008 | 1,680 Hp. Waukesha (L7044GSI) natural gas-fired, rich burn, turbocharged, with oxidation catalyst, compressor engine. | 2016-03-17 | C-7(Catalytic Converter): Engine Catalyst; C-8(Catalytic Converter): Engine Catalyst | Alliance Source Testing | 1680 hp | 1.0 g/hp-hr | 1406 hp | 0.02 g/hp-hr | 25A | VOC - Volatile Organic Compounds | PP | Y | NA
2016 | 1617 | 0661005010 | E2 Appalachian Compression LLC - Upper Hill | Opossum Run Rd and Town Hwy 120 | Sarahsville | 43779 |  | Noble | P003 | 1,680 Hp. Waukesha (L7044GSI) natural gas-fired, rich burn, turbocharged, with oxidation catalyst, compressor engine. | 2016-04-29 | C-3(Catalytic Converter): Engine Catalyst; C-9(Catalytic Converter): Engine Catalyst | Ecotest Energy Services | 1680 hp | 1.0 g/hp-hr | 1658 hp | 0.01 g/hp-hr | 6348 03 | VOC - Volatile Organic Compounds | PP | Y | NA
2016 | 1618 | 0661005010 | E2 Appalachian Compression LLC - Upper Hill | Opossum Run Rd and Town Hwy 120 | Sarahsville | 43779 |  | Noble | P009 | 1,680 Hp. Waukesha (L7044GSI) natural gas-fired, rich burn, turbocharged, with oxidation catalyst, compressor engine. | 2016-04-29 | C-3(Catalytic Converter): Engine Catalyst; C-9(Catalytic Converter): Engine Catalyst | Ecotest Energy Services | 1680 hp | 1.0 g/hp-hr | 1646 hp | 0.02 g/hp-hr | 6348 03 | VOC - Volatile Organic Compounds | PP | Y | NA
2016 | 1625 | 0661005010 | E2 Appalachian Compression LLC - Upper Hill | Opossum Run Rd and Town Hwy 120 | Sarahsville | 43779 |  | Noble | P002 | 1,680 Hp. Waukesha (L7044GSI) natural gas-fired, rich burn, turbocharged, with oxidation catalyst, compressor engine. | 2016-07-13 | C-2(Catalytic Converter): Engine Catalyst; C-8(Catalytic Converter): Engine Catalyst | Alliance Source Testing | 1,680 hp | 86 ppm | 1,529 hp | 1.1 ppm | 25A | VOC - Volatile Organic Compounds | PP | Y | NA
2016 | 1626 | 0661005010 | E2 Appalachian Compression LLC - Upper Hill | Opossum Run Rd and Town Hwy 120 | Sarahsville | 43779 |  | Noble | P008 | 1,680 Hp. Waukesha (L7044GSI) natural gas-fired, rich burn, turbocharged, with oxidation catalyst, compressor engine. | 2016-07-13 | C-2(Catalytic Converter): Engine Catalyst; C-8(Catalytic Converter): Engine Catalyst | Alliance Source Testing | 1,680 hp | 86 ppm | 1,518 hp | 1.1 ppm | 25A | VOC - Volatile Organic Compounds | PP | Y | NA
2016 | 1628 | 0661005027 | E2 Appalachian LLC - Batesville | 58380 St John Rd | Quaker City | 43773 |  | Noble | P001 | 1,680 Hp. Waukesha (L7044GSI) natural gas-fired, rich burn, turbocharged, with oxidation catalyst, compressor engine | 2016-04-13 | C2701C(Catalytic Converter): Engine Catalyst | E2 Appalachian | 1680 hp | 0.7 g/hp-hr | 1539 hp | 0.023 g/hp-hr | 6348 03 | VOC - Volatile Organic Compounds | PP | Y | NA
2016 | 1632 | 0661005027 | E2 Appalachian LLC - Batesville | 58380 St John Rd | Quaker City | 43773 |  | Noble | P002 | 1,680 Hp. Waukesha (L7044GSI) natural gas-fired, rich burn, turbocharged, with oxidation catalyst, compressor engine | 2016-03-24 | C2702C(Catalytic Converter): Engine Catalyst | E2 Appalachian | 1680 hp | 0.7 g/hp-hr | 1473 hp | 0.0225 g/hp-hr | 6348 03 | VOC - Volatile Organic Compounds | PP | Y | NA
2016 | 1633 | 0661005027 | E2 Appalachian LLC - Batesville | 58380 St John Rd | Quaker City | 43773 |  | Noble | P003 | 1,680 Hp. Waukesha (L7044GSI) natural gas-fired, rich burn, turbocharged, with oxidation catalyst, compressor engine | 2016-03-23 | C2703C(Catalytic Converter): Engine Catalyst | E2 Appalachian | 1680 hp | 0.7 g/hp-hr | 1348 hp | 0.0174 g/hp-hr | 6348 03 | VOC - Volatile Organic Compounds | PP | Y | NA
2016 | 1637 | 0661005027 | E2 Appalachian LLC - Batesville | 58380 St John Rd | Quaker City | 43773 |  | Noble | P004 | 1,680 Hp. Waukesha (L7044GSI) natural gas-fired, rich burn, turbocharged, with oxidation catalyst, compressor engine | 2016-03-30 | C2704C(Catalytic Converter): Engine Catalyst | E2 Appalachian | 1680 hp | 0.7 g/hp-hr | 1470 hp | 0.0180 g/hp-hr | 6348 03 | VOC - Volatile Organic Compounds | PP | Y | NA
2016 | 1641 | 0661005027 | E2 Appalachian LLC - Batesville | 58380 St John Rd | Quaker City | 43773 |  | Noble | P005 | 1,680 Hp. Waukesha (L7044GSI) natural gas-fired, rich burn, turbocharged, with oxidation catalyst, compressor engine | 2016-03-31 | C2705C(Catalytic Converter): Engine Catalyst | E2 Appalachian | 1680 hp | 0.7 g/hp-hr | 1425 hp | 0.0189 g/hp-hr | 6348 03 | VOC - Volatile Organic Compounds | PP | Y | NA
2016 | 1642 | 0661005027 | E2 Appalachian LLC - Batesville | 58380 St John Rd | Quaker City | 43773 |  | Noble | P006 | 1,680 Hp. Waukesha (L7044GSI) natural gas-fired, rich burn, turbocharged, with oxidation catalyst, compressor engine | 2016-04-01 | C2705C(Catalytic Converter): Engine Catalyst | E2 Appalachian | 1680 hp | 0.06 g/hp-hr | 1551 hp | 0.0077 g/hp-hr | 6348 03 | VOC - Volatile Organic Compounds | PP | Y | NA
2016 | 1647 | 0661005027 | E2 Appalachian LLC - Batesville | 58380 St John Rd | Quaker City | 43773 |  | Noble | P008 | 1,680 Hp. Waukesha (L7044GSI) natural gas-fired, rich burn, turbocharged, with oxidation catalyst, compressor engine | 2016-04-14 | C2708C(Catalytic Converter): Engine Catalyst | E2 Appalachian | 1680 hp | 0.7 g/hp-hr | 1475 hp | 0.0222 g/hp-hr | 6348 03 | VOC - Volatile Organic Compounds | PP | Y | NA
2016 | 1648 | 0661005027 | E2 Appalachian LLC - Batesville | 58380 St John Rd | Quaker City | 43773 |  | Noble | P002 | 1,680 Hp. Waukesha (L7044GSI) natural gas-fired, rich burn, turbocharged, with oxidation catalyst, compressor engine | 2016-04-14 | C2702C(Catalytic Converter): Engine Catalyst | E2 Energy Services | 1680 hp | 0.7 g/hp-hr | 1473 hp | 0.02 g/hp-hr | 6348 03 | VOC - Volatile Organic Compounds | PP | N | NA
2016 | 1653 | 0661005027 | E2 Appalachian LLC - Batesville | 58380 St John Rd | Quaker City | 43773 |  | Noble | P002 | 1,680 Hp. Waukesha (L7044GSI) natural gas-fired, rich burn, turbocharged, with oxidation catalyst, compressor engine | 2016-04-28 | C2702C(Catalytic Converter): Engine Catalyst | Alliance Source Testing | 1680 hp | 0.7 g/hp-hr | 1529 hp | 0.01 g/hp-hr | 25A | VOC - Volatile Organic Compounds | PP | N | NA
2016 | 1660 | 0661005027 | E2 Appalachian LLC - Batesville | 58380 St John Rd | Quaker City | 43773 |  | Noble | P001 | 1,680 Hp. Waukesha (L7044GSI) natural gas-fired, rich burn, turbocharged, with oxidation catalyst, compressor engine | 2016-07-11 | C2701C(Catalytic Converter): Engine Catalyst; C2707C(Catalytic Converter): Engine Catalyst; C2708C(Catalytic Converter): Engine Catalyst | Alliance Source Testing | 1,680 hp | 0.7 g/hp-hr | 1,529 hp | 0.01 g/hp-hr | 25A | VOC - Volatile Organic Compounds | PP | Y | NA
2016 | 1661 | 0661005027 | E2 Appalachian LLC - Batesville | 58380 St John Rd | Quaker City | 43773 |  | Noble | P007 | 1,680 Hp. Waukesha (L7044GSI) natural gas-fired, rich burn, turbocharged, with oxidation catalyst, compressor engine | 2016-07-11 | C2701C(Catalytic Converter): Engine Catalyst; C2707C(Catalytic Converter): Engine Catalyst; C2708C(Catalytic Converter): Engine Catalyst | Alliance Source Testing | 1,680 hp | 0.7 g/hp-hr | 1,607 hp | 0.03 g/hp-hr | 25A | VOC - Volatile Organic Compounds | PP | Y | NA
2016 | 1662 | 0661005027 | E2 Appalachian LLC - Batesville | 58380 St John Rd | Quaker City | 43773 |  | Noble | P008 | 1,680 Hp. Waukesha (L7044GSI) natural gas-fired, rich burn, turbocharged, with oxidation catalyst, compressor engine | 2016-07-11 | C2701C(Catalytic Converter): Engine Catalyst; C2707C(Catalytic Converter): Engine Catalyst; C2708C(Catalytic Converter): Engine Catalyst | Alliance Source Testing | 1,680 hp | 0.7 g/hp-hr | 1,568 hp | 0.01 g/hp-hr | 25A | VOC - Volatile Organic Compounds | PP | Y | NA
2016 | 1665 | 0661005027 | E2 Appalachian LLC - Batesville | 58380 St John Rd | Quaker City | 43773 |  | Noble | P006 | 1,680 Hp. Waukesha (L7044GSI) natural gas-fired, rich burn, turbocharged, with oxidation catalyst, compressor engine | 2016-07-12 | C2706C(Catalytic Converter): Engine Catalyst | Alliance Source Testing | 1,680 hp | 0.06 g/hp-hr | 1,490 hp | 0.01 g/hp-hr | 25A | VOC - Volatile Organic Compounds | PP | Y | NA
2016 | 1808 | 0744000150 | Hanging Rock Energy Facility | 1395 County Rd 1A | Ironton | 45638 |  | Lawrence | P001 | GE 7FA natural gas fired dry low NOx (DLN) combustion turbine No. 1, nominally rated at 2,045 MMBtu/hr, with duct burner nominally rated at 587MMBtu/hr operating in combined cycle mode controlled by Selective Calalytic Reduction (SCR) | 2016-04-07 | SCR - 1GT1(Other): Min temp - 525 F; SCR - 1GT2(Other): Min temp - 525 F; SCR - 2GT1(Other): Min temp - 525 F; SCR - 2GT2(Other): Min temp - 525 F | Mostardi Platt | 2,632 MMbtu/hr | duct burners operating 6.2 lbs/hr | 2,436 MMbtu/hr avg | 2.0 lbs/hr | 25A | VOC - Volatile Organic Compounds | PP | Y | NA | Tests conducted with DUCT BURNERS OPERATING
2016 | 1809 | 0744000150 | Hanging Rock Energy Facility | 1395 County Rd 1A | Ironton | 45638 |  | Lawrence | P002 | GE 7FA natural gas fired dry low NOx (DLN) combustion turbine No. 2, nominally rated at 2,045 MMBtu/hr, with duct burner nominally rated at 587 MMBtu/hr operating in combined cycle mode controlled by Selective Calalytic Reduction (SCR) | 2016-04-07 | SCR - 1GT1(Other): Min temp - 525 F; SCR - 1GT2(Other): Min temp - 525 F; SCR - 2GT1(Other): Min temp - 525 F; SCR - 2GT2(Other): Min temp - 525 F | Mostardi Platt | 2,632 MMbtu/hr | duct burners operating 6.2 lbs/hr | 2,370.1 MMbtu/hr avg | 1.31 lbs/hr | 25A | VOC - Volatile Organic Compounds | PP | Y | NA | Tests conducted with DUCT BURNERS OPERATING
2016 | 1810 | 0744000150 | Hanging Rock Energy Facility | 1395 County Rd 1A | Ironton | 45638 |  | Lawrence | P003 | GE 7FA natural gas fired dry low NOx (DLN) combustion turbine No. 3, nominally rated at 2,045 MMBtu/hr, with duct burner nominally rated at 587 MMBtu/hr operating in combined cycle mode controlled by Selective Calalytic Reduction (SCR) | 2016-04-07 | SCR - 1GT1(Other): Min temp - 525 F; SCR - 1GT2(Other): Min temp - 525 F; SCR - 2GT1(Other): Min temp - 525 F; SCR - 2GT2(Other): Min temp - 525 F | Mostardi Platt | 2,632 MMbtu/hr | duct burners operating 6.2 lbs/hr | 2,375.8 MMbtu/hr avg | 1.69 lbs/hr | 25A | VOC - Volatile Organic Compounds | PP | Y | NA | Tests conducted with DUCT BURNERS OPERATING
2016 | 1811 | 0744000150 | Hanging Rock Energy Facility | 1395 County Rd 1A | Ironton | 45638 |  | Lawrence | P004 | GE 7FA natural gas fired dry low NOx (DLN) combustion turbine No. 4, nominally rated at 2,045 MMBtu/hr, with duct burner nominally rated at 587 MMBtu/hr operating in combined cycle mode controlled by Selective Calalytic Reduction (SCR) | 2016-04-07 | SCR - 1GT1(Other): Min temp - 525 F; SCR - 1GT2(Other): Min temp - 525 F; SCR - 2GT1(Other): Min temp - 525 F; SCR - 2GT2(Other): Min temp - 525 F | Mostardi Platt | 2,632 MMbtu/hr | duct burners operating 6.2 lbs/hr | 2,342.7 MMbtu/hr avg | 0.37 lbs/hr | 25A | VOC - Volatile Organic Compounds | PP | Y | NA | Tests conducted with DUCT BURNERS OPERATING
2016 | 1828 | 0744000150 | Hanging Rock Energy Facility | 1395 County Rd 1A | Ironton | 45638 |  | Lawrence | P001 | GE 7FA natural gas fired dry low NOx (DLN) combustion turbine No. 1, nominally rated at 2,045 MMBtu/hr, with duct burner nominally rated at 587MMBtu/hr operating in combined cycle mode controlled by Selective Calalytic Reduction (SCR) | 2016-04-08 | SCR - 1GT1(Other): Min temp - 525 F; SCR - 1GT2(Other): Min temp - 525 F; SCR - 2GT1(Other): Min temp - 525 F; SCR - 2GT2(Other): Min temp - 525 F | Mostardi Platt | 2,045 MMbtu/hr | without duct burners 3.1 lbs/hr | 1,967.2 MMbtu/hr avg | 0.59 lbs/hr | 25A | VOC - Volatile Organic Compounds | PP | Y | NA | Tests conducted WITHOUT duct burners operating
2016 | 1829 | 0744000150 | Hanging Rock Energy Facility | 1395 County Rd 1A | Ironton | 45638 |  | Lawrence | P002 | GE 7FA natural gas fired dry low NOx (DLN) combustion turbine No. 2, nominally rated at 2,045 MMBtu/hr, with duct burner nominally rated at 587 MMBtu/hr operating in combined cycle mode controlled by Selective Calalytic Reduction (SCR) | 2016-04-08 | SCR - 1GT1(Other): Min temp - 525 F; SCR - 1GT2(Other): Min temp - 525 F; SCR - 2GT1(Other): Min temp - 525 F; SCR - 2GT2(Other): Min temp - 525 F | Mostardi Platt | 2,045 MMbtu/hr | without duct burners 3.1 lbs/hr | 1,967.2 MMbtu/hr avg | 1.41 lbs/hr | 25A | VOC - Volatile Organic Compounds | PP | Y | NA | Tests conducted WITHOUT duct burners operating
2016 | 2343 | 1483060328 | Texas Eastern Transmission - Lebanon | 1157 State Road 122 West | Lebanon | 45036 |  | Warren | P006 | Solar Taurus, 68.34 MMBtu/hr (ISO conditions), natural gas-fired turbine used for natural gas compression | 2016-11-09 | P006 Ox Cat(Other): oxidation catalyst | Nordon Corporation | 68.34 MMBtu/hr | < 10 TPY | 61.345 MMBtu | 0.50 TPY | 25A | VOC - Volatile Organic Compounds | PP | Y | NA | Stack Test Report - Compliance Report ID#130459 ITT - Compliance Report ID#129355 Permit - PTI P120361 1. An example calculation of EPA Method 4- moisture was not originally included in the emission compliance test report. The test report stated that EPA
2014 | 2174 | 0684000212 | Washington Energy Facility | 859 Ohio 83 | Beverly | 45715 | 1329 | Washington | P001 | 170 MW GE 7FA natural gas fired dry low NOx (DLN) combustion turbine with duct firing operating in combined cycle mode controlled by Selective Catalytic Reduction (SCR)- Modified | 2014-12-02 | SCR #1(Other): 32.3 lb/hr with duct burner firing(24.7 lb/hr w/o) | Mostardi Platt | 170 MW | 7.3 lbs/hr | 181 MW | 1.09 lbs/hr | 6348 03 | VOC - Volatile Organic Compounds | PASS | NA | Y | duct burners on Ammonia allowable- 28.1 lbs/hr emission rate-0.81 lb/hr formaldehyde allowable-0.82 lb/hr emission rate-<0.41 lb/hr | Yes
2014 | 2178 | 0684000212 | Washington Energy Facility | 859 Ohio 83 | Beverly | 45715 | 1329 | Washington | P001 | 170 MW GE 7FA natural gas fired dry low NOx (DLN) combustion turbine with duct firing operating in combined cycle mode controlled by Selective Catalytic Reduction (SCR)- Modified | 2014-12-03 | SCR #1(Other): 32.3 lb/hr with duct burner firing(24.7 lb/hr w/o) | Mostardi Platt | 170 MW | 3.0 lbs/hr | 180 MW | 0.44 lb/hr | 6348 03 | VOC - Volatile Organic Compounds | PASS | NA | Y | duct burners off ammonia allowable-26.6 lbs/hr emission rate-0.61 lbs/hr formaldehyde allowable-0.8 lb/hr emission rate-<0.41 lb/hr | Yes
2014 | 2183 | 0684000212 | Washington Energy Facility | 859 Ohio 83 | Beverly | 45715 | 1329 | Washington | P002 | 170 MW GE 7FA natural gas fired dry low NOx (DLN) combustion turbine with duct firing operating in combined cycle mode controlled with Selective Catalytic Reduction (SCR)- Modified | 2014-12-04 | SCR #2(Other): 32.3 lb/hr with duct burner firing(24.7 lb/hr w/o) | Mostardi Platt | 170 MW | 7.3 lbs/hr | 186 MW | 0.15 lb/hr | 6348 03 | VOC - Volatile Organic Compounds | PASS | NA | Y | ammonia allowable-28.1 lbs/hr emission rate-1.39 lbs/hr formaldehyde allowable-0.82 lb/hr emission rate-<0.43 lb/hr duct burners on | Yes
2014 | 2185 | 0684000212 | Washington Energy Facility | 859 Ohio 83 | Beverly | 45715 | 1329 | Washington | P002 | 170 MW GE 7FA natural gas fired dry low NOx (DLN) combustion turbine with duct firing operating in combined cycle mode controlled with Selective Catalytic Reduction (SCR)- Modified | 2014-12-05 | SCR #2(Other): 32.3 lb/hr with duct burner firing(24.7 lb/hr w/o) | Mostardi Platt | 170 MW | 3.0 lbs/hr | 181 MW | 0.36 lb/hr | 6348 03 | VOC - Volatile Organic Compounds | PASS | NA | Y | duct burners off ammonia allowable-26.6 lbs/hr emission rate-0.73 lb/hr formaldehyde allowable 0.8 lb/hr emission rate-<0.41 lb/hr | Yes
2016 | 1771 | 0684000212 | Washington Energy Facility | 859 Ohio 83 | Beverly | 45715 | 1329 | Washington | P001 | Nominally Rated 207 MW GE 7FA - Natural-Gas Fired Dry Low NOx (DLN) Combustion Turbine with duct firing operating in combined cycle mode controlled by Selective Catalytic Reduction (SCR) | 2016-06-29 | SCR #1(Other): 32.3 lb/hr with duct burner firing(24.7 lb/hr w/o); SCR #2(Other): 32.3 lb/hr with duct burner firing(24.7 lb/hr w/o) | Mostardi Platt | 207 MW | 7.3 lbs/hr burners on 3.0 lbs/hr burners off | 187 MW | 0 lb/hr 0.96 lb/hr | 25A | VOC - Volatile Organic Compounds | PP | Y | NA |  | Yes
2016 | 1772 | 0684000212 | Washington Energy Facility | 859 Ohio 83 | Beverly | 45715 | 1329 | Washington | P002 | Nominally Rated 207 MW GE 7FA - Natural-Gas Fired Dry Low NOx (DLN) Combustion Turbine with duct firing operating in combined cycle mode controlled by Selective Catalytic Reduction (SCR) | 2016-06-29 | SCR #1(Other): 32.3 lb/hr with duct burner firing(24.7 lb/hr w/o); SCR #2(Other): 32.3 lb/hr with duct burner firing(24.7 lb/hr w/o) | Mostardi Platt | 207 MW | 7.3 lbs/hr burners on 3.0 lbs/hr burners off | 185 MW 186 MW | 0.19 lb/hr 0.95 lb/hr | 25A | VOC - Volatile Organic Compounds | PP | Y | NA |  | Yes
2016 | 332 | 0165000132 | AEP Generation Resources Inc., - Darby Plant | 12509 Adkins Road | Mt. Sterling | 43143 | 9061 | Pickaway | P001 | Natural Gas or number two fuel oil-fired, simple cycle, combustion turbine having a nominal capacity of 1,115.2 MMBTU/hr (80 MW, nominal), controlled with a dry low NOx combustor; CT1 - Combustion Turbine No.1; *Modified | 2016-12-14 | PCT1(Other): Water Injection for NOx reduction during periods when distillate oil is used as fuel.; PCT2(Other): Water Injection for NOx reduction during periods when distillate oil is used as fuel; PCT3(Other): Water injection for NOx reduction during pe | Mostardi Platt | 80 MW, nominal | 5.5 lb/hr | 92 MWe | 0.7 lb/hr | 25A | VOC - Volatile Organic Compounds | PP | Y | NA | This test was conducted to demonstrate initial compliance with the VOC emissions limitation while burning No. 2 fuel oil. | Yes
2016 | 333 | 0165000132 | AEP Generation Resources Inc., - Darby Plant | 12509 Adkins Road | Mt. Sterling | 43143 | 9061 | Pickaway | P002 | Natural Gas or number two fuel oil-fired, simple cycle, combustion turbine having a nominal capacity of 1,115.2 MMBTU/hr (80 MW, nominal), controlled with a dry low NOx combustor; CT2 - Combustion Turbine No.2; *Modified | 2016-12-14 | PCT1(Other): Water Injection for NOx reduction during periods when distillate oil is used as fuel.; PCT2(Other): Water Injection for NOx reduction during periods when distillate oil is used as fuel; PCT3(Other): Water injection for NOx reduction during pe | Mostardi Platt | 80 MW, nominal | 5.5 lb/hr | 92 MWe | 0.1 lb/hr | 25A | VOC - Volatile Organic Compounds | PP | Y | NA | This test was conducted to demonstrate initial compliance with the VOC emissions limitation while burning No. 2 fuel oil. | Yes
2016 | 334 | 0165000132 | AEP Generation Resources Inc., - Darby Plant | 12509 Adkins Road | Mt. Sterling | 43143 | 9061 | Pickaway | P003 | Natural Gas or number two fuel oil-fired, simple cycle, combustion turbine having a nominal capacity of 1,115.2 MMBTU/hr (80 MW, nominal), controlled with a dry low NOx combustor; CT3 - Combustion Turbine No.3; *Modified | 2016-12-14 | PCT1(Other): Water Injection for NOx reduction during periods when distillate oil is used as fuel.; PCT2(Other): Water Injection for NOx reduction during periods when distillate oil is used as fuel; PCT3(Other): Water injection for NOx reduction during pe | Mostardi Platt | 80 MW, nominal | 5.5 lb/hr | 98 MWe | 0.7 lb/hr | 25A | VOC - Volatile Organic Compounds | PP | Y | NA | This test was conducted to demonstrate initial compliance with the VOC emissions limitation while burning No. 2 fuel oil. | Yes
2016 | 335 | 0165000132 | AEP Generation Resources Inc., - Darby Plant | 12509 Adkins Road | Mt. Sterling | 43143 | 9061 | Pickaway | P004 | Natural Gas or number two fuel oil-fired, simple cycle, combustion turbine having a nominal capacity of 1,115.2 MMBTU/hr (80 MW, nominal), controlled with a dry low NOx combustor; CT4 - Combustion Turbine No.4; *Modified | 2016-12-14 | PCT1(Other): Water Injection for NOx reduction during periods when distillate oil is used as fuel.; PCT2(Other): Water Injection for NOx reduction during periods when distillate oil is used as fuel; PCT3(Other): Water injection for NOx reduction during pe | Mostardi Platt | 80 MW, nominal | 5.5 lb/hr | 93 MWe | 0.3 lb/hr | 25A | VOC - Volatile Organic Compounds | PP | Y | NA | This test was conducted to demonstrate initial compliance with the VOC emissions limitation while burning No. 2 fuel oil. | Yes
2016 | 340 | 0165000132 | AEP Generation Resources Inc., - Darby Plant | 12509 Adkins Road | Mt. Sterling | 43143 | 9061 | Pickaway | P005 | Natural Gas or number two fuel oil-fired, simple cycle, combustion turbine having a nominal capacity of 1,115.2 MMBTU/hr (80 MW, nominal), controlled with a dry low NOx combustor; CT5 - Combustion Turbine No.5; *Modified | 2016-12-14 | PCT5(Other): Water injection for NOx reduction during periods when distillate oil is used as fuel.; PCT6(Other): Water injection for NOx reduction during periods when distillate oil is used for fuel. | Mostardi Platt | 80 MW, nominal | 5.5 lb/hr | 98 MWe | 1.3 lb/hr | 25A | VOC - Volatile Organic Compounds | PP | Y | NA | This test was conducted to demonstrate initial compliance with the VOC emissions limitation while burning No. 2 fuel oil. | Yes
2016 | 341 | 0165000132 | AEP Generation Resources Inc., - Darby Plant | 12509 Adkins Road | Mt. Sterling | 43143 | 9061 | Pickaway | P006 | Natural Gas or number two fuel oil-fired, simple cycle, combustion turbine having a nominal capacity of 1,115.2 MMBTU/hr (80 MW, nominal), controlled with a dry low NOx combustor; CT6 - Combustion Turbine No.6; *Modified | 2016-12-14 | PCT5(Other): Water injection for NOx reduction during periods when distillate oil is used as fuel.; PCT6(Other): Water injection for NOx reduction during periods when distillate oil is used for fuel. | Mostardi Platt | 80 MW, nominal | 5.5 lb/hr | 98 MWe | 1.1 lb/hr | 25A | VOC - Volatile Organic Compounds | PP | Y | NA | This test was conducted to demonstrate initial compliance with the VOC emissions limitation while burning No. 2 fuel oil. | Yes
2016 | 1929 | 0857043334 | AES Ohio Generation, LLC | 2101 Arbor Boulevard | Dayton | 45439 | 1511 | Montgomery | P003 | Natural gas and No. 2 fuel oil fired simple cycle stationary combustion turbine No. 6 - Tait CT6, with a nominal production rating of 80 MW and a nominal heat input of 1115.2 mmBtu/hour, with dry low NOx combustion and water injection controls | 2016-10-28 | Control is within the combustion zone as dry low NOx combustion | Mostardi Platt | 80 MW | 5.5 lb/hr | 85 MW | 0.36 lb/hr | 25A | VOC - Volatile Organic Compounds | PP | Y | NA | This test was designed to show compliance with permit allowables using #2 fuel oil. | Yes
2016 | 1940 | 0857043334 | AES Ohio Generation, LLC | 2101 Arbor Boulevard | Dayton | 45439 | 1511 | Montgomery | P001 | Natural gas and No. 2 fuel oil fired simple cycle stationary combustion turbine No. 4 - Tait CT4, with a nominal production rating of 80 MW and a nominal heat input of 1115.2 mmBtu/hour, with dry low NOx combustion and water injection controls | 2016-11-22 | Control is within the combustion zone as dry low NOx combustion | Mostardi Platt | 80 MW | 5.5 lb/hr | 76 MW | 0.55 lb/hr | 25A | VOC - Volatile Organic Compounds | PP | Y | NA | This test was designed to show compliance with permit allowables using #2 fuel oil and at base load. | Yes
2016 | 1941 | 0857043334 | AES Ohio Generation, LLC | 2101 Arbor Boulevard | Dayton | 45439 | 1511 | Montgomery | P002 | Natural gas and No. 2 fuel oil fired simple cycle stationary combustion turbine No. 5 - Tait CT5, with a nominal production rating of 80 MW and a nominal heat input of 1115.2 mmBtu/hour, with dry low NOx combustion and water injection controls | 2016-11-22 | Control is within the combustion zone as dry low NOx combustion | Mostardi Platt | 80 MW | 5.5 lb/hr | 80 MW | 0.45 lb/hr | 25A | VOC - Volatile Organic Compounds | PP | Y | NA | This test was designed to show compliance with permit allowables using #2 fuel oil and at base load. | Yes
2016 | 1942 | 0857043334 | AES Ohio Generation, LLC | 2101 Arbor Boulevard | Dayton | 45439 | 1511 | Montgomery | P004 | Natural gas and No. 2 fuel oil fired simple cycle stationary combustion turbine No. 7 - Tait CT7, with a nominal production rating of 80 MW and a nominal heat input of 1115.2 mmBtu/hour, with dry low NOx combustion and water injection controls | 2016-11-22 | Control is within the combustion zone as dry low NOx combustion | Mostardi Platt | 80 MW | 5.5 lb/hr | 83 MW | 0.48 lb/hr | 25A | VOC - Volatile Organic Compounds | PP | Y | NA | This test was designed to show compliance with permit allowables using #2 fuel oil and at base load. | Yes
2005 | 551 | 0387000377 | Troy Energy, LLC | 22379 Pemberville Road | Luckey | 43443 |  | Wood | P001 | 1,570 mmBTU/hr combustion turbine | 2005-07-13 | none | TRC ENVIRONMENTAL CORPORATION | 1749.5 mmbtu/hr | 3.0 lbs/hr; 0.0017 lbs/mmbtu | 1617 mmbtu/hr | 0.0 lbs/hr; 0.0 lbs/mmbtu | 24 | VOC - Volatile Organic Compounds | PASS | NA | Y | Generator fuel was natural gas.
2005 | 553 | 0387000377 | Troy Energy, LLC | 22379 Pemberville Road | Luckey | 43443 |  | Wood | P001 | 1,570 mmBTU/hr combustion turbine | 2005-07-14 | none | TRC ENVIRONMENTAL CORPORATION | 1988.7 mmbtu/hr | 8.0 lbs/hr; 0.004 lbs/mmbtu | 1749.21 mmbtu/hr | 0.19 lbs/hr; 0.0001 lbs/mmbtu | 24 | VOC - Volatile Organic Compounds | PASS | NA | Y | Generator fuel was fuel oil.
2005 | 559 | 0387000377 | Troy Energy, LLC | 22379 Pemberville Road | Luckey | 43443 |  | Wood | P002 | 1,570 mmBTU/hr combustion turbine | 2005-07-15 | none | TRC ENVIRONMENTAL CORPORATION | 1749.5 mmbtu/hr | 3.0 lbs/hr; 0.0017 lbs/mmbtu | 1597 mmbtu/hr | 0.32 lbs/hr; 0.0001 lbs/mmbtu | 24 | VOC - Volatile Organic Compounds | PASS | NA | Y | Generator fuel was natural gas.
2005 | 563 | 0387000377 | Troy Energy, LLC | 22379 Pemberville Road | Luckey | 43443 |  | Wood | P002 | 1,570 mmBTU/hr combustion turbine | 2005-07-18 | none | TRC ENVIRONMENTAL CORPORATION | 1988.7 mmbtu/hr | 8.0 lbs/hr; 0.004 lbs/mmbtu | 1929.4 mmbtu/hr | -0.29 lbs/hr; -0.0002 lbs/mmbtu | 24 | VOC - Volatile Organic Compounds | PASS | NA | Y | Generator fuel was fuel oil.
2005 | 567 | 0387000377 | Troy Energy, LLC | 22379 Pemberville Road | Luckey | 43443 |  | Wood | P003 | 1,570 mmBTU/hr combustion turbine | 2005-07-19 | none | TRC ENVIRONMENTAL CORPORATION | 1988.7 mmbtu/hr | 8.0 lbs/hr; 0.004 lbs/mmbtu | 1941.77 mmbtu/hr | -0.75 lbs/hr ; -0.0004 lbs/mmbtu | 24 | VOC - Volatile Organic Compounds | PASS | NA | Y | Generator fuel was fuel oil.
2005 | 568 | 0387000377 | Troy Energy, LLC | 22379 Pemberville Road | Luckey | 43443 |  | Wood | P003 | 1,570 mmBTU/hr combustion turbine | 2005-07-20 | none | TRC ENVIRONMENTAL CORPORATION | 1749.5 mmbtu/hr | 3.0 lbs/hr; 0.0017 lbs/mmbtu | 1633.7 mmbtu/hr | -0.36 lbs/hr; -0.0002 lbs/mmbtu | 24 | VOC - Volatile Organic Compounds | PASS | NA | Y | Generator fuel was natural gas.
2005 | 576 | 0387000377 | Troy Energy, LLC | 22379 Pemberville Road | Luckey | 43443 |  | Wood | P004 | 1,570 mmBTU/hr combustion turbine | 2005-07-21 | none | TRC ENVIRONMENTAL CORPORATION | 1749.5 mmbtu/hr | 3.0 lbs/hr; 0.0017 lbs/mmbtu | 1625.1 mmbtu/hr | 0.66 lbs/hr; 0.0004 lbs/mmbtu | 24 | VOC - Volatile Organic Compounds | PASS | NA | Y | Generator fuel was natural gas.
2005 | 580 | 0387000377 | Troy Energy, LLC | 22379 Pemberville Road | Luckey | 43443 |  | Wood | P004 | 1,570 mmBTU/hr combustion turbine | 2005-07-22 | none | TRC ENVIRONMENTAL CORPORATION | 1988.7 mmbtu/hr | 8.0 lbs/hr; 0.004 lbs/mmbtu | 1790.1 mmbtu/hr | -0.14 lbs/hr; 0.0 lbs/mmbtu | 24 | VOC - Volatile Organic Compounds | PASS | NA | Y | Generator fuel was fuel oil.
2004 | 1154 | 1431070849 | University of Cincinnati | Clifton Campus | Cincinnati | 45221 |  | Hamilton | P003 | 13.5 MW Natural Gas/ No. 2 Fuel Oil-fired Turbines with 98.5 mmBtu/hr duct burner | 2004-05-28 | control equipment? | RMC | 14.5mw/hr | .56 lb/hr | 12 mw/hr | .05 lb/hr | 25A | Total Hydrocarbons | PASS | Y | Y |  | Yes
2004 | 1159 | 1431070849 | University of Cincinnati | Clifton Campus | Cincinnati | 45221 |  | Hamilton | P004 | 13.5 MW Natural Gas/ No. 2 Fuel Oil-fired Turbines with 98.5 mmBtu/hr duct burner | 2004-05-28 | cat | RMC | 14.5mw/hr | 96ppm 54.9lb/hr | 12 mw/hr | 55ppm and 33.6lb/hr | 7 | Total Hydrocarbons | PASS | Y | Y |  | Yes
2004 | 1160 | 1431070849 | University of Cincinnati | Clifton Campus | Cincinnati | 45221 |  | Hamilton | P004 | 13.5 MW Natural Gas/ No. 2 Fuel Oil-fired Turbines with 98.5 mmBtu/hr duct burner | 2004-05-28 | cat | RMC | 14.5mw/hr | .56 lb/hr | 12 mw/hr | .02lb/hr | 25A | Total Hydrocarbons | PASS | Y | Y |  | Yes
2004 | 1164 | 1431070849 | University of Cincinnati | Clifton Campus | Cincinnati | 45221 |  | Hamilton | P003 | 13.5 MW Natural Gas/ No. 2 Fuel Oil-fired Turbines with 98.5 mmBtu/hr duct burner | 2004-09-08 | control equipment? | RMC | 14.5mw/hr | .55 lb/hr | 12 mw/hr | .4 lb/hr | 25A | Total Hydrocarbons | FAIL | N | Y |  | Yes
2011 | 1199 | 1667040085 | Kent State University Heating Plant | P.O. Box 5190 | Kent | 44242 | 0001 | Portage | B010 | Combustion Turbine CT 2 | 2011-12-01 | None | Air Compliance Testing Inc | 76 MMBtu/hr | 0.035 lb/MMBtu 11.7 TPY | 76 MMBtu/hr | <0.0088 lb/MMBtu 2.96 TPY | 25A | Total Hydrocarbons | PASS | NA | Y | EPA Method 25A Passed
2015 | 1392 | 1667040085 | Kent State University Heating Plant | P.O. Box 5190 | Kent | 44242 | 0001 | Portage | B010 | Combustion Turbine CT 2 | 2015-01-15 | none | Air Compliance Testing, Inc. | 7 MW | 0.35 lb/mmBtu | 7 MW | 0.0087 lb/mmBtu | 25A | Total Hydrocarbons | PP | NA | Y |  | Yes